## Workbook Summary
Workbook Table of Contents
Tab | Description
Workbook Summary
Summary by Measure | Summary table and chart comparison of prior workpaper revision measure equipment and labor costs to proposed udpated measure equipment and labor costs
Program Data | HVAC QM program data from the prior 12 months (April 2017 - April 2018), including unit tonnage frequency, refrigerant type prevalence, and total refrigerant weight (lbs) per refrigeration ton.
Materials Costs | Equipment cost estimates and supporting information for the economizer repair, economizer controls, condenser coil cleaning, evaporator coil cleaning, and ADEC equipment. (Refrigerant material costs were obtained through contractor survey responses.)
HVAC Labor_Union | Labor rates for select major California cities obtained from 2018 RSMeans (raw data)
HVAC Labor_Union pivot | Pivot table of HVAC Labor_Union tab used to derive average labor rate ($/hour)
Contractor responses | Labor hour estimates for each measure and refrigerant materials cost estimates were obtained from 8 active, program-participating contractors. Labor estimates were provided for system tonnage ranges, which were then used to derive a tonnage-normalized labor cost ($/ton) from a weighted average using weighting factors from the Program Data tab.
Contractor1_responses | Survey esponses for each individual contractor have anonymized and included on separate tabs.
Contractor2_responses
Contractor3_responses
Contractor4_responses
Contractor5_responses
Contractor6_responses
Contractor7_responses
Contractor8_responses

## Summary by Measure
|  |  |  | Old | Old | Old |  | New | New | New
Workpaper | Measure | Measure Detail | Rev | Equipment Cost ($/ton) | Labor Cost ($/ton) | Total Cost ($/ton) | Rev | Equipment Cost ($/ton) | Labor Cost ($/ton) | Total Cost ($/ton) | % diff Equipment | % diff Labor | % diff Total
PGE3PHVC151 – Economizer Repair |  |  | R3 |  |  |  | R4
PGE3PHVC151 – Economizer Repair | Economizer Repair | Non-ADEC | R3 | 19.64 | 19.78 | 39.42 | R4 | 21.9883 | 28.01 | 49.9983 | 11.96% | 41.61% | 26.83%
|  | ADEC | R3 | 84.78 | 52 | 136.78 | R4 | 69.6053 | 56.87 | 126.4753 | -17.9% | 9.365% | -7.534%
PGE3PHVC152 – Economizer Controls |  |  | R4 |  |  |  | R5 | [5 empty] | #VALUE!
PGE3PHVC152 – Economizer Controls | Economizer Controls | Adjustment | R4 | 0 | 5.43 | 5.43 | R5 | 0 | 2.93 | 2.93 |  | -46.04% | -46.04%
|  | Replacement | R4 | 2.88 | 10.86 | 13.74 | R5 | 3.2102 | 18.78 | 21.9902 | 11.47% | 72.93% | 60.05%
PGE3PHVC156 – Condenser Coil Cleaning | Condenser Coil Cleaning |  | R2 | 6.73 | 25.65 | 32.38 | R3 | 0.72225 | 18.79 | 19.5122 | -89.27% | -26.74% | -39.74%
PGE3PHVC157 – Unoccupied Supply Fan Control | Unoccupied Supply Fan Control |  | R2 | 0 | 5.43 | 5.43 | R3 | 0 | 2.93 | 2.93 |  | -46.04% | -46.04%
PGE3PHVC158 – Evaporator Coil Cleaning | Evaporator Coil Cleaning |  | R2 | 7.98 | 33.69 | 41.67 | R3 | 0.72643 | 22.41 | 23.1364 | -90.9% | -33.48% | -44.48%
PGE3PHVC160 – Refrigerant Charge Adjustment | Refrigerant Charge Adjustment |  | R2 | 9.92 | 26.78 | 36.7 | R3 | 8.3231 | 39.17 | 47.4931 | -16.1% | 46.27% | 29.41%
Narrative on changes
PGE3PHVC151 – Economizer Repair
Non-ADEC
Prior cost estimates were obtained from WO017 Ex Ante Measure Cost Study Final Report, as referenced by the prior workpaper revision. For the updated cost, equipment cost estimates were provided by CLEAResult field staff (see "Materials Costs" tab) and labor cost estimates were obtained from contractor survey responses ("Contractor responses" tab). Equipment costs are relatively consistent with the prior estimate and labor costs have increased, likely due to an increase in labor rates.
ADEC
Prior cost estimates were obtained from PGECOHVC143 Revision 1 VFD and Enhanced Ventilation for Packaged HVAC units with Gas Heating and Packaged Heat Pumps. For the updated cost, equipment costs were derived from a combination of manufacturer pricing and program invoicing ("Contractor responses" tab). Equipment costs for advanced digital controllers has dropped significantly since 2014 (when PGECOHVC143 Revision 1 was authored) and the labor hours to install have also decreased as contractors have become more familiar with this equipment. Therefore, equipment costs have decreased since the prior estimate and labor costs have only increased slightly (due to an increase in labor rates, not in labor hours).
PGE3PHVC152 – Economizer Controls
Adjustment
There is no equipment cost for this measure, as it involves making an adjustment to existing equipment with no materials required. The prior workpaper revision provided a labor cost estimate based on an assumption of 1 hour of labor at a DEER labor rate of $67.88 and normalized to an assumed average RTU tonnage of 12.5 tons. For the updated cost, it is assumed that the controls adjustment requires 15 minutes of labor (based on estimates from CLEAResult field staff) at a labor rate of $82.35 (from 2018 RSMeans data; see "HVAC Labor_Union pivot" tab) and an average RTU tonnage of 7 tons (from historical program data; see "Program Data" tab). This results in a reduction in measure cost from the prior estimate.
Replacement
The prior workpaper revision provided an equipment cost by averaging five cost estimates of a replacement sensor combined with a labor cost by assuming 2 hours of labor at a DEER labor rate of $67.88, all normalized to an assumed average RTU tonnage of 12.5 tons. For the updated cost, four cost estimates of a replacement sensor were obtained ("Materials Costs" tab) combined with a labor cost estimate obtained from contractor survey responses ("Contractor responses" tab) and an average RTU tonnage of 7 tons ("Program Data" tab). Equipment costs are relatively consistent with the prior estimate and labor costs have increased, likely due to an increase in labor rates.
PGE3PHVC156 – Condenser Coil Cleaning
Prior cost estimates were obtained from WO017 Ex Ante Measure Cost Study Final Report, as referenced by the prior workpaper revision. For the updated cost, equipment cost estimates were obtained for multiple cleaner products (see "Materials Costs" tab) and labor cost estimates were obtained from contractor survey responses ("Contractor responses" tab). Equipment costs are much lower than the prior estimate and labor costs have decreased as well. Without knowledge of how the WO017 coil cleaning estimates were obtained, it's difficult to conjecture as to the reduction in cost but we have provided sources for our cost estimates in this workbook as described above.
PGE3PHVC157 – Unoccupied Supply Fan Control
There is no equipment cost for this measure, as it involves making an adjustment to existing equipment with no materials required. The prior workpaper revision provided a labor cost estimate based on an assumption of 1 hour of labor at a DEER labor rate of $67.88 and normalized to an assumed average RTU tonnage of 12.5 tons. For the updated cost, it is assumed that the controls adjustment requires 15 minutes of labor (based on estimates from CLEAResult field staff) at a labor rate of $82.35 (from 2018 RSMeans data; see "HVAC Labor_Union pivot" tab) and an average RTU tonnage of 7 tons (from historical program data; see "Program Data" tab). This results in a reduction in measure cost from the prior estimate.
PGE3PHVC158 – Evaporator Coil Cleaning
Prior cost estimates were obtained from WO017 Ex Ante Measure Cost Study Final Report, as referenced by the prior workpaper revision. For the updated cost, equipment cost estimates were obtained for multiple cleaner products (see "Materials Costs" tab) and labor cost estimates were obtained from contractor survey responses ("Contractor responses" tab). Equipment costs are much lower than the prior estimate and labor costs have decreased as well. Without knowledge of how the WO017 coil cleaning estimates were obtained, it's difficult to conjecture as to the reduction in cost but we have provided sources for our cost estimates in this workbook as described above.
PGE3PHVC160 – Refrigerant Charge Adjustment
Prior cost estimates were obtained from the 2010-2012 WO017 Ex Ante Measure Cost Study Final Report, as referenced by the prior workpaper revision. For the updated cost, materials (i.e., refrigerant) cost estimates and labor cost estimates were obtained from contractor survey responses ("Contractor responses" tab). Equipment costs are lower than the prior estimate - we feel this is likely due to units having R22 being less prevalent now than in 2012, offsetting the R22 cost increase that has occurred since 2012. For the amount of refrigerant added we have assumed a 4.5% of factory charge addition (typical addition from Resolution E-4867) and a total system charge per RTU tonnage of 2 lbs/ton from historical program data ("Program Data" tab). Labor costs are higher than the prior estimate - this is likely due to an increase in labor rates.
http://www.inflation.eu/inflation-rates/united-states/historic-inflation/cpi-inflation-united-states.aspx
Inflation
2014 |  | 3.26% |  | 100
2015 |  | 3.42% |  | 103.26
2016 |  | 2.54% |  | 106.7915
2017 |  | 4.08% |  | 109.504
113.9718
2014-2018 |  |  |  | 13.97%
Note on I15: Phil Jordan: Assuming 4.5% addition is typical per Resolution E-4867

## Program Data
Tonnage | [8 empty] | Refrigerant
Filter | 0
Row Labels | Count of IOUExAnteQuantity | Weighting Factor Group #1 | Weighting Factor Group #2 |  | Weighting Factors |  | Weighting Factors |  | Row Labels | Count of Refrigerant type
1 | 1 | 2-5 | 2-6 | 1 | 2-5 | 1852 | 2-6 | 1969 | R-22 | 1521 | 44.88%
2 | 47 | 2-5 | 2-6 | 1 | 6-20 | 614 | 7-15 | 477 | R-407C | 2 | 0.05901%
2.5 | 10 | 2-5 | 2-6 | 1 | 25-30 | 1 | 15-20 | 20 | R-410A | 1866 | 55.06%
3 | 112 | 2-5 | 2-6 | 1 | 35-50 | 32 | 25-30 | 1 | Grand Total | 3389
3.5 | 442 | 2-5 | 2-6 | 1 | >50 | 38 | 35-50 | 32
4 | 686 | 2-5 | 2-6 | 1 |  |  | >50 | 38 | Omit | 0
5 | 554 | 2-5 | 2-6 | 1 | Average Tonnage
5.5 | 14 | 6-20 | 2-6 | 1 | 7.0307 |  |  |  | Row Labels | Average of lbs/ton |  | 2.0119 | lbs/ton
6 | 103 | 6-20 | 2-6 | 1 |  |  |  |  | 1 | 5.5625
6.5 | 1 | 6-20 | 7-15 | 1 |  |  |  |  | 1.5 | 2.8917
7 | 84 | 6-20 | 7-15 | 1 |  |  |  |  | 2 | 2.8481
7.5 | 131 | 6-20 | 7-15 | 1 |  |  |  |  | 2.5 | 2.4193
8 | 8 | 6-20 | 7-15 | 1 |  |  |  |  | 3 | 2.4844
8.5 | 57 | 6-20 | 7-15 | 1 |  |  |  |  | 3.5 | 2.1907
10 | 88 | 6-20 | 7-15 | 1 |  |  |  |  | 4 | 2.2524
11 | 16 | 6-20 | 7-15 | 1 |  |  |  |  | 4.5 | 4.0667
12 | 16 | 6-20 | 7-15 | 1 |  |  |  |  | 5 | 2.0995
12.5 | 17 | 6-20 | 7-15 | 1 |  |  |  |  | 5.5 | 1.7841
14 | 6 | 6-20 | 7-15 | 1 |  |  |  |  | 6 | 2.1309
15 | 53 | 6-20 | 7-15 | 1 |  |  |  |  | 6.5 | 2.6858
20 | 20 | 6-20 | 15-20 | 1 |  |  |  |  | 7 | 1.8873
30 | 1 | 25-30 | 25-30 | 1 |  |  |  |  | 7.5 | 2.0593
40 | 10 | 35-50 | 35-50 | 1 |  |  |  |  | 8 | 1.8531
50 | 22 | 35-50 | 35-50 | 1 |  |  |  |  | 8.5 | 1.8713
62 | 1 | >50 | >50 | 1 |  |  |  |  | 8.75 | 3.3357
75 | 32 | >50 | >50 | 1 |  |  |  |  | 9.5 | 2.3169
103 | 2 | >50 | >50 | 1 |  |  |  |  | 10 | 1.7194
148.5 | 1 | >50 | >50 | 1 |  |  |  |  | 11 | 2.4957
150 | 1 | >50 | >50 | 1 |  |  |  |  | 11.16 | 3.0802
263.5 | 1 | >50 | >50 | 1 |  |  |  |  | 12 | 2.0185
Grand Total | 2537 | [7 empty] | 12.5 | 1.7919
[9 empty] | 13 | 1.9856
Total Tonnage | 17837 | 7.0307 | [6 empty] | 14 | 1.6183
Total Count | 2537 | [7 empty] | 15 | 1.7919
[9 empty] | 16 | 2.2325
[9 empty] | 17 | 2.4118
[9 empty] | 17.5 | 1.9232
[9 empty] | 20 | 1.7086
[9 empty] | 24 | 1.388
[9 empty] | 25 | 1.484
[9 empty] | 25.1 | 1.9821
[9 empty] | 28.8 | 1
[9 empty] | 30 | 2.2733
[9 empty] | 34 | 0.73529
[9 empty] | 35 | 0.98631
[9 empty] | 40 | 1.1326
[9 empty] | 50 | 1.4117
[9 empty] | 51 | 1.1458
[9 empty] | 54 | 0.16435
[9 empty] | 55 | 1.2182
[9 empty] | 60 | 1.7932
[9 empty] | 70 | 1.4445
[9 empty] | 75 | 0.85917
[9 empty] | Grand Total | 2.121

## Materials Costs
Economizer Repair
Description | Price | Frequency |  | Tonnage | Price Est. | Factor | Weight |  | Tonnage | Price Est. | Factor | Weight
Wiring | 15 | 1 | Dampers | 5-10 | 175 | 1040 | 155.6886 | Linkage | 5-25 | 35 | 1168 | 34.0383
Dampers | 205.6031 | 0.33 |  | 12.5-25 | 350 | 96 | 28.7425 |  | 30 | 50 | 1 | 0.041632
Actuator | 180 | 0.33 |  | 25-50 | 750 | 33 | 21.1719 |  | 40-50 | 125 | 32 | 3.3306
Linkage | 37.4105 | 0.33 |  |  |  |  | 205.6031 |  |  |  |  | 37.4105
Average Cost: | 154.5945
Normalized Cost: | 21.9883
Economizer Control Replacement
Mfg | Sensor Type | Total Cost
Honeywell | C7660A1000 | 35.35
Honeywell | C7660A1000 | 21.24
Honeywell | C7660A1000 | 58.93
Honeywell | C7660A1000 | 44.99
| Average Cost: | 40.1275
| Normalized Cost: | 3.2102
Coil Cleaning
Condenser Coil Cleaning
Amount | Price | Units Cleaned | Normalized Price
18 oz. | 17.7 | 1 | 2.5286
18 oz. | 13.45 | 1 | 1.9214
20 oz. | 14.5 | 1 | 2.0714
1 qt. | 26 | 5 | 0.74286
1 gal. | 22.8 | 20 | 0.16286
1 gal. | 20.6 | 20 | 0.14714
1 gal. | 29.4 | 20 | 0.21
1 gal. | 19.6 | 20 | 0.14
2.5 gal. | 70.75 | 50 | 0.20214
2.5 gal. | 49.2 | 50 | 0.14057
1 gal. | 30.4 | 20 | 0.21714
1 gal. | 25.6 | 20 | 0.18286
|  | Average Normalized Cost: | 0.72225
Evaporator Coil Cleaning
Amount | Price | Units Cleaned | Normalized Price
18 oz. | 13.3 | 1 | 1.9
18 oz. | 12.5 | 1 | 1.7857
1 gal. | 24.5 | 20 | 0.175
1 gal. | 20.4 | 20 | 0.14571
1 gal. | 27.8 | 20 | 0.19857
2.5 gal. | 53.75 | 50 | 0.15357
|  | Average Normalized Cost: | 0.72643
ADEC
Manufacturer | Description | Price |  | MfgA (standalone controller) | [8 empty] | MfgB (standalone controller) | MfgC (kit) | MfgD (kit) | MfgE (kit) | Sensors & Actuator
ManufacturerA | Controller (standalone) | 814.81
ManufacturerB | Controller (standalone) | 153.85
ManufacturerC | Controller kit (includes actuator and sensors) | 372.95
ManufacturerD | Controller kit (includes actuator and sensors) | 431.99
ManufacturerE | Controller kit (includes actuator and sensors) | 366
| Sensors & Actuator | 235.3
| Average Cost: | 522.04
| Average Normalized Cost: | 69.6053
Note on A1: Phil Jordan: Economizer repair cost estimates from Michael Blazey, Field Manager
Note on C53: Phil Jordan: Assume 20 units/gallon
Note on C69: Phil Jordan: Assume 20 units/gallon

## HVAC Labor_Union
2018 RSMeans data from Gordian
https://www.rsmeansonline.com/
Location | Quantity | LineNumber | Line Source | SubContracted Ind. | Description | Crew | Daily Output | Labor Hours | Unit | Material | Labor | Equipment | Total | Ext. Mat. | Ext. Labor | Ext. Equip. | Ext. Total | Mat. O&P | Labor O&P | Equip. O&P | Total O&P | Ext. Mat. O&P | Ext. Labor O&P | Ext. Equip. O&P | Ext. Total O&P | Labor Type | Data Release | CCI Location | Notes
San Jose | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 2106 | 0 | 4906 | 0 | 0 | 0 | 0 | 3075 | 3159 | 0 | 6234 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 2430 | 0 | 5755 | 0 | 0 | 0 | 0 | 3650 | 3645 | 0 | 7295 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2632.5 | 0 | 7007.5 | 0 | 0 | 0 | 0 | 4800 | 3928.5 | 0 | 8728.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2835 | 0 | 7835 | 0 | 0 | 0 | 0 | 5475 | 4252.5 | 0 | 9727.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2956.5 | 0 | 8781.5 | 0 | 0 | 0 | 0 | 6400 | 4455 | 0 | 10855 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 3199.5 | 0 | 10274.5 | 0 | 0 | 0 | 0 | 7775 | 4819.5 | 0 | 12594.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 3442.5 | 0 | 12592.5 | 0 | 0 | 0 | 0 | 10100 | 5143.5 | 0 | 15243.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 3604.5 | 0 | 14004.5 | 0 | 0 | 0 | 0 | 11400 | 5467.5 | 0 | 16867.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 4009.5 | 0 | 17109.5 | 0 | 0 | 0 | 0 | 14400 | 6034.5 | 0 | 20434.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 4374 | 0 | 18274 | 0 | 0 | 0 | 0 | 15300 | 6601.5 | 0 | 21901.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 4657.5 | 0 | 34157.5 | 0 | 0 | 0 | 0 | 32500 | 7006.5 | 0 | 39506.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 5589 | 0 | 37589 | 0 | 0 | 0 | 0 | 35200 | 8424 | 0 | 43624 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 6642 | 0 | 42342 | 0 | 0 | 0 | 0 | 39300 | 10003.5 | 0 | 49303.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 8869.5 | 0 | 52769.5 | 0 | 0 | 0 | 0 | 48200 | 13324.5 | 0 | 61524.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 11056.5 | 0 | 60956.5 | 0 | 0 | 0 | 0 | 55000 | 16686 | 0 | 71686 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 13284 | 0 | 72784 | 0 | 0 | 0 | 0 | 65500 | 20088 | 0 | 85588 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 15552 | 0 | 93052 | 0 | 0 | 0 | 0 | 85000 | 23490 | 0 | 108490 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 18306 | 0 | 125306 | 0 | 0 | 0 | 0 | 118000 | 27540 | 0 | 145540 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
San Jose | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 22194 | 0 | 147694 | 0 | 0 | 0 | 0 | 138000 | 33372 | 0 | 171372 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN JOSE (951)
Los Angeles | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1773.2 | 0 | 4573.2 | 0 | 0 | 0 | 0 | 3075 | 2659.8 | 0 | 5734.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 2046 | 0 | 5371 | 0 | 0 | 0 | 0 | 3650 | 3069 | 0 | 6719 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2216.5 | 0 | 6591.5 | 0 | 0 | 0 | 0 | 4800 | 3307.7 | 0 | 8107.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2387 | 0 | 7387 | 0 | 0 | 0 | 0 | 5475 | 3580.5 | 0 | 9055.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2489.3 | 0 | 8314.3 | 0 | 0 | 0 | 0 | 6400 | 3751 | 0 | 10151 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2693.9 | 0 | 9768.9 | 0 | 0 | 0 | 0 | 7775 | 4057.9 | 0 | 11832.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2898.5 | 0 | 12048.5 | 0 | 0 | 0 | 0 | 10100 | 4330.7 | 0 | 14430.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 3034.9 | 0 | 13434.9 | 0 | 0 | 0 | 0 | 11400 | 4603.5 | 0 | 16003.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3375.9 | 0 | 16475.9 | 0 | 0 | 0 | 0 | 14400 | 5080.9 | 0 | 19480.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3682.8 | 0 | 17582.8 | 0 | 0 | 0 | 0 | 15300 | 5558.3 | 0 | 20858.3 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3921.5 | 0 | 33421.5 | 0 | 0 | 0 | 0 | 32500 | 5899.3 | 0 | 38399.3 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4705.8 | 0 | 36705.8 | 0 | 0 | 0 | 0 | 35200 | 7092.8 | 0 | 42292.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5592.4 | 0 | 41292.4 | 0 | 0 | 0 | 0 | 39300 | 8422.7 | 0 | 47722.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7467.9 | 0 | 51367.9 | 0 | 0 | 0 | 0 | 48200 | 11218.9 | 0 | 59418.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 9309.3 | 0 | 59209.3 | 0 | 0 | 0 | 0 | 55000 | 14049.2 | 0 | 69049.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 11184.8 | 0 | 70684.8 | 0 | 0 | 0 | 0 | 65500 | 16913.6 | 0 | 82413.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 13094.4 | 0 | 90594.4 | 0 | 0 | 0 | 0 | 85000 | 19778 | 0 | 104778 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 15413.2 | 0 | 122413.2 | 0 | 0 | 0 | 0 | 118000 | 23188 | 0 | 141188 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
Los Angeles | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 18686.8 | 0 | 144186.8 | 0 | 0 | 0 | 0 | 138000 | 28098.4 | 0 | 166098.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LOS ANGELES (900-902)
San Francisco | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 2345.2 | 0 | 5145.2 | 0 | 0 | 0 | 0 | 3075 | 3517.8 | 0 | 6592.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 2706 | 0 | 6031 | 0 | 0 | 0 | 0 | 3650 | 4059 | 0 | 7709 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2931.5 | 0 | 7306.5 | 0 | 0 | 0 | 0 | 4800 | 4374.7 | 0 | 9174.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 3157 | 0 | 8157 | 0 | 0 | 0 | 0 | 5475 | 4735.5 | 0 | 10210.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 3292.3 | 0 | 9117.3 | 0 | 0 | 0 | 0 | 6400 | 4961 | 0 | 11361 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 3562.9 | 0 | 10637.9 | 0 | 0 | 0 | 0 | 7775 | 5366.9 | 0 | 13141.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 3833.5 | 0 | 12983.5 | 0 | 0 | 0 | 0 | 10100 | 5727.7 | 0 | 15827.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 4013.9 | 0 | 14413.9 | 0 | 0 | 0 | 0 | 11400 | 6088.5 | 0 | 17488.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 4464.9 | 0 | 17564.9 | 0 | 0 | 0 | 0 | 14400 | 6719.9 | 0 | 21119.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 4870.8 | 0 | 18770.8 | 0 | 0 | 0 | 0 | 15300 | 7351.3 | 0 | 22651.3 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 5186.5 | 0 | 34686.5 | 0 | 0 | 0 | 0 | 32500 | 7802.3 | 0 | 40302.3 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 6223.8 | 0 | 38223.8 | 0 | 0 | 0 | 0 | 35200 | 9380.8 | 0 | 44580.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 7396.4 | 0 | 43096.4 | 0 | 0 | 0 | 0 | 39300 | 11139.7 | 0 | 50439.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 9876.9 | 0 | 53776.9 | 0 | 0 | 0 | 0 | 48200 | 14837.9 | 0 | 63037.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 12312.3 | 0 | 62212.3 | 0 | 0 | 0 | 0 | 55000 | 18581.2 | 0 | 73581.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 14792.8 | 0 | 74292.8 | 0 | 0 | 0 | 0 | 65500 | 22369.6 | 0 | 87869.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 17318.4 | 0 | 94818.4 | 0 | 0 | 0 | 0 | 85000 | 26158 | 0 | 111158 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 20385.2 | 0 | 127385.2 | 0 | 0 | 0 | 0 | 118000 | 30668 | 0 | 148668 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
San Francisco | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 24714.8 | 0 | 150214.8 | 0 | 0 | 0 | 0 | 138000 | 37162.4 | 0 | 175162.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN FRANCISCO (940-941)
Fresno | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1714.7 | 0 | 4514.7 | 0 | 0 | 0 | 0 | 3075 | 2572.05 | 0 | 5647.05 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1978.5 | 0 | 5303.5 | 0 | 0 | 0 | 0 | 3650 | 2967.75 | 0 | 6617.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2143.38 | 0 | 6518.38 | 0 | 0 | 0 | 0 | 4800 | 3198.58 | 0 | 7998.58 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2308.25 | 0 | 7308.25 | 0 | 0 | 0 | 0 | 5475 | 3462.38 | 0 | 8937.38 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2407.18 | 0 | 8232.18 | 0 | 0 | 0 | 0 | 6400 | 3627.25 | 0 | 10027.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2605.03 | 0 | 9680.03 | 0 | 0 | 0 | 0 | 7775 | 3924.03 | 0 | 11699.03 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2802.88 | 0 | 11952.88 | 0 | 0 | 0 | 0 | 10100 | 4187.83 | 0 | 14287.83 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 2934.78 | 0 | 13334.78 | 0 | 0 | 0 | 0 | 11400 | 4451.63 | 0 | 15851.63 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3264.53 | 0 | 16364.53 | 0 | 0 | 0 | 0 | 14400 | 4913.28 | 0 | 19313.28 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3561.3 | 0 | 17461.3 | 0 | 0 | 0 | 0 | 15300 | 5374.93 | 0 | 20674.93 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3792.13 | 0 | 33292.13 | 0 | 0 | 0 | 0 | 32500 | 5704.68 | 0 | 38204.68 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4550.55 | 0 | 36550.55 | 0 | 0 | 0 | 0 | 35200 | 6858.8 | 0 | 42058.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5407.9 | 0 | 41107.9 | 0 | 0 | 0 | 0 | 39300 | 8144.83 | 0 | 47444.83 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7221.53 | 0 | 51121.53 | 0 | 0 | 0 | 0 | 48200 | 10848.78 | 0 | 59048.78 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 9002.18 | 0 | 58902.18 | 0 | 0 | 0 | 0 | 55000 | 13585.7 | 0 | 68585.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 10815.8 | 0 | 70315.8 | 0 | 0 | 0 | 0 | 65500 | 16355.6 | 0 | 81855.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 12662.4 | 0 | 90162.4 | 0 | 0 | 0 | 0 | 85000 | 19125.5 | 0 | 104125.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 14904.7 | 0 | 121904.7 | 0 | 0 | 0 | 0 | 118000 | 22423 | 0 | 140423 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Fresno | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 18070.3 | 0 | 143570.3 | 0 | 0 | 0 | 0 | 138000 | 27171.4 | 0 | 165171.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / FRESNO (936-938)
Anaheim | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1803.1 | 0 | 4603.1 | 0 | 0 | 0 | 0 | 3075 | 2704.65 | 0 | 5779.65 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 2080.5 | 0 | 5405.5 | 0 | 0 | 0 | 0 | 3650 | 3120.75 | 0 | 6770.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2253.88 | 0 | 6628.88 | 0 | 0 | 0 | 0 | 4800 | 3363.48 | 0 | 8163.48 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2427.25 | 0 | 7427.25 | 0 | 0 | 0 | 0 | 5475 | 3640.88 | 0 | 9115.88 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2531.28 | 0 | 8356.28 | 0 | 0 | 0 | 0 | 6400 | 3814.25 | 0 | 10214.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2739.33 | 0 | 9814.33 | 0 | 0 | 0 | 0 | 7775 | 4126.33 | 0 | 11901.33 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2947.38 | 0 | 12097.38 | 0 | 0 | 0 | 0 | 10100 | 4403.73 | 0 | 14503.73 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 3086.08 | 0 | 13486.08 | 0 | 0 | 0 | 0 | 11400 | 4681.13 | 0 | 16081.13 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3432.83 | 0 | 16532.83 | 0 | 0 | 0 | 0 | 14400 | 5166.58 | 0 | 19566.58 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3744.9 | 0 | 17644.9 | 0 | 0 | 0 | 0 | 15300 | 5652.03 | 0 | 20952.03 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3987.63 | 0 | 33487.63 | 0 | 0 | 0 | 0 | 32500 | 5998.78 | 0 | 38498.78 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4785.15 | 0 | 36785.15 | 0 | 0 | 0 | 0 | 35200 | 7212.4 | 0 | 42412.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5686.7 | 0 | 41386.7 | 0 | 0 | 0 | 0 | 39300 | 8564.73 | 0 | 47864.73 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7593.83 | 0 | 51493.83 | 0 | 0 | 0 | 0 | 48200 | 11408.08 | 0 | 59608.08 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 9466.28 | 0 | 59366.28 | 0 | 0 | 0 | 0 | 55000 | 14286.1 | 0 | 69286.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 11373.4 | 0 | 70873.4 | 0 | 0 | 0 | 0 | 65500 | 17198.8 | 0 | 82698.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 13315.2 | 0 | 90815.2 | 0 | 0 | 0 | 0 | 85000 | 20111.5 | 0 | 105111.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 15673.1 | 0 | 122673.1 | 0 | 0 | 0 | 0 | 118000 | 23579 | 0 | 141579 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Anaheim | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 19001.9 | 0 | 144501.9 | 0 | 0 | 0 | 0 | 138000 | 28572.2 | 0 | 166572.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / ANAHEIM (928)
Long Beach | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2797.2 | 1700.4 | 0 | 4497.6 | 0 | 0 | 0 | 0 | 3071.93 | 2550.6 | 0 | 5622.53 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3321.68 | 1962 | 0 | 5283.68 | 0 | 0 | 0 | 0 | 3646.35 | 2943 | 0 | 6589.35 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4370.63 | 2125.5 | 0 | 6496.13 | 0 | 0 | 0 | 0 | 4795.2 | 3171.9 | 0 | 7967.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 4995 | 2289 | 0 | 7284 | 0 | 0 | 0 | 0 | 5469.53 | 3433.5 | 0 | 8903.03 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5819.18 | 2387.1 | 0 | 8206.28 | 0 | 0 | 0 | 0 | 6393.6 | 3597 | 0 | 9990.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7067.93 | 2583.3 | 0 | 9651.23 | 0 | 0 | 0 | 0 | 7767.23 | 3891.3 | 0 | 11658.53 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9140.85 | 2779.5 | 0 | 11920.35 | 0 | 0 | 0 | 0 | 10089.9 | 4152.9 | 0 | 14242.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10389.6 | 2910.3 | 0 | 13299.9 | 0 | 0 | 0 | 0 | 11388.6 | 4414.5 | 0 | 15803.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13086.9 | 3237.3 | 0 | 16324.2 | 0 | 0 | 0 | 0 | 14385.6 | 4872.3 | 0 | 19257.9 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13886.1 | 3531.6 | 0 | 17417.7 | 0 | 0 | 0 | 0 | 15284.7 | 5330.1 | 0 | 20614.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29470.5 | 3760.5 | 0 | 33231 | 0 | 0 | 0 | 0 | 32467.5 | 5657.1 | 0 | 38124.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 31968 | 4512.6 | 0 | 36480.6 | 0 | 0 | 0 | 0 | 35164.8 | 6801.6 | 0 | 41966.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35664.3 | 5362.8 | 0 | 41027.1 | 0 | 0 | 0 | 0 | 39260.7 | 8076.9 | 0 | 47337.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43856.1 | 7161.3 | 0 | 51017.4 | 0 | 0 | 0 | 0 | 48151.8 | 10758.3 | 0 | 58910.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49850.1 | 8927.1 | 0 | 58777.2 | 0 | 0 | 0 | 0 | 54945 | 13472.4 | 0 | 68417.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59440.5 | 10725.6 | 0 | 70166.1 | 0 | 0 | 0 | 0 | 65434.5 | 16219.2 | 0 | 81653.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77422.5 | 12556.8 | 0 | 89979.3 | 0 | 0 | 0 | 0 | 84915 | 18966 | 0 | 103881 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 106893 | 14780.4 | 0 | 121673.4 | 0 | 0 | 0 | 0 | 117882 | 22236 | 0 | 140118 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Long Beach | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125374.5 | 17919.6 | 0 | 143294.1 | 0 | 0 | 0 | 0 | 137862 | 26944.8 | 0 | 164806.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / LONG BEACH (906-908)
Redding | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1686.1 | 0 | 4486.1 | 0 | 0 | 0 | 0 | 3075 | 2529.15 | 0 | 5604.15 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1945.5 | 0 | 5270.5 | 0 | 0 | 0 | 0 | 3650 | 2918.25 | 0 | 6568.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2107.63 | 0 | 6482.63 | 0 | 0 | 0 | 0 | 4800 | 3145.23 | 0 | 7945.23 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2269.75 | 0 | 7269.75 | 0 | 0 | 0 | 0 | 5475 | 3404.63 | 0 | 8879.63 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2367.03 | 0 | 8192.03 | 0 | 0 | 0 | 0 | 6400 | 3566.75 | 0 | 9966.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2561.58 | 0 | 9636.58 | 0 | 0 | 0 | 0 | 7775 | 3858.58 | 0 | 11633.58 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2756.13 | 0 | 11906.13 | 0 | 0 | 0 | 0 | 10100 | 4117.98 | 0 | 14217.98 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 2885.83 | 0 | 13285.83 | 0 | 0 | 0 | 0 | 11400 | 4377.38 | 0 | 15777.38 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3210.08 | 0 | 16310.08 | 0 | 0 | 0 | 0 | 14400 | 4831.33 | 0 | 19231.33 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3501.9 | 0 | 17401.9 | 0 | 0 | 0 | 0 | 15300 | 5285.28 | 0 | 20585.28 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3728.88 | 0 | 33228.88 | 0 | 0 | 0 | 0 | 32500 | 5609.53 | 0 | 38109.53 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4474.65 | 0 | 36474.65 | 0 | 0 | 0 | 0 | 35200 | 6744.4 | 0 | 41944.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5317.7 | 0 | 41017.7 | 0 | 0 | 0 | 0 | 39300 | 8008.98 | 0 | 47308.98 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7101.08 | 0 | 51001.08 | 0 | 0 | 0 | 0 | 48200 | 10667.83 | 0 | 58867.83 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 8852.03 | 0 | 58752.03 | 0 | 0 | 0 | 0 | 55000 | 13359.1 | 0 | 68359.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 10635.4 | 0 | 70135.4 | 0 | 0 | 0 | 0 | 65500 | 16082.8 | 0 | 81582.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 12451.2 | 0 | 89951.2 | 0 | 0 | 0 | 0 | 85000 | 18806.5 | 0 | 103806.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 14656.1 | 0 | 121656.1 | 0 | 0 | 0 | 0 | 118000 | 22049 | 0 | 140049 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Redding | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 17768.9 | 0 | 143268.9 | 0 | 0 | 0 | 0 | 138000 | 26718.2 | 0 | 164718.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / REDDING (960)
Bakersfield | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1697.8 | 0 | 4497.8 | 0 | 0 | 0 | 0 | 3075 | 2546.7 | 0 | 5621.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1959 | 0 | 5284 | 0 | 0 | 0 | 0 | 3650 | 2938.5 | 0 | 6588.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2122.25 | 0 | 6497.25 | 0 | 0 | 0 | 0 | 4800 | 3167.05 | 0 | 7967.05 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2285.5 | 0 | 7285.5 | 0 | 0 | 0 | 0 | 5475 | 3428.25 | 0 | 8903.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2383.45 | 0 | 8208.45 | 0 | 0 | 0 | 0 | 6400 | 3591.5 | 0 | 9991.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2579.35 | 0 | 9654.35 | 0 | 0 | 0 | 0 | 7775 | 3885.35 | 0 | 11660.35 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2775.25 | 0 | 11925.25 | 0 | 0 | 0 | 0 | 10100 | 4146.55 | 0 | 14246.55 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 2905.85 | 0 | 13305.85 | 0 | 0 | 0 | 0 | 11400 | 4407.75 | 0 | 15807.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3232.35 | 0 | 16332.35 | 0 | 0 | 0 | 0 | 14400 | 4864.85 | 0 | 19264.85 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3526.2 | 0 | 17426.2 | 0 | 0 | 0 | 0 | 15300 | 5321.95 | 0 | 20621.95 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3754.75 | 0 | 33254.75 | 0 | 0 | 0 | 0 | 32500 | 5648.45 | 0 | 38148.45 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4505.7 | 0 | 36505.7 | 0 | 0 | 0 | 0 | 35200 | 6791.2 | 0 | 41991.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5354.6 | 0 | 41054.6 | 0 | 0 | 0 | 0 | 39300 | 8064.55 | 0 | 47364.55 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7150.35 | 0 | 51050.35 | 0 | 0 | 0 | 0 | 48200 | 10741.85 | 0 | 58941.85 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 8913.45 | 0 | 58813.45 | 0 | 0 | 0 | 0 | 55000 | 13451.8 | 0 | 68451.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 10709.2 | 0 | 70209.2 | 0 | 0 | 0 | 0 | 65500 | 16194.4 | 0 | 81694.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 12537.6 | 0 | 90037.6 | 0 | 0 | 0 | 0 | 85000 | 18937 | 0 | 103937 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 14757.8 | 0 | 121757.8 | 0 | 0 | 0 | 0 | 118000 | 22202 | 0 | 140202 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Bakersfield | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 17892.2 | 0 | 143392.2 | 0 | 0 | 0 | 0 | 138000 | 26903.6 | 0 | 164903.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / BAKERSFIELD (932-933)
Sacramento | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1714.7 | 0 | 4514.7 | 0 | 0 | 0 | 0 | 3075 | 2572.05 | 0 | 5647.05 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1978.5 | 0 | 5303.5 | 0 | 0 | 0 | 0 | 3650 | 2967.75 | 0 | 6617.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2143.38 | 0 | 6518.38 | 0 | 0 | 0 | 0 | 4800 | 3198.58 | 0 | 7998.58 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2308.25 | 0 | 7308.25 | 0 | 0 | 0 | 0 | 5475 | 3462.38 | 0 | 8937.38 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2407.18 | 0 | 8232.18 | 0 | 0 | 0 | 0 | 6400 | 3627.25 | 0 | 10027.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2605.03 | 0 | 9680.03 | 0 | 0 | 0 | 0 | 7775 | 3924.03 | 0 | 11699.03 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2802.88 | 0 | 11952.88 | 0 | 0 | 0 | 0 | 10100 | 4187.83 | 0 | 14287.83 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 2934.78 | 0 | 13334.78 | 0 | 0 | 0 | 0 | 11400 | 4451.63 | 0 | 15851.63 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3264.53 | 0 | 16364.53 | 0 | 0 | 0 | 0 | 14400 | 4913.28 | 0 | 19313.28 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3561.3 | 0 | 17461.3 | 0 | 0 | 0 | 0 | 15300 | 5374.93 | 0 | 20674.93 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3792.13 | 0 | 33292.13 | 0 | 0 | 0 | 0 | 32500 | 5704.68 | 0 | 38204.68 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4550.55 | 0 | 36550.55 | 0 | 0 | 0 | 0 | 35200 | 6858.8 | 0 | 42058.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5407.9 | 0 | 41107.9 | 0 | 0 | 0 | 0 | 39300 | 8144.83 | 0 | 47444.83 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7221.53 | 0 | 51121.53 | 0 | 0 | 0 | 0 | 48200 | 10848.78 | 0 | 59048.78 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 9002.18 | 0 | 58902.18 | 0 | 0 | 0 | 0 | 55000 | 13585.7 | 0 | 68585.7 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 10815.8 | 0 | 70315.8 | 0 | 0 | 0 | 0 | 65500 | 16355.6 | 0 | 81855.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 12662.4 | 0 | 90162.4 | 0 | 0 | 0 | 0 | 85000 | 19125.5 | 0 | 104125.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 14904.7 | 0 | 121904.7 | 0 | 0 | 0 | 0 | 118000 | 22423 | 0 | 140423 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
Sacramento | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 18070.3 | 0 | 143570.3 | 0 | 0 | 0 | 0 | 138000 | 27171.4 | 0 | 165171.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SACRAMENTO (942,956-958)
San Diego | 0 | 237433101100 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1687.4 | 0 | 4487.4 | 0 | 0 | 0 | 0 | 3075 | 2531.1 | 0 | 5606.1 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101120 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1947 | 0 | 5272 | 0 | 0 | 0 | 0 | 3650 | 2920.5 | 0 | 6570.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101140 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2109.25 | 0 | 6484.25 | 0 | 0 | 0 | 0 | 4800 | 3147.65 | 0 | 7947.65 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101145 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.52 | 30.77 | Ea. | 5000 | 2271.5 | 0 | 7271.5 | 0 | 0 | 0 | 0 | 5475 | 3407.25 | 0 | 8882.25 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101150 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.5 | 32.26 | Ea. | 5825 | 2368.85 | 0 | 8193.85 | 0 | 0 | 0 | 0 | 6400 | 3569.5 | 0 | 9969.5 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101156 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.46 | 34.78 | Ea. | 7075 | 2563.55 | 0 | 9638.55 | 0 | 0 | 0 | 0 | 7775 | 3861.55 | 0 | 11636.55 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101160 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.67 | 35.98 | Ea. | 9150 | 2758.25 | 0 | 11908.25 | 0 | 0 | 0 | 0 | 10100 | 4121.15 | 0 | 14221.15 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101170 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.63 | 37.98 | Ea. | 10400 | 2888.05 | 0 | 13288.05 | 0 | 0 | 0 | 0 | 11400 | 4380.75 | 0 | 15780.75 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101180 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.57 | 42.03 | Ea. | 13100 | 3212.55 | 0 | 16312.55 | 0 | 0 | 0 | 0 | 14400 | 4835.05 | 0 | 19235.05 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101190 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | Q6 | 0.52 | 45.89 | Ea. | 13900 | 3504.6 | 0 | 17404.6 | 0 | 0 | 0 | 0 | 15300 | 5289.35 | 0 | 20589.35 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101200 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.67 | 47.98 | Ea. | 29500 | 3731.75 | 0 | 33231.75 | 0 | 0 | 0 | 0 | 32500 | 5613.85 | 0 | 38113.85 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101210 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.56 | 57.55 | Ea. | 32000 | 4478.1 | 0 | 36478.1 | 0 | 0 | 0 | 0 | 35200 | 6749.6 | 0 | 41949.6 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101220 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.47 | 68.38 | Ea. | 35700 | 5321.8 | 0 | 41021.8 | 0 | 0 | 0 | 0 | 39300 | 8015.15 | 0 | 47315.15 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101240 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.35 | 91.17 | Ea. | 43900 | 7106.55 | 0 | 51006.55 | 0 | 0 | 0 | 0 | 48200 | 10676.05 | 0 | 58876.05 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101260 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.28 | 114 | Ea. | 49900 | 8858.85 | 0 | 58758.85 | 0 | 0 | 0 | 0 | 55000 | 13369.4 | 0 | 68369.4 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101265 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.23 | 137 | Ea. | 59500 | 10643.6 | 0 | 70143.6 | 0 | 0 | 0 | 0 | 65500 | 16095.2 | 0 | 81595.2 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101270 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.2 | 160 | Ea. | 77500 | 12460.8 | 0 | 89960.8 | 0 | 0 | 0 | 0 | 85000 | 18821 | 0 | 103821 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101275 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.17 | 188 | Ea. | 107000 | 14667.4 | 0 | 121667.4 | 0 | 0 | 0 | 0 | 118000 | 22066 | 0 | 140066 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)
San Diego | 0 | 237433101280 |  |  | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | Q7 | 0.14 | 229 | Ea. | 125500 | 17782.6 | 0 | 143282.6 | 0 | 0 | 0 | 0 | 138000 | 26738.8 | 0 | 164738.8 | 0 | 0 | 0 | 0 | STD | Year 2018 | CALIFORNIA / SAN DIEGO (919-921)

## HVAC Labor_Union pivot
Location | Description | Sum of Labor Hours | Sum of Labor | 82.3457 | Average labor rate ($/hour)
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 3833.5 | 106.5453 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 24714.8 | 107.9249 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 4013.9 | 105.6846 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 4464.9 | 106.2313 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 4870.8 | 106.1408 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 5186.5 | 108.0971 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 6223.8 | 108.146 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 2345.2 | 102.5897 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 7396.4 | 108.1661 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 2706 | 102.5 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 9876.9 | 108.335 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2931.5 | 102.7875 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 12312.3 | 108.0026 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 3157 | 102.5999 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 14792.8 | 107.9766 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 3292.3 | 102.0552 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 3562.9 | 102.4411 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 17318.4 | 108.24 | San Francisco
San Francisco | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 20385.2 | 108.4319 | San Francisco
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 3442.5 | 95.6782 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 22194 | 96.917 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 3604.5 | 94.9052 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 4009.5 | 95.3961 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 4374 | 95.3149 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 4657.5 | 97.0717 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 5589 | 97.1156 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 2106 | 92.126 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 6642 | 97.1337 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 2430 | 92.0455 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 8869.5 | 97.2853 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2632.5 | 92.3036 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 11056.5 | 96.9868 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2835 | 92.1352 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 13284 | 96.9635 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2956.5 | 91.646 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 3199.5 | 91.9925 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 15552 | 97.2 | San Jose
San Jose | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 18306 | 97.3723 | San Jose
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2898.5 | 80.5586 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 18686.8 | 81.6017 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 3034.9 | 79.9078 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3375.9 | 80.3212 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3682.8 | 80.2528 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3921.5 | 81.732 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4705.8 | 81.7689 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1773.2 | 77.5678 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5592.4 | 81.7841 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 2046 | 77.5 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7467.9 | 81.9118 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2216.5 | 77.7174 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 9309.3 | 81.6605 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2387 | 77.5756 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 11184.8 | 81.6409 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2489.3 | 77.1637 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2693.9 | 77.4554 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 13094.4 | 81.84 | Los Angeles
Los Angeles | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 15413.2 | 81.9851 | Los Angeles
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2802.88 | 77.9011 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 18070.3 | 78.9096 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2934.78 | 77.2717 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3264.53 | 77.6714 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3561.3 | 77.6051 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3792.13 | 79.0356 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4550.55 | 79.0712 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1714.7 | 75.0087 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5407.9 | 79.086 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1978.5 | 74.9432 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7221.53 | 79.2095 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2143.38 | 75.1536 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 9002.18 | 78.9665 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2308.25 | 75.0162 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10815.8 | 78.9474 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2407.18 | 74.6181 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2605.03 | 74.9002 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12662.4 | 79.14 | Fresno
Fresno | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14904.7 | 79.2803 | Fresno
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2947.38 | 81.9172 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 19001.9 | 82.9777 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 3086.08 | 81.2554 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3432.83 | 81.6757 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3744.9 | 81.606 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3987.63 | 83.1103 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4785.15 | 83.1477 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1803.1 | 78.8758 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5686.7 | 83.1632 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 2080.5 | 78.8068 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7593.83 | 83.2931 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2253.88 | 79.0281 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 9466.28 | 83.0375 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2427.25 | 78.8837 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 11373.4 | 83.0175 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2531.28 | 78.465 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2739.33 | 78.7616 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 13315.2 | 83.22 | Anaheim
Anaheim | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 15673.1 | 83.3676 | Anaheim
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2779.5 | 77.2513 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 17919.6 | 78.2515 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2910.3 | 76.6272 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3237.3 | 77.0236 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3531.6 | 76.9579 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3760.5 | 78.3764 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4512.6 | 78.4118 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1700.4 | 74.3832 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5362.8 | 78.4264 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1962 | 74.3182 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7161.3 | 78.5489 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2125.5 | 74.5266 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 8927.1 | 78.3079 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2289 | 74.3906 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10725.6 | 78.2891 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2387.1 | 73.9957 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2583.3 | 74.2754 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12556.8 | 78.48 | Long Beach
Long Beach | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14780.4 | 78.6191 | Long Beach
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2756.13 | 76.6017 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 17768.9 | 77.5934 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2885.83 | 75.9829 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3210.08 | 76.3759 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3501.9 | 76.3107 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3728.88 | 77.7174 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4474.65 | 77.7524 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1686.1 | 73.7577 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5317.7 | 77.7669 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1945.5 | 73.6932 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7101.08 | 77.8883 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2107.63 | 73.9001 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 8852.03 | 77.6494 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2269.75 | 73.765 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10635.4 | 77.6307 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2367.03 | 73.3735 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2561.58 | 73.6509 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12451.2 | 77.82 | Redding
Redding | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14656.1 | 77.958 | Redding
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2775.25 | 77.1331 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 17892.2 | 78.1319 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2905.85 | 76.51 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3232.35 | 76.9058 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3526.2 | 76.8403 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3754.75 | 78.2566 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4505.7 | 78.2919 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1697.8 | 74.2695 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5354.6 | 78.3065 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1959 | 74.2045 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7150.35 | 78.4288 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2122.25 | 74.4127 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 8913.45 | 78.1882 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2285.5 | 74.2769 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10709.2 | 78.1693 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2383.45 | 73.8825 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2579.35 | 74.1619 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12537.6 | 78.36 | Bakersfield
Bakersfield | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14757.8 | 78.4989 | Bakersfield
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2802.88 | 77.9011 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 18070.3 | 78.9096 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2934.78 | 77.2717 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3264.53 | 77.6714 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3561.3 | 77.6051 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3792.13 | 79.0356 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4550.55 | 79.0712 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1714.7 | 75.0087 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5407.9 | 79.086 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1978.5 | 74.9432 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7221.53 | 79.2095 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2143.38 | 75.1536 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 9002.18 | 78.9665 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2308.25 | 75.0162 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10815.8 | 78.9474 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2407.18 | 74.6181 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2605.03 | 74.9002 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12662.4 | 79.14 | Sacramento
Sacramento | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14904.7 | 79.2803 | Sacramento
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 10 ton cooling, 200 MBH heating, includes, standard controls, curb and economizer | 35.98 | 2758.25 | 76.6606 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 100 ton cooling, 1,350 MBH heating, includes, standard controls, curb and economizer | 229 | 17782.6 | 77.6533 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 12.5 ton cooling, 230 MBH heating, includes, standard controls, curb and economizer | 37.98 | 2888.05 | 76.0413 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 15 ton cooling, 270 MBH heating, includes, standard controls, curb and economizer | 42.03 | 3212.55 | 76.4347 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 18 ton cooling, 330 MBH heating, includes, standard controls, curb and economizer | 45.89 | 3504.6 | 76.3696 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 20 ton cooling, 360 MBH heating, includes, standard controls, curb and economizer | 47.98 | 3731.75 | 77.7772 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 25 ton cooling, 450 MBH heating, includes, standard controls, curb and economizer | 57.55 | 4478.1 | 77.8123 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | 22.86 | 1687.4 | 73.8145 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 30 ton cooling, 540 MBH heating, includes, standard controls, curb and economizer | 68.38 | 5321.8 | 77.8268 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | 26.4 | 1947 | 73.75 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 40 ton cooling, 675 MBH heating, includes, standard controls, curb and economizer | 91.17 | 7106.55 | 77.9483 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | 28.52 | 2109.25 | 73.9569 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 50 ton cooling, 810 MBH heating, includes, standard controls, curb and economizer | 114 | 8858.85 | 77.7092 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 6 ton cooling, 140 MBH heating, includes, standard controls, curb and economizer | 30.77 | 2271.5 | 73.8219 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 60 ton cooling, 900 MBH heating, includes, standard controls, curb and economizer | 137 | 10643.6 | 77.6905 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 7.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 32.26 | 2368.85 | 73.4299 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 8.5 ton cooling, 170 MBH heating, includes, standard controls, curb and economizer | 34.78 | 2563.55 | 73.7076 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 80 ton cooling, 1,000 MBH heating, includes, standard controls, curb and economizer | 160 | 12460.8 | 77.88 | San Diego
San Diego | Rooftop air conditioner, single zone, electric cool, gas heat, 90 ton cooling, 1,200 MBH heating, includes, standard controls, curb and economizer | 188 | 14667.4 | 78.0181 | San Diego

## Contractor responses
Diagnosed Malfunction
Required
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours) | [14 empty] | Average Hours | Tonnage Midpoint | Weighting Factor | Labor $ | Labor $/ton
Economizer Repair | Replace worn/damaged economizer damper linkage |  | Contractor1 | Contractor2 Adjustment | Contractor2 Hour Estimate | Contractor3 Adjustment | Contractor3 Hour Estimate | Contractor4 Adjustment | Contractor4 Hour Estimate | Contractor5 Adjustment | Contractor5 Hour Estimate | Contractor6 Adjustment | Contractor6 Hour Estimate | Contractor7 Adjustment | Contractor7 Hour Estimate | Contractor8 Adjustment | Contractor8 Hour Estimate
| Replace linkage | 2-5 Tons | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 1.125 | 3.5 | 1852 | 92.639 | 19.3217
| Replace linkage | 6-20 Tons | 1.5 | 0 | 1.5 | 0.5 | 2 | 0.45 | 1.95 | 0 | 1.5 | 0.25 | 1.75 | 0 | 1.5 | 0 | 1.5 | 1.65 | 13 | 614 | 135.8705 | 2.5295
| Replace linkage | 25-30 Tons | 2 | 0 | 2 | 0.5 | 2.5 | 1 | 3 | 0 | 2 | 0.25 | 2.25 | 0 | 2 | 0 | 2 | 2.2188 | 27.5 | 1 | 182.7046 | 0.0026188
| Replace linkage | 35-50 Tons | 2.5 | 0 | 2.5 | 0.5 | 3 | 1 | 3.5 | 0 | 2.5 | 0.25 | 2.75 | 0 | 2.5 | 0 | 2.5 | 2.7188 | 42.5 | 32 | 223.8775 | 0.066443
| Replace linkage | > 50 Tons | 3 | 0 | 3 | 0.5 | 3.5 | 0 | 3 | 0 | 3 | 0.5 | 3.5 | 0 | 3 | 0 | 3 | 3.125 | 75 | 38 | 257.3305 | 0.051392
21.9717
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3.5 | 1852 | 82.3457 | 17.1749
|  | 6-20 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0.5 | 1.5 | 1.125 | 13 | 614 | 92.639 | 1.7246
|  | 25-30 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0.5 | 2 | 0 | 1.5 | 0.5 | 2 | 1.625 | 27.5 | 1 | 133.8118 | 0.001918
|  | 35-50 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0.5 | 2 | 0 | 1.5 | 0.5 | 2 | 1.625 | 42.5 | 32 | 133.8118 | 0.039713
|  | >50 Tons | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0.5 | 2.5 | 0 | 2 | 0.5 | 2.5 | 2.125 | 75 | 38 | 174.9847 | 0.034946
18.9761
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 3.5 | 1852 | 164.6915 | 34.3498
| Wiring only - no circuit boards | 6-20 Tons | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 13 | 614 | 164.6915 | 3.066
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | 0 | 2.5 | 0 | 2.5 | 0 | 2.5 | 0 | 2.5 | 0.25 | 2.75 | 0 | 2.5 | 0 | 2.5 | 2.5312 | 27.5 | 1 | 208.4377 | 0.0029876
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | 0 | 2.5 | 0 | 2.5 | 0 | 2.5 | 0 | 2.5 | 0.25 | 2.75 | 0 | 2.5 | 0 | 2.5 | 2.5312 | 42.5 | 32 | 208.4377 | 0.061861
| Wiring only - no circuit boards | > 50 Tons | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0.25 | 3.25 | 0 | 3 | 0 | 3 | 3.0312 | 75 | 38 | 249.6106 | 0.04985
37.5305
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | 3 | 3 | 1 | 3 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2.25 | 3.5 | 1852 | 185.2779 | 38.6435
|  | 6-20 Tons | 2 | 3 | 3 | 1 | 3 | 2 | 4 | 0 | 2 | 0 | 2 | 0.5 | 2.5 | 0 | 2 | 2.5625 | 13 | 614 | 211.011 | 3.9283
|  | 25-30 Tons | 3 | 4.5 | 4.5 | 1 | 4 | 1.5 | 4.5 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 3.5 | 27.5 | 1 | 288.2101 | 0.004131
|  | 35-50 Tons | 3 | 6 | 6 | 1 | 4 | 1.5 | 4.5 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 3.6875 | 42.5 | 32 | 303.65 | 0.090118
|  | > 50 Tons | 5 | 15 | 15 | 1 | 6 | 2.5 | 7.5 | 6 | 6 | 0.75 | 5.75 | 0 | 5 | 0 | 5 | 6.9062 | 75 | 38 | 568.7003 | 0.11358
42.7796
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3.5 | 1852 | 82.3457 | 17.1749
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 13 | 614 | 82.3457 | 1.533
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | 2.25 | 2.25 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.5938 | 27.5 | 1 | 131.2385 | 0.0018811
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | 2.625 | 2.625 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.6406 | 42.5 | 32 | 135.0985 | 0.040095
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | 3.5 | 3.5 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2.1875 | 75 | 38 | 180.1313 | 0.035974
18.7858
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1.0625 | 3.5 | 1852 | 87.4924 | 18.2483
|  | 6-20 Tons | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1.0625 | 13 | 614 | 87.4924 | 1.6288
|  | 25-30 Tons | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1.0625 | 27.5 | 1 | 87.4924 | 0.0012541
|  | 35-50 Tons | 1.5 | 0 | 1.5 | 0.5 | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.5625 | 42.5 | 32 | 128.6652 | 0.038186
|  | > 50 Tons | 2 | 0 | 2 | 0.5 | 2.5 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2.0625 | 75 | 38 | 169.8381 | 0.033919
19.9505
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3.5 | 1852 | 82.3457 | 17.1749
|  | 6-20 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 13 | 614 | 82.3457 | 1.533
|  | 25-30 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.5 | 27.5 | 1 | 123.5186 | 0.0017704
|  | 35-50 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.5 | 42.5 | 32 | 123.5186 | 0.036658
|  | > 50 Tons | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 1.5 | 1.5 | 0 | 2 | 0 | 2 | 0 | 2 | 1.9375 | 75 | 38 | 159.5449 | 0.031863
18.7782
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0.25 | 3.25 | 0 | 3 | 0 | 3 | 3.0312 | 3.5 | 1852 | 249.6106 | 52.0613
| ADEC upgrade | 6-20 Tons | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0.25 | 3.25 | 0 | 3 | 0 | 3 | 3.0312 | 13 | 614 | 249.6106 | 4.6469
| ADEC upgrade | 25-30 Tons | 3.5 | 3.5 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0.25 | 3.75 | 0 | 3.5 | 0 | 3.5 | 3.5312 | 27.5 | 1 | 290.7834 | 0.0041679
| ADEC upgrade | 35-50 Tons | 3.5 | 3.5 | 3.5 | 1 | 4.5 | 0 | 3.5 | 0 | 3.5 | 0.25 | 3.75 | 0 | 3.5 | 0 | 3.5 | 3.6562 | 42.5 | 32 | 301.0766 | 0.089355
| ADEC upgrade | > 50 Tons | 4 | 6 | 6 | 1 | 5 | 0 | 4 | 0 | 4 | 0.25 | 4.25 | 0 | 4 | 0 | 4 | 4.4062 | 75 | 38 | 362.836 | 0.072462
56.8743
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | 0 | 3 | 1 | 4 | 0 | 3 | 4 | 4 | 0.33 | 3.33 | 0 | 3 | 0 | 3 | 3.2912 | 3.5 | 1852 | 271.0204 | 56.5268
| Add VFD to ADEC | 6-20 Tons | 3 | 0 | 3 | 1 | 4 | 0 | 3 | 4 | 4 | 0.33 | 3.33 | 0 | 3 | 0 | 3 | 3.2912 | 13 | 614 | 271.0204 | 5.0455
| Add VFD to ADEC | 25-30 Tons | 4 | 0 | 4 | 1 | 5 | 0 | 4 | 6 | 6 | 0.33 | 4.33 | 0 | 4 | 0 | 4 | 4.4162 | 27.5 | 1 | 363.6594 | 0.0052124
| Add VFD to ADEC | 35-50 Tons | 4 | 0 | 4 | 1 | 5 | 0 | 4 | 6 | 6 | 0.33 | 4.33 | 0 | 4 | 0 | 4 | 4.4162 | 42.5 | 32 | 363.6594 | 0.10793
| Add VFD to ADEC | > 50 Tons | 5 | 0 | 5 | 1 | 6 | 0 | 5 | 6 | 6 | 0.33 | 5.33 | 0 | 5 | 0 | 5 | 5.2912 | 75 | 38 | 435.7119 | 0.087016
61.7725
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 |  | 1.5 | 2 | 2 | 0.35 | 1.85 | 0 | 1.5 | 0 | 1.5 | 1.6062 | 3.5 | 1852 | 132.2679 | 27.5871
| Add DCV to ADEC | 6-20 Tons | 1.5 | 0 | 1.5 | 0 | 1.5 |  | 1.5 | 2 | 2 | 0.35 | 1.85 | 0 | 1.5 | 0 | 1.5 | 1.6062 | 13 | 614 | 132.2679 | 2.4624
| Add DCV to ADEC | 25-30 Tons | 2 | 0 | 2 | 0 | 2 |  | 2 | 3 | 3 | 0.5 | 2.5 | 0 | 2 | 0 | 2 | 2.1875 | 27.5 | 1 | 180.1313 | 0.0025819
| Add DCV to ADEC | 35-50 Tons | 2 | 0 | 2 | 0 | 2 |  | 2 | 3 | 3 | 0.5 | 2.5 | 0 | 2 | 0 | 2 | 2.1875 | 42.5 | 32 | 180.1313 | 0.05346
| Add DCV to ADEC | > 50 Tons | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 3 | 75 | 38 | 247.0372 | 0.049336
30.1549
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 3.5 | 1852 | 82.3457 | 17.1749
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 13 | 614 | 82.3457 | 1.533
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | 1.5 | 1.5 | 0 | 1.5 | 0 | 1.5 | 2 | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.5625 | 27.5 | 1 | 128.6652 | 0.0018442
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | 2.25 | 2.25 | 0 | 1.5 | 0 | 1.5 | 2 | 2 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 1.6562 | 42.5 | 32 | 136.3851 | 0.040477
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | 4 | 4 | 0 | 2 | 0 | 2 | 3 | 3 | 0 | 2 | 0 | 2 | 0 | 2 | 2.375 | 75 | 38 | 195.5712 | 0.039058
18.7893
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 1.1875 | 3.5 | 1852 | 97.7856 | 20.3952
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 | 1.5 | 1.5 | 1 | 2 |  | 1 | 1 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 1.25 | 13 | 614 | 102.9322 | 1.9163
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 | 2.25 | 2.25 | 1.5 | 3 |  | 1.5 | 2 | 2 | 0.5 | 2 | 0 | 1.5 | 0 | 1.5 | 1.9062 | 27.5 | 1 | 156.9716 | 0.0022499
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 | 2.25 | 2.25 | 1.5 | 3 |  | 1.5 | 2 | 2 | 0.5 | 2 | 0 | 1.5 | 0.5 | 2 | 1.9688 | 42.5 | 32 | 162.1182 | 0.048114
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 | 3 | 3 | 2 | 4 |  | 2 | 3 | 3 | 0.5 | 2.5 | 0 | 2 | 1 | 3 | 2.6875 | 75 | 38 | 221.3042 | 0.044197
22.406
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0.875 | 3.5 | 1852 | 72.0525 | 15.028
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0.5 | 1.5 | 0.9375 | 13 | 614 | 77.1991 | 1.4372
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | 0 | 0 | 0.5 | 1.5 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0.5 | 1.5 | 1 | 27.5 | 1 | 82.3457 | 0.0011803
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | 0 | 0 | 0.5 | 1.5 | 0 | 1 | 1.5 | 1.5 | 0 | 1 | 0 | 1 | 0.5 | 1.5 | 1.0625 | 42.5 | 32 | 87.4924 | 0.025966
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 | 0 | 0 | 0.5 | 2 | 0 | 1.5 | 2 | 2 | 0.33 | 1.83 | 0 | 1.5 | 1 | 2.5 | 1.6038 | 75 | 38 | 132.062 | 0.026374
16.5187
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2 | 3.5 | 1969 | 164.6915 | 36.5198
| Two stages | 7-20 Tons | 2 | 0 | 2 | 0.5 | 2.5 |  | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 2.0625 | 13 | 477 | 169.8381 | 2.4563
| Three or four stages | 15-20 Tons | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 3 | 27.5 | 20 | 247.0372 | 0.070817
| Three or four stages | 25-30 Tons | 3 | 0 | 3 | 0.5 | 3.5 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 3 | 3.0625 | 42.5 | 1 | 252.1839 | 0.0023389
| Four stages | 35-50 Tons | 3.5 | 0 | 3.5 | 0.5 | 4 | 0 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0 | 3.5 | 3.5625 | 75 | 32 | 293.3567 | 0.049336
| Four stages | > 50 Tons | 4 | 0 | 4 | 0.5 | 4.5 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 0 | 4 | 4.0625 | 75 | 38 | 334.5296 | 0.066809
39.1654
| Refrigerant Retail Price ($/lb) | [20 empty] | Materials $/ton
| R-22 |  | 125 | 0 | 125 | 0 | 125 |  | 125 | 0 | 125 | 0 | 125 | 0 | 125 | 0 | 125 | 125 |  | 0.4488 |  | 56.1006
| R-410A |  | 65 | 0 | 65 | 0 | 65 |  | 65 | 0 | 65 | 0 | 65 | 0 | 65 | 0 | 65 | 65 |  | 0.5506 |  | 35.7893
| 407C |  |  |  |  | 0 | 65 | [5 empty] | 75 |  |  |  |  | 70 |  | 0.00059014 |  | 0.04131
| insert refrigerant used if other | [20 empty] | 91.9312
Unoccupied Fan Control | Programmable thermostat Adjustment | [19 empty] | Labor $ | Labor $/ton
| Program thermostat to match occupancy | All Sizes | 1 | 0 | 1 | 0 | 1 |  | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0.25 |  |  | 20.5864 | 2.9281
[12 empty] | 0 | 0 | 0 | 0
Programmable Thermostat | Install & Program Progrmmable thermostat | [10 empty] | 0 | 0 | 0 | 0
| Install Title-24-approved programmable thermostat | All Sizes | 1 | 0 | 1 | 0.5 | 1.5 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1.0625 |  |  | 87.4924 | 12.4443
Note on S111: Phil Jordan: Assume 15 minutes to perform adjustment

## Contractor1_responses
Diagnosed Malfunction
|  |  | Required | Optional
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours) | Labor Rate ($) | Est. Parts Sell Price ($) | Typical Materials Markup (%) | Tonnage Midpoint | Weighting Factor | Labor $ | Labor $/ton
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
| Replace linkage | 6-20 Tons | 1.5 |  |  |  | 13 | 614 | 123.5186 | 2.2995
| Replace linkage | 25-30 Tons | 2 |  |  |  | 27.5 | 1 | 164.6915 | 0.0023606
| Replace linkage | 35-50 Tons | 2.5 |  |  |  | 42.5 | 32 | 205.8644 | 0.061097
| Replace linkage | > 50 Tons | 3 |  |  |  | 75 | 38 | 247.0372 | 0.049336
19.5872
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
|  | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
|  | 25-30 Tons | 1.5 |  |  |  | 27.5 | 1 | 123.5186 | 0.0017704
|  | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
|  | >50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7792
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 |  |  |  | 3.5 | 1852 | 164.6915 | 34.3498
| Wiring only - no circuit boards | 6-20 Tons | 2 |  |  |  | 13 | 614 | 164.6915 | 3.066
| Wiring only - no circuit boards | 25-30 Tons | 2.5 |  |  |  | 27.5 | 1 | 205.8644 | 0.0029507
| Wiring only - no circuit boards | 35-50 Tons | 2.5 |  |  |  | 42.5 | 32 | 205.8644 | 0.061097
| Wiring only - no circuit boards | > 50 Tons | 3 |  |  |  | 75 | 38 | 247.0372 | 0.049336
37.5292
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 |  |  |  | 3.5 | 1852 | 164.6915 | 34.3498
|  | 6-20 Tons | 2 |  |  |  | 13 | 614 | 164.6915 | 3.066
|  | 25-30 Tons | 3 |  |  |  | 27.5 | 1 | 247.0372 | 0.0035409
|  | 35-50 Tons | 3 |  |  |  | 42.5 | 32 | 247.0372 | 0.073317
|  | > 50 Tons | 5 |  |  |  | 75 | 38 | 411.7287 | 0.082227
37.5749
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 |  |  |  | 27.5 | 1 | 123.5186 | 0.0017704
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7792
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
|  | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
|  | 25-30 Tons | 1 |  |  |  | 27.5 | 1 | 82.3457 | 0.0011803
|  | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
|  | > 50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7786
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
|  | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
|  | 25-30 Tons | 1.5 |  |  |  | 27.5 | 1 | 123.5186 | 0.0017704
|  | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
|  | > 50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7792
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 |  |  |  | 3.5 | 1852 | 247.0372 | 51.5246
| ADEC upgrade | 6-20 Tons | 3 |  |  |  | 13 | 614 | 247.0372 | 4.599
| ADEC upgrade | 25-30 Tons | 3.5 |  |  |  | 27.5 | 1 | 288.2101 | 0.004131
| ADEC upgrade | 35-50 Tons | 3.5 |  |  |  | 42.5 | 32 | 288.2101 | 0.085536
| ADEC upgrade | > 50 Tons | 4 |  |  |  | 75 | 38 | 329.383 | 0.065781
56.2791
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 |  |  |  | 3.5 | 1852 | 247.0372 | 51.5246
| Add VFD to ADEC | 6-20 Tons | 3 |  |  |  | 13 | 614 | 247.0372 | 4.599
| Add VFD to ADEC | 25-30 Tons | 4 |  |  |  | 27.5 | 1 | 329.383 | 0.0047212
| Add VFD to ADEC | 35-50 Tons | 4 |  |  |  | 42.5 | 32 | 329.383 | 0.097756
| Add VFD to ADEC | > 50 Tons | 5 |  |  |  | 75 | 38 | 411.7287 | 0.082227
56.3084
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 |  |  |  | 3.5 | 1852 | 123.5186 | 25.7623
| Add DCV to ADEC | 6-20 Tons | 1.5 |  |  |  | 13 | 614 | 123.5186 | 2.2995
| Add DCV to ADEC | 25-30 Tons | 2 |  |  |  | 27.5 | 1 | 164.6915 | 0.0023606
| Add DCV to ADEC | 35-50 Tons | 2 |  |  |  | 42.5 | 32 | 164.6915 | 0.048878
| Add DCV to ADEC | > 50 Tons | 3 |  |  |  | 75 | 38 | 247.0372 | 0.049336
28.1624
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 |  |  |  | 27.5 | 1 | 123.5186 | 0.0017704
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7792
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 |  |  |  | 27.5 | 1 | 123.5186 | 0.0017704
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 |  |  |  | 42.5 | 32 | 123.5186 | 0.036658
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 |  |  |  | 75 | 38 | 164.6915 | 0.032891
18.7792
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 |  |  |  | 3.5 | 1852 | 82.3457 | 17.1749
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 |  |  |  | 13 | 614 | 82.3457 | 1.533
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 |  |  |  | 27.5 | 1 | 82.3457 | 0.0011803
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 |  |  |  | 42.5 | 32 | 82.3457 | 0.024439
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 |  |  |  | 75 | 38 | 123.5186 | 0.024668
18.7582
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 |  |  |  | 3.5 | 1852 | 164.6915 | 34.3498
| Two stages | 7-20 Tons | 2 |  |  |  | 13 | 614 | 164.6915 | 3.066
| Three or four stages | 15-20 Tons | 3 |  |  |  | 27.5 | 1 | 247.0372 | 0.0035409
| Three or four stages | 25-30 Tons | 3 |  |  |  | 42.5 | 32 | 247.0372 | 0.073317
| Four stages | 35-50 Tons | 3.5 |  |  |  | 75 | 38 | 288.2101 | 0.057559
| Four stages | > 50 Tons | 4 | [6 empty] | 37.5502
Refrigerant Retail Price ($/lb)
| R-22 |  |  | $/lb
| R-410A |  |  | $/lb
$/lb
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | [5 empty] | 82.3457 | 11.7122
Programmable Thermostat | Install & Program Progrmmable thermostat
| Install Title-24-approved programmable thermostat | All Sizes | 1 | [5 empty] | 82.3457 | 11.7122

## Contractor2_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | Yes |  |  | Depends on type | 0 | 1
| Replace linkage | 6-20 Tons | 1.5 | Yes |  |  | Gear driven or blade | 0 | 1.5
| Replace linkage | 25-30 Tons | 2 | Yes |  |  |  | 0 | 2
| Replace linkage | 35-50 Tons | 2.5 | Yes |  |  |  | 0 | 2.5
| Replace linkage | > 50 Tons | 3 | Yes |  |  |  | 0 | 3
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | >50 Tons | 2 | Yes |  |  |  | 0 | 2
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | Yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | Yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | Yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | Yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | Yes |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | No | Yes | 150% | A lot of variables | 3 | 3
|  | 6-20 Tons | 2 | No | Yes | 150% | age, condition, | 3 | 3
|  | 25-30 Tons | 3 | No | Yes | 150% | manufacture | 4.5 | 4.5
|  | 35-50 Tons | 3 | No | Yes | 200% |  | 6 | 6
|  | > 50 Tons | 5 | No | Yes | 300% |  | 15 | 15
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | Yes | No |  | A lot of variables | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | Yes | No |  | age, condition, | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | No | Yes | 150% | changed to 150% | 2.25 | 2.25
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | No | Yes | 175% | changed to 175% | 2.625 | 2.625
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | No | Yes | 175% | changed to 175% | 3.5 | 3.5
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | Yes |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | Yes |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | Yes | No |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | Yes | No |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | No | Yes | 100% |  | 3.5 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | No | Yes | 100% |  | 3.5 | 3.5
| ADEC upgrade | > 50 Tons | 4 | No | Yes | 150% |  | 6 | 6
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | Yes |  |  |  | 0 | 3
| Add VFD to ADEC | 6-20 Tons | 3 | Yes |  |  |  | 0 | 3
| Add VFD to ADEC | 25-30 Tons | 4 | Yes |  |  |  | 0 | 4
| Add VFD to ADEC | 35-50 Tons | 4 | Yes |  |  |  | 0 | 4
| Add VFD to ADEC | > 50 Tons | 5 | Yes |  |  |  | 0 | 5
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
| Add DCV to ADEC | 6-20 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
| Add DCV to ADEC | 25-30 Tons | 2 | Yes |  |  |  | 0 | 2
| Add DCV to ADEC | 35-50 Tons | 2 | Yes |  |  |  | 0 | 2
| Add DCV to ADEC | > 50 Tons | 3 | Yes |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | Yes | No |  | Type of coil | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | No | Yes | 100% | Split face? | 1 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | No | Yes | 100% |  | 1.5 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | No | Yes | 150% |  | 2.25 | 2.25
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | No | Yes | 200% |  | 4 | 4
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | Yes | No |  |  | 0 | 1
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 | No | Yes | 150% |  | 1.5 | 1.5
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 | No | Yes | 150% |  | 2.25 | 2.25
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 | No | Yes | 150% |  | 2.25 | 2.25
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 | No | Yes | 150% |  | 3 | 3
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | no |  | 0.5 | Too High | 0 | 0
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | no |  | 0.5 | Too High | 0 | 0
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | no |  | 0.5 | Too High | 0 | 0
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | no |  | 0.5 | Too High | 0 | 0
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 | no |  | 0.5 | Too High | 0 | 0
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | Yes |  |  | Per Circuit? | 0 | 2
| Two stages | 7-20 Tons | 2 | Yes |  |  | Per Circuit? | 0 | 2
| Three or four stages | 15-20 Tons | 3 | Yes |  |  | Per Circuit? | 0 | 3
| Three or four stages | 25-30 Tons | 3 | Yes |  |  | Per Circuit? | 0 | 3
| Four stages | 35-50 Tons | 3.5 | Yes |  |  | Per Circuit? | 0 | 3.5
| Four stages | > 50 Tons | 4 | Yes |  |  | Per Circuit? | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 | Yes |  |  | A little high, but in a | 0 | 125
| R-410A |  | 65 | Yes |  |  | Year it will be low | 0 | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | yes |  |  |  | 0 | 1
Programmable Thermostat | Install & Program Progrmmable thermostat
| Install Title-24-approved programmable thermostat | All Sizes | 1 | yes |  |  |  | 0 | 1

## Contractor3_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | no | add .5 |  |  | 0.5 | 1.5
| Replace linkage | 6-20 Tons | 1.5 | no | add .5 |  |  | 0.5 | 2
| Replace linkage | 25-30 Tons | 2 | no | add .5 |  |  | 0.5 | 2.5
| Replace linkage | 35-50 Tons | 2.5 | no | add .5 |  |  | 0.5 | 3
| Replace linkage | > 50 Tons | 3 | no | add .5 |  |  | 0.5 | 3.5
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | yes |  |  | if repair is possible | 0 | 1
|  | 6-20 Tons | 1 | yes |  |  | if repair is possible | 0 | 1
|  | 25-30 Tons | 1.5 | yes |  |  | if repair is possible | 0 | 1.5
|  | 35-50 Tons | 1.5 | yes |  |  | if repair is possible | 0 | 1.5
|  | >50 Tons | 2 | yes |  |  | if repair is possible | 0 | 2
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | yes |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | no |  | Add 1 hour |  | 1 | 3
|  | 6-20 Tons | 2 | no |  | Add 1 hour |  | 1 | 3
|  | 25-30 Tons | 3 | no |  | Add 1 hour |  | 1 | 4
|  | 35-50 Tons | 3 | no |  | Add 1 hour |  | 1 | 4
|  | > 50 Tons | 5 | no |  | Add 1 hour |  | 1 | 6
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | no |  | Add .5 hour |  | 0.5 | 1.5
|  | 6-20 Tons | 1 | no |  | Add .5 hour |  | 0.5 | 1.5
|  | 25-30 Tons | 1 | no |  | Add .5 hour |  | 0.5 | 1.5
|  | 35-50 Tons | 1.5 | no |  | Add .5 hour |  | 0.5 | 2
|  | > 50 Tons | 2 | no |  | Add .5 hour |  | 0.5 | 2.5
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | yes |  |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | yes |  |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | yes |  |  |  | 0 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | no |  | Add 1 hour |  | 1 | 4.5
| ADEC upgrade | > 50 Tons | 4 | no |  | Add 1 hour |  | 1 | 5
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | no |  | Add 1 hour |  | 1 | 4
| Add VFD to ADEC | 6-20 Tons | 3 | no |  | Add 1 hour |  | 1 | 4
| Add VFD to ADEC | 25-30 Tons | 4 | no |  | Add 1 hour |  | 1 | 5
| Add VFD to ADEC | 35-50 Tons | 4 | no |  | Add 1 hour |  | 1 | 5
| Add VFD to ADEC | > 50 Tons | 5 | no |  | Add 1 hour |  | 1 | 6
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Add DCV to ADEC | 6-20 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Add DCV to ADEC | 25-30 Tons | 2 | yes |  |  |  | 0 | 2
| Add DCV to ADEC | 35-50 Tons | 2 | yes |  |  |  | 0 | 2
| Add DCV to ADEC | > 50 Tons | 3 | yes |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | no |  | Add 1 hour | More difficult for down flow to prevent water entering ducting | 1 | 2
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 | no |  | Add 1 hour | More difficult for down flow to prevent water entering ducting | 1 | 2
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 | no |  | Add 1 hour | More difficult for down flow to prevent water entering ducting | 1.5 | 3
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 | no |  | Add 1 hour | More difficult for down flow to prevent water entering ducting | 1.5 | 3
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 | no |  | Add 1 hour | More difficult for down flow to prevent water entering ducting | 2 | 4
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | no |  | Add .5 hr |  | 0.5 | 1.5
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | no |  | Add .5 hr |  | 0.5 | 1.5
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 | no |  | Add .5 hr |  | 0.5 | 2
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | yes |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 | no |  | Add .5 | more time for 2x the circuits | 0.5 | 2.5
| Three or four stages | 15-20 Tons | 3 | yes |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | no |  | Add .5 |  | 0.5 | 3.5
| Four stages | 35-50 Tons | 3.5 | no |  | Add .5 |  | 0.5 | 4
| Four stages | > 50 Tons | 4 | no |  | Add .5 |  | 0.5 | 4.5
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 | yes |  |  |  | 0 | 125
| R-410A |  | 65 | yes |  |  |  | 0 | 65
| 407C |  | 65 | yes |  |  |  | 0 | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | yes |  |  | assume yes | 0 | 1
Programmable Thermostat | Install & Program Progrmmable thermostat
| Install Title-24-approved programmable thermostat | All Sizes | 1 | no |  | Add .5 | programming is part of installtion | 0.5 | 1.5

## Contractor4_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Replace linkage | 6-20 Tons | 1.5 | no | yes | 30% |  | 0.45 | 1.95
| Replace linkage | 25-30 Tons | 2 | no | yes | 50% |  | 1 | 3
| Replace linkage | 35-50 Tons | 2.5 | no | yes | 40% |  | 1 | 3.5
| Replace linkage | > 50 Tons | 3 | yes | no |  |  | 0 | 3
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
|  | >50 Tons | 2 | yes |  |  |  | 0 | 2
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | Yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | Yes |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | Yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | Yes |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | Yes |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | Yes | no |  |  | 0 | 2
|  | 6-20 Tons | 2 | no | yes | 100% |  | 2 | 4
|  | 25-30 Tons | 3 | no | yes | 50% |  | 1.5 | 4.5
|  | 35-50 Tons | 3 | no | yes | 50% |  | 1.5 | 4.5
|  | > 50 Tons | 5 | no | yes | 50% |  | 2.5 | 7.5
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | yes |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | Yes |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | yes |  |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | yes |  |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | yes |  |  |  | 0 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | yes |  |  |  | 0 | 3.5
| ADEC upgrade | > 50 Tons | 4 | yes |  |  |  | 0 | 4
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | yes |  |  |  | 0 | 3
| Add VFD to ADEC | 6-20 Tons | 3 | yes |  |  |  | 0 | 3
| Add VFD to ADEC | 25-30 Tons | 4 | yes |  |  |  | 0 | 4
| Add VFD to ADEC | 35-50 Tons | 4 | yes |  |  |  | 0 | 4
| Add VFD to ADEC | > 50 Tons | 5 | yes |  |  |  | 0 | 5
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 |  | yes | 100% |  |  | 1.5
| Add DCV to ADEC | 6-20 Tons | 1.5 |  | yes | 100% |  |  | 1.5
| Add DCV to ADEC | 25-30 Tons | 2 |  | yes | 50% |  |  | 2
| Add DCV to ADEC | 35-50 Tons | 2 |  | yes | 50% |  |  | 2
| Add DCV to ADEC | > 50 Tons | 3 | yes |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | yes |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | yes |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | yes |  |  |  | 0 | 2
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | yes |  |  |  | 0 | 1
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 |  | yes | 100% |  |  | 1
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 |  | yes | 100% |  |  | 1.5
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 |  | yes | 250% |  |  | 1.5
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 |  | yes | 250% |  |  | 2
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | Yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | Yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | Yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | Yes |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 | Yes |  |  |  | 0 | 1.5
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | yes |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 |  | yes | 50% |  |  | 2
| Three or four stages | 15-20 Tons | 3 | yes |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | yes |  |  |  | 0 | 3
| Four stages | 35-50 Tons | 3.5 | yes |  |  |  | 0 | 3.5
| Four stages | > 50 Tons | 4 | yes |  |  |  | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 |  |  |  | $18lb |  | 125
| R-410A |  | 65 |  |  |  | $7lb |  | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | [5 empty] | 1
Programmable Thermostat | Install & Program Progrmmable thermostat
| Install Title-24-approved programmable thermostat | All Sizes | 1 | yes |  |  |  | 0 | 1

## Contractor5_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
| Replace linkage | 6-20 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
| Replace linkage | 25-30 Tons | 2 | Time is right |  |  |  | 0 | 2
| Replace linkage | 35-50 Tons | 2.5 | Time is right |  |  |  | 0 | 2.5
| Replace linkage | > 50 Tons | 3 | Time is right |  |  |  | 0 | 3
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
|  | >50 Tons | 2 | Time is right |  |  |  | 0 | 2
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | Time is right |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | Time is right |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | Time is right |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | Time is right |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | Time is right |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | Time is right |  |  |  | 0 | 2
|  | 6-20 Tons | 2 | Time is right |  |  |  | 0 | 2
|  | 25-30 Tons | 3 | Time is right |  |  |  | 0 | 3
|  | 35-50 Tons | 3 | Time is right |  |  |  | 0 | 3
|  | > 50 Tons | 5 |  | 6 Hours |  |  | 6 | 6
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | Time is right |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | Time is right |  |  |  | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | Time is right |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | Time is right |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | Time is right |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 |  |  | 1.5 is ok for this |  | 1.5 | 1.5
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | Time is right |  |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | Time is right |  |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | Time is right |  |  |  | 0 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | Time is right |  |  |  | 0 | 3.5
| ADEC upgrade | > 50 Tons | 4 | Time is right |  |  |  | 0 | 4
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 |  | 4 Hours |  |  | 4 | 4
| Add VFD to ADEC | 6-20 Tons | 3 |  | 4 Hours |  |  | 4 | 4
| Add VFD to ADEC | 25-30 Tons | 4 |  | 6 Hours |  |  | 6 | 6
| Add VFD to ADEC | 35-50 Tons | 4 |  | 6 Hours |  |  | 6 | 6
| Add VFD to ADEC | > 50 Tons | 5 |  | 6 Hours |  |  | 6 | 6
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 |  | 2 hours |  |  | 2 | 2
| Add DCV to ADEC | 6-20 Tons | 1.5 |  | 2hours |  |  | 2 | 2
| Add DCV to ADEC | 25-30 Tons | 2 |  | 3 hours |  |  | 3 | 3
| Add DCV to ADEC | 35-50 Tons | 2 |  | 3 hours |  |  | 3 | 3
| Add DCV to ADEC | > 50 Tons | 3 | Time is right |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 |  | 1.5 hours |  |  | 1 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 |  | 1.5 hours |  |  | 1 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 |  | 2 hours |  |  | 2 | 2
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 |  | 2 hours |  |  | 2 | 2
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 |  | 3 hours |  |  | 3 | 3
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 |  | 1.5 hours |  |  | 1 | 1
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 |  | 1.5 hours |  |  | 1 | 1
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 |  | 2 hours |  |  | 2 | 2
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 |  | 2 hours |  |  | 2 | 2
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 |  | 3 hours |  |  | 3 | 3
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | Time is right |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | Time is right |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 |  | 1.5 hours |  | More than 1 belt | 1 | 1
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 |  | 1.5 hours |  | More than 1 belt | 1.5 | 1.5 | Manual Entry - formula issue
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 |  | 2 hours |  | More than 1 belt | 2 | 2
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | Time is right |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 | Time is right |  |  |  | 0 | 2
| Three or four stages | 15-20 Tons | 3 | Time is right |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | Time is right |  |  |  | 0 | 3
| Four stages | 35-50 Tons | 3.5 | Time is right |  |  |  | 0 | 3.5
| Four stages | > 50 Tons | 4 | Time is right |  |  |  | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 |  |  |  |  | 0 | 125
| R-410A |  | 65 |  |  |  |  | 0 | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 |  |  |  |  | 0 | 1
Programmable Thermostat | Install & Program Progrmmable thermostat
| Install Title-24-approved programmable thermostat | All Sizes | 1 | Time is right |  |  |  | 0 | 1

## Contractor6_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 |  | X | 0.5 |  | 0.5 | 1.5
| Replace linkage | 6-20 Tons | 1.5 |  | X | 0.25 |  | 0.25 | 1.75
| Replace linkage | 25-30 Tons | 2 |  | X | 0.25 |  | 0.25 | 2.25
| Replace linkage | 35-50 Tons | 2.5 |  | X | 0.25 |  | 0.25 | 2.75
| Replace linkage | > 50 Tons | 3 |  | X | 0.5 | Trane is all I can say! | 0.5 | 3.5
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 |  | X | 0.5 |  | 0.5 | 1.5
|  | 25-30 Tons | 1.5 |  | X | 0.5 |  | 0.5 | 2
|  | 35-50 Tons | 1.5 |  | X | 0.5 |  | 0.5 | 2
|  | >50 Tons | 2 |  | X | 0.5 |  | 0.5 | 2.5
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 |  | X | 0.25 | TRANE again all black wires. | 0.25 | 2.75
| Wiring only - no circuit boards | 35-50 Tons | 2.5 |  | X | 0.25 |  | 0.25 | 2.75
| Wiring only - no circuit boards | > 50 Tons | 3 |  | X | 0.25 |  | 0.25 | 3.25
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 |  | X | 100 | Lots of Aerokroil | 0 | 2
|  | 6-20 Tons | 2 |  | X | 100 |  | 0 | 2
|  | 25-30 Tons | 3 |  | X | 100 |  | 0 | 3
|  | 35-50 Tons | 3 |  | X | 100 |  | 0 | 3
|  | > 50 Tons | 5 |  | X | 0.75 |  | 0.75 | 5.75
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 |  | X | 100 | broken terminals | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 |  | X | 100 | "" | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 |  | X | 100 | "" | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 |  | X | 100 | "" | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 |  | X | 100 | "" | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | X |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 |  | X | 0.25 |  | 0.25 | 3.25
| ADEC upgrade | 6-20 Tons | 3 |  | X | 0.25 |  | 0.25 | 3.25
| ADEC upgrade | 25-30 Tons | 3.5 |  | X | 0.25 |  | 0.25 | 3.75
| ADEC upgrade | 35-50 Tons | 3.5 |  | X | 0.25 |  | 0.25 | 3.75
| ADEC upgrade | > 50 Tons | 4 |  | X | 0.25 | Larger actuators | 0.25 | 4.25
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 |  | X | 0.33 | wiring mods. | 0.33 | 3.33
| Add VFD to ADEC | 6-20 Tons | 3 |  | X | 0.33 | " | 0.33 | 3.33
| Add VFD to ADEC | 25-30 Tons | 4 |  | X | 0.33 | " | 0.33 | 4.33
| Add VFD to ADEC | 35-50 Tons | 4 |  | X | 0.33 | " | 0.33 | 4.33
| Add VFD to ADEC | > 50 Tons | 5 |  | X | 0.33 | " | 0.33 | 5.33
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 |  | X | 0.35 | Wired or wireless | 0.35 | 1.85
| Add DCV to ADEC | 6-20 Tons | 1.5 |  | X | 0.35 |  | 0.35 | 1.85
| Add DCV to ADEC | 25-30 Tons | 2 |  | X | 0.5 |  | 0.5 | 2.5
| Add DCV to ADEC | 35-50 Tons | 2 |  | X | 0.5 |  | 0.5 | 2.5
| Add DCV to ADEC | > 50 Tons | 3 | X |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | X |  |  |  | 0 | 2
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 |  | X | 0.5 |  | 0.5 | 1.5
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 |  | X | 0.5 | Lid off Rheem | 0.5 | 1.5
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 |  | X | 0.5 | "" | 0.5 | 2
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 |  | X | 0.5 |  | 0.5 | 2
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 |  | X | 0.5 |  | 0.5 | 2.5
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 |  | X | 0.33 | Multi Groove | 0.33 | 1.83
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | X |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 | X |  |  |  | 0 | 2
| Three or four stages | 15-20 Tons | 3 | X |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | X |  |  |  | 0 | 3
| Four stages | 35-50 Tons | 3.5 | X |  |  |  | 0 | 3.5
| Four stages | > 50 Tons | 4 | X |  |  |  | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 | X |  |  |  | 0 | 125
| R-410A |  | 65 | X |  |  |  | 0 | 65
| R407C |  | 75 | [5 empty] | 75
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 |  |  |  |  | 0 | 1
[8 empty] | 0 | 0
Programmable Thermostat | Install & Program Progrmmable thermostat | [6 empty] | 0 | 0
| Install Title-24-approved programmable thermostat | All Sizes | 1 | X |  |  |  | 0 | 1
Note on I27: Phil Jordan: Can't accept 100 and can't assume 1 - omit
Note on I34: Phil Jordan: Can't accept 100 and can't assume 1 - omit

## Contractor7_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Replace linkage | 6-20 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Replace linkage | 25-30 Tons | 2 | X |  |  |  | 0 | 2
| Replace linkage | 35-50 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Replace linkage | > 50 Tons | 3 | X |  |  |  | 0 | 3
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | >50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | X |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | X |  |  |  | 0 | 2
|  | 6-20 Tons | 2 |  | X | 0.5 |  | 0.5 | 2.5
|  | 25-30 Tons | 3 | X |  |  |  | 0 | 3
|  | 35-50 Tons | 3 | X |  |  |  | 0 | 3
|  | > 50 Tons | 5 | X |  |  |  | 0 | 5
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | X |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | X |  |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | X |  |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | X |  |  |  | 0 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | X |  |  |  | 0 | 3.5
| ADEC upgrade | > 50 Tons | 4 | X |  |  |  | 0 | 4
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | X |  |  |  | 0 | 3
| Add VFD to ADEC | 6-20 Tons | 3 | X |  |  |  | 0 | 3
| Add VFD to ADEC | 25-30 Tons | 4 | X |  |  |  | 0 | 4
| Add VFD to ADEC | 35-50 Tons | 4 | X |  |  |  | 0 | 4
| Add VFD to ADEC | > 50 Tons | 5 | X |  |  |  | 0 | 5
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Add DCV to ADEC | 6-20 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Add DCV to ADEC | 25-30 Tons | 2 | X |  |  |  | 0 | 2
| Add DCV to ADEC | 35-50 Tons | 2 | X |  |  |  | 0 | 2
| Add DCV to ADEC | > 50 Tons | 3 | X |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | X |  |  |  | 0 | 2
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 | X |  |  |  | 0 | 2
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 | X |  |  |  | 0 | 1
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 | X |  |  |  | 0 | 1.5
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | X |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 | X |  |  |  | 0 | 2
| Three or four stages | 15-20 Tons | 3 | X |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | X |  |  |  | 0 | 3
| Four stages | 35-50 Tons | 3.5 | X |  |  |  | 0 | 3.5
| Four stages | > 50 Tons | 4 | X |  |  |  | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 | X |  |  |  | 0 | 125
| R-410A |  | 65 | X |  |  |  | 0 | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | X |  |  |  | 0 | 1
[8 empty] | 0 | 0
Programmable Thermostat | Install & Program Progrmmable thermostat | [6 empty] | 0 | 0
| Install Title-24-approved programmable thermostat | All Sizes | 1 | X |  |  |  | 0 | 1

## Contractor8_responses
Diagnosed Malfunction
|  |  | Estimated | About Right ? | Too Low? | Add/Remove Time | Comments | Contractor Adjustment | hours for study
Program Measure Name | Description | Unit Size | Approx. Time to Repair (hours)
Economizer Repair | Replace worn/damaged economizer damper linkage
| Replace linkage | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Replace linkage | 6-20 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Replace linkage | 25-30 Tons | 2 | X |  |  |  | 0 | 2
| Replace linkage | 35-50 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Replace linkage | > 50 Tons | 3 | X |  |  |  | 0 | 3
Economizer Repair | Repair stuck economizer damper
|  | 2-5 Tons | 1 | X |  | 0.5 | BEACH LOCATION ADD TIME | 0 | 1
|  | 6-20 Tons | 1 |  | X | 0.5 | BEACH LOCATION ADD TIME | 0.5 | 1.5
|  | 25-30 Tons | 1.5 |  | X | 0.5 | BEACH LOCATION ADD TIME | 0.5 | 2
|  | 35-50 Tons | 1.5 |  | X | 0.5 | BEACH LOCATION ADD TIME | 0.5 | 2
|  | >50 Tons | 2 |  | X | 0.5 | BEACH LOCATION ADD TIME | 0.5 | 2.5
Economizer Repair | Repair damaged control wiring
| Wiring only - no circuit boards | 2-5 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 6-20 Tons | 2 | X |  |  |  | 0 | 2
| Wiring only - no circuit boards | 25-30 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | 35-50 Tons | 2.5 | X |  |  |  | 0 | 2.5
| Wiring only - no circuit boards | > 50 Tons | 3 | X |  |  |  | 0 | 3
Economizer Repair | Replace economizer damper assembly
|  | 2-5 Tons | 2 | X |  |  |  | 0 | 2
|  | 6-20 Tons | 2 | X |  |  | MAY REQUIRE RETROFIT KIT | 0 | 2
|  | 25-30 Tons | 3 | X |  |  | MAY REQUIRE RETROFIT KIT | 0 | 3
|  | 35-50 Tons | 3 | X |  |  | MAY REQUIRE RETROFIT KIT | 0 | 3
|  | > 50 Tons | 5 | X |  |  | MAY REQUIRE RETROFIT KIT | 0 | 5
Economizer Repair | Replace economizer controller
| Kind for kind - not an ADEC upgrade | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Kind for kind - not an ADEC upgrade | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Kind for kind - not an ADEC upgrade | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Adjust economizer changeover setpoint
Control Adjustment |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1 | X |  |  |  | 0 | 1
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer sensor
Control Replacement |  | 2-5 Tons | 1 | X |  |  |  | 0 | 1
|  | 6-20 Tons | 1 | X |  |  |  | 0 | 1
|  | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
|  | > 50 Tons | 2 | X |  |  |  | 0 | 2
Economizer Controls | Replace economizer controller
Control Replacement | ADEC upgrade | 2-5 Tons | 3 | X |  |  |  | 0 | 3
| ADEC upgrade | 6-20 Tons | 3 | X |  |  |  | 0 | 3
| ADEC upgrade | 25-30 Tons | 3.5 | X |  |  |  | 0 | 3.5
| ADEC upgrade | 35-50 Tons | 3.5 | X |  |  |  | 0 | 3.5
| ADEC upgrade | > 50 Tons | 4 | X |  |  |  | 0 | 4
Economizer Controls | Variable Frequency Drive (VFD)
Control Upgrade | Add VFD to ADEC | 2-5 Tons | 3 | X |  |  | ASSUMING MOTOR IS RATED | 0 | 3
| Add VFD to ADEC | 6-20 Tons | 3 | X |  |  | ASSUMING MOTOR IS RATED | 0 | 3
| Add VFD to ADEC | 25-30 Tons | 4 | X |  |  | ASSUMING MOTOR IS RATED | 0 | 4
| Add VFD to ADEC | 35-50 Tons | 4 | X |  |  | ASSUMING MOTOR IS RATED | 0 | 4
| Add VFD to ADEC | > 50 Tons | 5 | X |  |  | ASSUMING MOTOR IS RATED | 0 | 5
Economizer Controls | Demand Controlled Ventilation (DCV)
Control Upgrade | Add DCV to ADEC | 2-5 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Add DCV to ADEC | 6-20 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Add DCV to ADEC | 25-30 Tons | 2 | X |  |  |  | 0 | 2
| Add DCV to ADEC | 35-50 Tons | 2 | X |  |  |  | 0 | 2
| Add DCV to ADEC | > 50 Tons | 3 | X |  |  |  | 0 | 3
Condenser Coil Cleaning | Condenser Coil Cleaning (conventional coil)
| Typical coil cleaner and water - moderately dirty coil | 2-5 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 6-20 Tons | 1 | X |  |  |  | 0 | 1
| Typical coil cleaner and water - moderately dirty coil | 25-30 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | 35-50 Tons | 1.5 | X |  |  |  | 0 | 1.5
| Typical coil cleaner and water - moderately dirty coil | > 50 Tons | 2 | X |  |  |  | 0 | 2
Evaporator Coil Cleaning | Evaporator Coil Cleaning
| Residential grade equipment - some disassembly | 2-5 Tons | 1 | X |  |  | DOES THIS INCLUDE SET UP TIME? | 0 | 1
| Typical coil cleaner & water - moderately dirty | 6-20 Tons | 1 | X |  |  | DOES THIS INCLUDE SET UP TIME? | 0 | 1
| Typical coil cleaner & water - moderately dirty | 25-30 Tons | 1.5 | X |  |  | DOES THIS INCLUDE SET UP TIME? | 0 | 1.5
| Typical coil cleaner & water - moderately dirty | 35-50 Tons | 1.5 |  | x | 0.5 | DOES THIS INCLUDE SET UP TIME? | 0.5 | 2
| Typical coil cleaner & water - moderately dirty | > 50 Tons | 2 |  | x | 1 | DOES THIS INCLUDE SET UP TIME? | 1 | 3
Cogged V-belt | Notched V-belt
| Replace existing smooth belt w/ notched V-belt | 2-5 Tons | 1 | X |  |  | MOTOR ADJUSTMENT MAY BE NEEDED | 0 | 1
| Replace existing smooth belt w/ notched V-belt | 6-20 Tons | 1 |  | x | 0.5 | MOTOR ADJUSTMENT MAY BE NEEDED | 0.5 | 1.5
| Replace existing smooth belt w/ notched V-belt | 25-30 Tons | 1 |  | x | 0.5 | MOTOR ADJUSTMENT MAY BE NEEDED | 0.5 | 1.5
| Replace existing smooth belt w/ notched V-belt | 35-50 Tons | 1 |  | x | 0.5 | MOTOR ADJUSTMENT MAY BE NEEDED | 0.5 | 1.5
| Replace existing smooth belt w/ notched V-belt | > 50 Tons | 1.5 |  | x | 1 | MOTOR ADJUSTMENT MAY BE NEEDED | 1 | 2.5
Refrigerant Charge Adjustment | Refrigerant Charge Adjustment
| Single stage - no repairs | 2-6 Tons | 2 | X |  |  |  | 0 | 2
| Two stages | 7-20 Tons | 2 | X |  |  |  | 0 | 2
| Three or four stages | 15-20 Tons | 3 | X |  |  |  | 0 | 3
| Three or four stages | 25-30 Tons | 3 | X |  |  |  | 0 | 3
| Four stages | 35-50 Tons | 3.5 | X |  |  |  | 0 | 3.5
| Four stages | > 50 Tons | 4 | X |  |  |  | 0 | 4
Refrigerant Retail Price ($/lb)
| R-22 |  | 125 | X |  |  |  | 0 | 125
| R-410A |  | 65 | X |  |  |  | 0 | 65
insert refrigerant used if other
Unoccupied Fan Control | Programmable thermostat Adjustment
| Program thermostat to match occupancy | All Sizes | 1 | X |  |  |  | 0 | 1
[8 empty] | 0 | 0
Programmable Thermostat | Install & Program Progrmmable thermostat | [6 empty] | 0 | 0
| Install Title-24-approved programmable thermostat | All Sizes | 1 | X |  |  |  | 0 | 1