Work Paper PGE3PHVC160

Revision 4

Pacific Gas & Electric

Refrigerant Charge Adjustment (RCA)

# At-a-Glance Summary

| Measure Codes | HV387, HV388, HV389, HV390 |
| --- | --- |
| Measure Description | Adjust refrigerant charge to meet manufacturer specifications |
| Base Case Description | Refrigerant charge does not meet manufacturer specifications |
| Units | Per ton cooling capacity, Cap-Tons. |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | $47.49 / ton |
| Incremental Measure Cost ($/unit) | $47.49 / ton |
| Effective Useful Life | 3 years (DEER EUL ID: NonRes-RCx-Operational, capped EUL per E-4818) |
| Measure Installation Type | Retro-Commissioning (RC), (RC, previously known as Retrofit Add-on (REA)) |
| Net-to-Gross Ratio | 0.73 (DEER NTGR ID: NonRes-sAll-mHVAC-RCA) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| Revision 0 | 06/01/2012 | Tai Voong (PG&E) | At-A-Glance Measure List: Changed Building Vintage from “AV” to “Any” and Unit Definition from “Ton” to “Cap-Tons”. |
| Revision 0 | 08/28/2012 | Tai Voong (PG&E) | - Revised savings, NTG, and ISR to comply with ED’s Disposition on the HVAC Quality Maintenance/AirCare Plus Workpapers dated on the March 2, 2013 and May 16, 2013 disposition. - Only the PG&E executive summary savings template was updated. Workpaper language will be updated later. - For updated Savings values, see file PGE3PHVC160 R1_RCA(chl7v2).xlsx |
| Revision 1 | 7/11/2013 | Christopher Li (PG&E) | At-A-Glance Measure List: Changed Building Vintage from “AV” to “Any” and Unit Definition from “Ton” to “Cap-Tons”. |
| Revision 2 | 10-8-15 | Matt Tyler (CLEAResult), Sherry Hu (PG&E) | - Work paper was updated according to Workpaper Disposition for Nonresidential HVAC Rooftop Quality Maintenance and WO32. - Removed measure HA80 and added 16 new ones. |
| Revision 3 | 11/30/18 | Tai Voong (PG&E) | - Retroactive updates to EUL for BRO measures per Resolution E-4952 and E-4818. Retroactive to 1/1/2018. |
| Revision 4 | 12/20/18 | Phil Jordan (CLEAResult), Tai Voong (PG&E) | - Measure cost analysis was updated to use current information - Work paper content was updated according to Resolution E-4818 including Installation Type and EUL/RUL values - Substituted DEER RCA measures for previous RCA measure approach |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This statewide work paper details refrigerant charge adjustment on existing nonresidential split-system and unitary HVAC equipment. This is one of eight work papers that cover specific HVAC Quality Maintenance (QM) treatments formerly combined into the measures described in the Revision 0 version of the June 26, 2012 Work Paper PGECOHVC138 Nonresidential HVAC RTU Quality Maintenance and the Revision 3 version of the December 26, 2014 Work Paper SCE13HC037 Comprehensive Commercial HVAC Rooftop Unit Quality Maintenance. All HVAC QM treatments are now covered by the following work papers:

- Condenser Coil Cleaning (PGE3PHVC156R3)

- Economizer Controls (PGE3PHVC152R5)

- Economizer Repair (PGE3PHVC151R4)

- Evaporator Coil Cleaning (PGE3PHVC158R3)

- Refrigerant Charge Adjustment (PGE3PHVC160R3)

- Unoccupied Fan Control (PGE3PHVC157R2)

- Programmable Thermostat (PGE3PHVC153R3)

Separation of this HVAC QM treatment into a statewide set of measures was performed using guidance from the document WORKPAPER DISPOSITION FOR Non-Residential HVAC Rooftop Quality Maintenance and supplementary spreadsheet: 20132014-CommercialHVACMaintenance-SavingsValues-April2013-v1-2.xlsx.

Table 1 Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Adjust refrigerant charge to meet manufacturer specifications |
| Existing Condition | Refrigerant charge 4-50% greater or less than manufacturer specifications |
| Code/Standard | N/A |
| Industry Standard Practice | Standard 180-2008, Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems |

Table 2 Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  |  | HV387: NE-HVAC-RefChg-Inc-Typ-ntxv | Small Pkg AC system with No TXV, increase refrigerant charge from Typical under-charge (4 - 50%) to factory specified level |
|  |  |  | HV390: NE-HVAC-RefChg-Inc-Typ-txv | Small Pkg AC system with TXV, increase refrigerant charge from Typical under-charge (4 - 50%) to factory specified level |
|  |  |  | HV388: NE-HVAC-RefChg-Dec-Typ-ntxv | Small Pkg AC system with No TXV, decrease refrigerant charge from Typical over-charge (4 - 50%) to factory specified level |
|  |  |  | HV389: NE-HVAC-RefChg-Dec-Typ-txv | Small Pkg AC system with TXV, decrease refrigerant charge from Typical over-charge (4 - 50%) to factory specified level |

This statewide work paper supports HVAC QM programs as well as HVAC tune-up programs in multiple programs and service territories. Refer to programs that offer the measure for specific restrictions and guidelines in addition to those described herein.

The target market for this measure is nonresidential buildings served by unitary DX and split systems that do not serve process or refrigeration loads. The measure is defined for all nonresidential building types and all 16 California climate zones. Database for Energy Efficient Resources (DEER19) savings are for a weighted average of seven DEERvintages using utility-specific weightings. Savings are specified for units with and without thermal expansion valves (TXV).

Participating contractors must ensure the customer facility is physically located within the service territory of the Investor Owned Utility (IOU) administering the program and that the customer receives electric services from that IOU. Other terms and conditions are set by individual programs.

This measure requires field documentation of the existing conditions that verify the measure was necessary and that the measure was successfully applied. The following applicable measure criteria are per CPUC Resolution E-4867: “To be eligible for savings claims all charge adjustments must be performed by technicians with proper training, using a “fault” diagnosis and correction sequence and procedure in a program implementation that includes a continuous verification activity to assure the refrigerant charge adjustment, and related system fault detection and correction work, is being performed properly. The diagnosis and correction must be performed using appropriate methods and tools that allow the identification and correction of all system “fault” conditions that affect the refrigerant system measurements prior to proceeding with a charge state measurement and then any indicated appropriate charge adjustment. Technicians performing HVAC system fault diagnosis and correction must have all the proper tools, must follow the appropriate procedures, and have been trained by an experienced and qualified professional on the procedures and use of the tools.”

## 1.2 Technical Description

This measure involves refrigerant charge correction to nonresidential direct expansion (DX) air-cooled HVAC units. When an HVAC unit’s refrigerant charge does not meet the manufacturer recommended levels it results in a decrease in the unit’s energy efficiency ratio (EER).

Some units may be undercharged, which can result in decreased power draw but potentially longer run times.  Other units may be overcharged, which can result in increased power draw but potentially shorter run times. In either case, energy savings can be achieved by correcting refrigerant charge to optimum levels based on the manufacturers’ specifications. This measure is only appropriate for 4-50% undercharged or overcharged units Systems undercharged or overcharged by <4% are not eligible for claimed savings. For units with multiple circuits, UES values must be applied to the tonnage of the circuit being recharged, not the tonnage of all circuits.

## 1.3 Installation Types and Delivery Mechanisms

The installation type describes the program scenario in which the measure is applied, thus guiding energy savings and measure cost methodology. The installation type is retrocommissioning and operational programs in commercial settings (RC, previously known as REA in the table below, but terminology updated per CPUC Resolution E-4818) since the baseline is the existing unit. These are summarized below in Table 3.

Table 3 Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| New Construction (NEW/NC) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit or Early Replacement (RET/ER) | Above Customer Existing | Above Code or Standard | RUL | EUL-RUL |
| Retrofit First Baseline Only (REF) | Above Customer Existing | N/A | EUL | N/A |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings. See Table 4 and Table 5 below for descriptions of available delivery methods and incentive methods, respectively.

SCE Delivery Mechanism: Financial Support paired with Direct Install, Down-Stream Incentive – Deemed, or Mid-Stream Incentive

PG&E Delivery Mechanism: Financial Support paired with Direct Install or Mid-Stream Incentive

Table 4 Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Appliance Turn-in and Recycling | The program motivates customers, through financial incentives, to recycle appliances that are functional but inefficient. This prevents the continued use of those appliances, by both the current owner and potential future owners. |
| Audit/Information/Testing Services | The program performs a free assessment of a customer’s facility and provides the customer with information and guidance on energy efficiency opportunities. |
| Commissioning and Retrocommissioning | The program modifies or repairs existing equipment to ensure that it works as intended. |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Innovative Design | The program funds new ideas that meet reasonable scientific scrutiny for potential energy savings. These innovative measures typically have small market penetration (less than 5%) or are targeted toward relatively unreached market segments. |
| New Construction | The program offers financial incentives and/or design assistance to customers involved with new building construction. This is intended is to motivate customer to exceed Title 24 building energy efficiency requirements (residential or nonresidential). |
| Partnership | The program implements projects through a partnership between the utility and an institutional, government, or community-based organization. |
| Performance Based | The program offers financial incentives that vary based on the energy efficiency performance of specific projects. |
| Up-Stream Programs | See Up-Stream Incentive and Up-Stream Buy Down in the Incentive Method table. |

Table 5 Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Mid-Stream Incentive | The program gives a financial incentive to a midstream market actor, such as a retailer or contractor, to encourage the promotion of efficient measures. The incentive may or may not be passed on to the end-use customer. |
| Up-Stream Incentive | The program gives a financial incentive to an upstream market actor, such as a manufacturer or distributor, to encourage the manufacture, provision, or distribution of an efficient measure. The incentive may or may not be passed on to the end-use customer. |
| Up-Stream Buy Down | The program gives a financial incentive to an upstream market actor, such as a manufacturer or distributor, with specific requirements to pass down the incentive to the end use customer. Such an incentive buys-down the cost of an efficient measure for the end-use customer by at least the amount of the financial incentive. |
| Giveaway | The program provides customers with energy efficiency equipment or services for free. |
| Exchange/Replacement | The utility program holds events where customers can trade functional equipment for similar but more energy efficient equipment, free of charge. |
| On-bill Finance/Loan | The program offers financing for the cost an efficient measure as part of the utility bill. This can be an add-on option to an existing program or can serve as an organizing principle for its own program. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER was referenced on October 2, 2018 for 2019 updates to the measure. A DEER 2019 update to the RCA measures has occurred and is incorporated herein. This work paper uses RCA unit energy savings (UES) values from the existing DEER RCA measure. .

Table 6 DEER Difference Summary

| DEER Item | Used for Work Paper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | Yes |
| DEER Version | DEER 2019, READI v2.5.1 |
| Reason for Deviation from DEER | No deviation from DEER |
| DEER Measure IDs Used | Yes |

Net-to-Gross Ratio

The Net-to-Gross Ratio (NTGR) was obtained using the DEER READI tool. The relevant NTGR for the measures in this work paper is shown in Table 7.

Table 7 Measure Net-to-Gross Ratios

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mHVAC-RCA | HVAC Maintenance: Refrigerant Charge Adjustment (RCA) | Com | Any | DirInstall, NonUpStrm | 0.73 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document that will be supplied to the Commission Staff.

Installation Rate

The installation rate (IR) values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in Table 8 below.

Table 8 Installation Rates

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Com-RCA-All | Commercial Refrigerant Charge & Airflow Adjustment; Annual Installation Rate | Com | Any | DirInstall, NonUpStrm | 0.638 |
| Com-RCA-PGE | Commercial Refrigerant Charge & Airflow Adjustment; Annual Installation Rate | Com | Any | DirInstall, NonUpStrm | 0.575 |
| Com-RCA-SCE | Commercial Refrigerant Charge & Airflow Adjustment; Annual Installation Rate | Com | Any | NonUpStrm | 0.67 |
| Com-RCA-SDG | Commercial Refrigerant Charge & Airflow Adjustment; Annual Installation Rate | Com | Any | DirInstall, NonUpStrm | 0.67 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for a RC measure with an applicable code baseline. Per Resolution E-4818, measures resulting in performance that does not exceed the nominal efficiency of the pre-existing equipment have an effective useful life not to exceed three years, and for this reason the EUL and RUL of this measure is capped at three years. The relevant EUL and RUL values for the measures in this work paper are shown in Table 9 below.

Table 9 EUL and RUL

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-RefChg | Refrigerant Charge - Commercial | Com | HVAC | 3 | 3 |

### 1.4.2 Codes and Standards Analysis

These maintenance measures are not governed by either state or federal codes and standards. The document Standard 180-2008, Standard Practice for Inspection and Maintenance of Commercial Building HVAC SystemsError: Reference source not found may be used by QM programs as a guide for measure implementation. Only licensed California contractors will participate in the program.  As required by the California State Licensing Board, contractors will be responsible for meeting all applicable codes. In general, maintenance and repairs do not require permits.

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

Studies of significant importance to the measure development in this work paper are described in the following section.

### 1.5.1 Laboratory HVAC Testing Research for 2013-14 (HVAC5): An Introduction and Data Dictionary

Completion date: 	2/3/2017

Author:			California Public Utilities Commission, Energy Division

The HVAC-5 EM&V study included laboratory investigations of refrigerant charge adjustments (RCA), with data to demonstrate how those adjustments affect the cooling capacity and efficiency of package HVAC systems. The results of the HVAC-5 lab tests have been processed and used to update the DEER non-residential refrigerant charge measures. The HVAC-5 data also show significantly lower electric input ratio (EIR) adjustment factors than the DEER2014 values, especially for overcharged systems.

## 1.6 Data Quality and Future Data Needs

# Additional study of the impacts of refrigerant charge testing and adjustment protocols may be warranted. The improvements that RCA can bestow on HVAC system efficiency are highly dependent on the existing condition of the refrigeration system and determining the most accurate testing protocol would allow for a higher confidence in achieved savings.

# Section 2. Calculation Methodology

DEER UES values are used; no calculation methodology was used in this workpaper to derive UES values. UES values are per ton of unit capacity. For units with multiple refrigerant circuits, UES values are only to be applied to the tonnage of the circuit being recharged, not the total unit tonnage. .

## 2.1 Electric Energy Savings Estimation Methodologies

UES values for kWh per year savings from the DEER RCA measures are used. UES values are per ton of refrigerant circuit capacity. For units with multiple refrigerant circuits, UES values are only to be applied to the tonnage of the circuit being recharged, not the total unit tonnage.

## Demand Reduction Estimation Methodologies

UES values for kWh per year savings from the DEER RCA measures are used. UES values are per ton of refrigerant circuit capacity. For units with multiple refrigerant circuits, UES values are only to be applied to the tonnage of the circuit being recharged, not the total unit tonnage.

## Gas Energy Savings Estimation Methodologies

UES values for therms per year savings from the DEER RCA measures are used. UES values are per ton of refrigerant circuit capacity. For units with multiple refrigerant circuits, UES values are only to be applied to the tonnage of the circuit being recharged, not the total unit tonnage. .

# Section 3. Load Shapes

Load shapes are used for portfolio lifecycle cost analysis. A load shape indicates the distribution of a measure’s energy savings over one year. A load shape is a set of fractions summing to unity, with one fraction per hour (or other time period). Multiplying a savings value by the load shape value for any particular hour yields the energy savings for that particular hour.

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in Table 10 Building Types and Load Shapes.

Table 10 Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:HVAC_Split-Package_AC, | NON_RES |
| Education - Primary School |  |  |
| Education - Secondary School |  |  |
| Education - Relocatable Classroom |  |  |
| Education - Community College |  |  |
| Education - University |  |  |
| Grocery |  |  |
| Health/Medical - Nursing Home |  |  |
| Health/Medical - Hospital |  |  |
| Lodging – Hotel |  |  |
| Lodging - Motel |  |  |
| Manufacturing – Bio/Tech |  |  |
| Manufacturing – Light Industrial |  |  |
| Office - Large |  |  |
| Office - Small |  |  |
| Restaurant - Fast-Food |  |  |
| Restaurant - Sit-Down |  |  |
| Retail - Multistory Large |  |  |
| Retail - Single-Story Large |  |  |
| Retail - Small |  |  |
| Storage - Conditioned |  |  |
| Warehouse - Refrigerated |  |  |

# Section 4. Costs

Due to the age of the cost resources from the prior revision of this workpaper, a cost survey was conducted of active, program-participating contractors and technicians (attached). The 2010-2012 WO17 Ex Ante Measure Cost Study (Cost Study) and the DEER Measure Cost Data Users Guide were also referenced. As a RC measure, the incremental cost for RCA is equal to the gross measure cost.

## 4.1 Base Case Cost

The base case is the customer’s existing equipment; therefore, the base case cost is $0.00.

## 4.2 Measure Case Cost

Labor and equipment costs were derived from a cost survey conducted of active, program-participating contractors and technicians (attached). The resulting costs per ton cooling for RCA are $8.32 for materials and $39.17 for labor for a total cost of $47.49/ton.

## 4.3 Full and Incremental Measure Cost

Table 11 Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| RC | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Table 12 Full and Incremental Costs

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| RC | $8.32 + $39.17 = $47.49 | $8.32 + $39.17 = $47.49 | N/A |

# Attachments

Attachment 1 – Cost survey conducted by CLEAResult (April 2018) of active, program-participating contractors and technicians

# References

Judith Jennings, et al, Pacific Gas and Electric Company (2012,06,26). Work Paper PGECOHVC138 Nonresidential HVAC RTU Quality Maintenance,.

Andres Fergadiotti, Southern California Edison (2014,12,26). Work Paper SCE13HC037 Comprehensive Commercial HVAC Rooftop Unit Quality Maintenance

California Public Utilities Commission, Energy Division, WORKPAPER DISPOSITION FOR Non-Residential HVAC Rooftop Quality Maintenance, 5-2-2013.

California Public Utilities Commission, Energy Division, Spreadsheet: 20132014-CommercialHVACMaintenance-SavingsValues-April2013-v1-2.xlsx,submitted as addendum to WORKPAPER DISPOSITION FOR Non-Residential HVAC Rooftop Quality Maintenance.

American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc. and Air Conditioning Contractors of America. (© ASHRAE and ACCA, 2008). Standard 180-2008, Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems.

Public Utilities Commission of the State of California (2017, March 3). Energy Division Resolution E-4818. Retrieved from http://docs.cpuc.ca.gov/ResolutionSearchForm.aspx.

Database for Energy Efficient Resources, http://www.deeresources.com/index.php/deer-versions/deer2019-and-june-2017-updates

James J. Hirsch & Associates. READi tool, V2.5.1. Developed for California Energy Commission.

Public Utilities Commission of the State of California (2/3/2017). Laboratory HVAC Testing Research for 2013-14 (HVAC5): An Introduction and Data Dictionary.

Itron. 2010-2012 WO017 Ex Ante Measure Cost Study Final Report. San Francisco, CA (2014, May 27). Retrieved 8/26/2015 at http://www.energydataweb.com/cpucFiles/pdaDocs/1100/2010-2012%20WO017%20Ex%20Ante%20Measure%20Cost%20Study%20-%20Final%20Report.pdf.

DEER Measure Cost Data Users Guide found on www.deeresources.com under DEER2011 Database Format hyperlink, DEER2011 for 13-14, spreadsheet SPTdata_format-V0.97.xls.