Work Paper PGE3PREF121

Refrigeration Case SST Control

Revision # 2

PECI

EnergySmart Grocer

Refrigeration Case SST Control

Measure Codes R119

EnergySmart Grocer, PECI

# At-a-Glance Summary

| Applicable Measure Codes: | R119 |
| --- | --- |
| Measure Description: | Floating SST control on low temperature and medium temperature suction groups |
| Energy Impact Common Units: | CAP-TONS (tons cooling capacity) |
| Base Case Description: | Source: DEER 2008 Standard air-cooled multiplex system, SST controlled to fixed setpoint |
| Base Case Energy Consumption: | Source: DEER 2008 The base case energy consumption varies by climate zone and vintage. |
| Measure Energy Consumption: | Source: DEER 2008 generated by MASControl V3.00.19 The energy efficient measure energy consumption varies by climate zone and vintage. |
| Energy Savings (Base Case – Measure) | Source: DEER 2008 generated by MASControl V3.00.19 The energy efficient savings varies by climate zone and vintage. |
| Costs Common Units: | CAP-TONS (tons cooling capacity) |
| Base Case Equipment Cost ($/unit): | REA: $0.00 |
| Measure Equipment Cost ($/unit): | Source: DEER 2008 REA: $14.69 |
| Gross Measure Cost ($/unit) | Source: DEER 2008 REA: $44.15 |
| Measure Incremental Cost ($/unit): | Source: DEER 2008 REA: $44.15 |
| Effective Useful Life (years): | Source: DEER 2008 15 years |
| Measure Application Type: | Retrofit Add On (REA) |
| Net-to-Gross Ratios: | Source: DEER 2011 4.00 0.6 |
| Important Comments: |  |

# Work Paper Approvals

The following Manager(s) approved this workpaper through the PG&E Electronic Data Routing System under Routing Requisition # _______________

Grant Brohard Manager, Technical Product Support

Carolyn Weiner Principal, CES Products and Programs

# Document Revision History

| Revision # | Date | Section by Section Description of Revisions | Author (Company) |
| --- | --- | --- | --- |
| Revision 0 | 4/7/2008 | Original work paper | (PECI Engineering) |
| Revision 1 | 5/30/2012 | Updated to PG&E 2013-2014 format Update cost data to reflect DEER 2008 Update EUL to reflect DEER 2008 | Ricky Armendariz (EnergySmart Grocer) |
| Revision 2 | 5/14/2014 | Updated savings data according to new climate zone weather files. Formatting updated per PG&E guidelines | Ben Wright, PECI Danielle Geers, PECI |

# Table of Contents

At-a-Glance Summary	ii

Work Paper Approvals	iii

Document Revision History	iv

Table of Contents	v

List of Tables	v

Section 1. General Measure & Baseline Data	1

1.1 Product Measure Description & Background	1

1.2 Product Technical Description	1

1.3 Measure Application Type	1

1.4 Product Base Case and Measure Case Data	2

1.4.1 DEER Base Case and Measure Case Information	2

1.4.2 Codes & Standards Requirements Base Case and Measure Information	3

1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases	3

1.4.5  Time-of-Use Adjustment Factor	3

Section 2. Calculation Methods	4

Section 3. Load Shapes	4

3.1 Base Case Load Shapes	4

3.2 Measure Load Shapes	4

Section 4. Base Case & Measure Costs	5

4.1 Base Case(s) Costs	5

4.2 Measure Case Costs	5

4.3 Incremental & Full Measure Costs	5

4.3.1 Full Measure Cost	5

4.3.2  Incremental Measure Costs	6

Appendices	7

A. (1.4.1) DEER Base Case and Measure Case Information	7

References:	9

# List of Tables

Table 1 Measure Application Type	6

Table 2  Net-to-Gross Ratios	7

# Section 1. General Measure & Baseline Data

This workpaper details the DEER measure D03-220 for adding controls to reset the suction pressure setpoint during periods of low loads based on zone temperature.

## 1.1 Product Measure Description & Background

Program Restrictions and Guidelines

Terms and Conditions:

Requirements:

- Must convert the suction pressure controls of an existing multiplex system from fixed control to floating control.

- Suction pressure must be adjusted to the highest point that can still maintain setpoint temperatures at monitored cases on the suction circuit.

Additional Details:

- To qualify for rebate, new hardware must be installed. Projects that only reprogram a controller are not eligible for this rebate.

Market Applicability:  This is a retrofit measure that is applicable to existing multiplex refrigeration systems in the grocery sector in a downstream rebate program.  The rebate encourages the grocer to add this refrigeration control strategy to make their existing refrigeration system more energy efficient.

This paper applies to grocery-type buildings, five building vintage categories and nine California climate zones (CZ 1, 2, 3, 4, 5, 11, 12, 13 and 16).

## 1.2 Product Technical Description

This DEER measure adds controls to reset the suction pressure setpoint based on zone temperature.  The compressors then operate more efficiently during periods of low load.

## 1.3 Measure Application Type

This is a Retrofit Add On (REA) measure: adding an EE feature or new equipment to a unit to make it more efficient.

The DEER Measure Cost Data Users Guide found on www.deeresources.com under DEER2011 Database Format hyperlink, DEER2011 for 13-14, spreadsheet SPTdata_format-V0.97.xls, defines the terms as follows:

Table 1 Measure Application Type

Identifies the measure application type in the Measure Implemenation table in DEER2011.

| Code | Description | Comment |
| --- | --- | --- |
| REA | Retrofit Add On | Single baseline (above pre-existing, full measure costs required |

## 1.4 Product Base Case and Measure Case Data

### 1.4.1 DEER Base Case and Measure Case Information

The 2008 DEER data generated by MASControl V3.00.19 data include: demand, electric and interactive gas energy savings.   DEER 2008 data includes: equipment unit costs, equipment incremental costs, equipment useful life and Net-to-Gross values.

The original measures and energy models were created with DEER 2005. Measure information was updated in DEER 2008. The MAS Control tool that ran the batch simulations with the new 2014 T24 weather files appear to have pulled from the D08 version of the measure. We therefore cited the DEER 2008 measure with the update generated through most up to date version of MAS Control.

Delta Wattage Assumption (ΔW):

The EUL peak electric savings were downloaded from DEER directly, they match the intended measures.

| Building type | Bldg Vintage | Climate Zone | Electric Savings Watts | Deer units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- |
| GRO | 03 | CZ01 | 15.200 | tons | 2008 | D03-220 |
| GRO | 03 | CZ02 | 40.912 | tons | 2008 | D03-220 |
| GRO | 03 | CZ03 | 13.646 | tons | 2008 | D03-220 |

Therms Savings Assumption (ΔTh)

EUL Gas Savings (ΔTh): The gas savings were generated by MASControl V3.00.19; they match the intended measures and express interactive effects only.

| Building type | Bldg Vintage | Climate Zone | Interactive Only? Yes / No | Gas Savings Therms | Deer units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GRO | 03 | CZ01 | Yes | 0.08321 | tons | 2008 | D03-220 |
| GRO | 03 | CZ02 | Yes | 0.06278 | tons | 2008 | D03-220 |
| GRO | 03 | CZ03 | Yes | 0.07759 | tons | 2008 | D03-220 |

Base Case Costs and Measure Case Costs

The Base Case, Measure Case and Incremental costs are from the DEER database file Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls; they match the intended measures for climate zones and building types and ages.

|  |  |  | Costs ($) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Building type | Bldg Vintage | Climate Zone | Base Case | Measure Case | IMC | DEER Version | Impact IDs |
| GRO | ALL | ALL | $0.00 | $44.15 | $44.15 | 2008 | D03-220 |

Net-to-Gross Assumption:  2011 DEER Update Report – Section 15 Table 15-3

Table 1 below summarizes all applicable DEER based Net-to-Gross ratios for programs that may use this measure.

Table 2  Net-to-Gross Ratios

|  |  | DEER Spreadsheet |  |
| --- | --- | --- | --- |
| Program Approach | NTG | File name | Cell Number |
| EnergySmart Grocer | 0.6 | DEER2011_NTGR_2012-05-16 | T57 |

Effective Useful Life / Remaining Useful Life:

The Effective Useful Life estimates were downloaded directly from DEER directly; they match the intended measures for climate zones and building types and ages.

| Building type | Bldg Vintage | Climate Zone | EUL (yrs) | RUL (yrs) | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- |
| GRO | ALL | ALL | 15 | N/A | DEER 2008 | D03-220 |

### 1.4.2 Codes & Standards Requirements Base Case and Measure Information

The measure in this work paper is not governed by either state or federal codes and standards.

Title 20: This measure does not fall under Title 20 of the California Energy Regulations.

Title 24: There are no code changes. T24 p. 32 Section 100.0(a)2, code only required when building permit or permit renewal is needed. An included copy of Title 24 can be referenced at the file “Title 24 Building Energy Efficiency Standards.pdf.”

Federal Standards: This measure does not fall under Federal DOE or EPA Energy Regulations.

### 1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases

There are no further data or calculations provided for the support of the measures in this workpaper.

### 1.4.5  Time-of-Use Adjustment Factor

We are required by CPUC decision 06-06-063 dated June 29, 2006 to apply time-of-use (TOU) adjustment factors on residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.   Since this is not an A/C measure, the TOU adjustment factor is 0.  Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

1.5 Summary of Inputs for Savings Calculations

The following table provides references to sections that document the inputs for calculation:

| Input Variable | Variations | Base Case 1 Average Value | Base Case 2 Average Value | Measure Case Average Value | Reference Section |
| --- | --- | --- | --- | --- | --- |
| Electric Savings | CZ, BT, BV | 283 | N/A | 283 | Section 1.4.1 |
| Gas Savings | CZ, BT, BV | 0.060 | N/A | 0.060 | Section 1.4.1 |
| Hours of operation | N/A | N/A | N/A | N/A | N/A |
| Full Cost | REA | 44.15 | N/A | 44.15 | Section 1.4.1 |
| Incremental Cost | REA | 44.15 | N/A | 44.15 | Section 1.4.1 |
| EUL /RUL | REA | 15 | N/A | 15 |  |
| NTG | One | 0.6 | N/A | 0.6 | Section 1.4.1 |
| ISR | Applies -- Yes / No | 1 | N/A | 1 | Section 1.4.1 |
| TOU Factor | A/C projects only | N/A | N/A | N/A | Section 1.4.5 |

# Section 2. Calculation Methods

The saving for this measure is from DEER 2008 and generated through MASControl V3.00.19. The nonresidential technology code selected was D08-NE-GrocRefg-FltSucPres-SSTReset.The grocery building type was selected for PG&E climate zones (1,2,3,4,5,11,12,13,16) and vintage codes 75, 85, 96, 03, and 07.

# Section 3. Load Shapes

## 3.1 Base Case Load Shapes

The base case load shape, characterized by the PG&E E3 Calculator, is “Commercial Refrigeration.”

## 3.2 Measure Load Shapes

The measure load shape, characterized by the PG&E E3 Calculator, is “Commercial Refrigeration.”

# Section 4. Base Case & Measure Costs

| Measure Application Type | Measure Life Basis | First Baseline Period Full Measure Cost (RUL) | Second Baseline Period Full Measure Cost (EUL – RUL) |
| --- | --- | --- | --- |
| REA (Retrofit Add on) | EUL | Calculated as Full Gross Measure Cost | N/A |

## 4.1 Base Case(s) Costs

The following Measure Application type is appropriate to this measure. The Base Case Costs are:

| Measure Code | Measure Application Type | Baseline | Equipment Cost | Labor / Installation Cost | Maintenance / Other Cost | Total Base Case Cost |
| --- | --- | --- | --- | --- | --- | --- |
| R119 | REA | Existing | $0 | $0 | $0 | $0 |

All costs are noted as $ per measure unit

## 4.2 Measure Case Costs

The following Measure Application type is appropriate to this measure. The Measure Case Costs are:

| Measure Code | Measure Application Type | Baseline | Equipment Cost | Labor / Installation Cost | Maintenance / Other Cost | Total Measure Case Cost |
| --- | --- | --- | --- | --- | --- | --- |
| R119 | REA | Existing | $14.69 | $29.46 | $0 | $44.15 |

All costs are noted as $ per measure unit

## 4.3 Incremental & Full Measure Costs

| Measure Application Type | Full Measure Cost (RUL Period/First Baseline) | Full Measure Cost (EUL-RUL Period/ Second Baseline) | Incremental Measure Cost |
| --- | --- | --- | --- |
| REA | Measure Equipment Cost +Measure Labor Cost | N/A | Measure Equipment Cost + Measure Labor Cost |

### 4.3.1 Full Measure Cost

This Measure Application type is REA for a single baseline period, so the Full Measure Cost (FMC) is represented by the equation below:

FMC = Measure Equipment Cost + Measure Labor Cost

FMC = $14.69/ ton + $29.46/ ton =  $44.15/ ton

*Note: Various complicated price fluctuations are not addressed in these equations, such as future costs due to inflation in labor, future costs due to deflation in material cost, and other variables that cannot be accurately described at this time.

### 4.3.2  Incremental Measure Costs

This Measure Application type is Retrofit Add On (REA).  The Incremental Measure Cost (IMC) is represented by the equation below as there exists no base case with which to compare the measure to:

IMC = Measure Equipment Cost + Measure Labor Cost

Using this equation, the incremental measure cost for the measure in this workpaper is $44.15 per ton.

IMC = $14.69 per ton + $29.46 per ton =  $44.15 per ton

Summary Table for Section 4

| Measure ID | Measure Application Type | Base Case Total Cost | Measure Case Total Cost | Gross Measure Case Cost | Incremental Measure Cost |
| --- | --- | --- | --- | --- | --- |
| R119 | REA | $0 | $44.15 | $44.15 | $44.15 |

# Appendices

## A. (1.4.1) DEER Base Case and Measure Case Information

Electric Savings (ΔW):

| Building type | Bldg Vintage | Climate Zone | Electric Savings Watts | Deer units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- |
| GRO | 03 | CZ01 | 15.200 | tons | 2008 | D03-220 |
| GRO | 03 | CZ02 | 40.912 | tons | 2008 | D03-220 |
| GRO | 03 | CZ03 | 13.646 | tons | 2008 | D03-220 |
| GRO | 03 | CZ04 | 26.304 | tons | 2008 | D03-220 |
| GRO | 03 | CZ05 | 20.031 | tons | 2008 | D03-220 |
| GRO | 03 | CZ11 | 33.132 | tons | 2008 | D03-220 |
| GRO | 03 | CZ12 | 18.391 | tons | 2008 | D03-220 |
| GRO | 03 | CZ13 | 30.177 | tons | 2008 | D03-220 |
| GRO | 03 | CZ16 | 36.158 | tons | 2008 | D03-220 |
| GRO | 07 | CZ01 | 9.413 | tons | 2008 | D03-220 |
| GRO | 07 | CZ02 | 12.176 | tons | 2008 | D03-220 |
| GRO | 07 | CZ03 | 2.268 | tons | 2008 | D03-220 |
| GRO | 07 | CZ04 | 3.982 | tons | 2008 | D03-220 |
| GRO | 07 | CZ05 | 1.313 | tons | 2008 | D03-220 |
| GRO | 07 | CZ11 | 32.058 | tons | 2008 | D03-220 |
| GRO | 07 | CZ12 | 10.184 | tons | 2008 | D03-220 |
| GRO | 07 | CZ13 | 11.217 | tons | 2008 | D03-220 |
| GRO | 07 | CZ16 | 15.293 | tons | 2008 | D03-220 |
| GRO | 75 | CZ01 | 29.5875 | tons | 2008 | D03-220 |
| GRO | 75 | CZ02 | 53.0066 | tons | 2008 | D03-220 |
| GRO | 75 | CZ03 | 40.7274 | tons | 2008 | D03-220 |
| GRO | 75 | CZ04 | 35.6264 | tons | 2008 | D03-220 |
| GRO | 75 | CZ05 | 17.2158 | tons | 2008 | D03-220 |
| GRO | 75 | CZ11 | 54.1262 | tons | 2008 | D03-220 |
| GRO | 75 | CZ12 | 45.6171 | tons | 2008 | D03-220 |
| GRO | 75 | CZ13 | 50.8956 | tons | 2008 | D03-220 |
| GRO | 75 | CZ16 | 42.6660 | tons | 2008 | D03-220 |
| GRO | 85 | CZ01 | 31.0056 | tons | 2008 | D03-220 |
| GRO | 85 | CZ02 | 57.8061 | tons | 2008 | D03-220 |
| GRO | 85 | CZ03 | 40.6397 | tons | 2008 | D03-220 |
| GRO | 85 | CZ04 | 38.8936 | tons | 2008 | D03-220 |
| GRO | 85 | CZ05 | 17.8846 | tons | 2008 | D03-220 |
| GRO | 85 | CZ11 | 52.1035 | tons | 2008 | D03-220 |
| GRO | 85 | CZ12 | 41.8047 | tons | 2008 | D03-220 |
| GRO | 85 | CZ13 | 45.1955 | tons | 2008 | D03-220 |
| GRO | 85 | CZ16 | 36.4641 | tons | 2008 | D03-220 |
| GRO | 96 | CZ01 | 10.3514 | tons | 2008 | D03-220 |
| GRO | 96 | CZ02 | 28.2625 | tons | 2008 | D03-220 |
| GRO | 96 | CZ03 | 17.4673 | tons | 2008 | D03-220 |
| GRO | 96 | CZ04 | 19.7229 | tons | 2008 | D03-220 |
| GRO | 96 | CZ05 | 11.0086 | tons | 2008 | D03-220 |
| GRO | 96 | CZ11 | 27.8790 | tons | 2008 | D03-220 |
| GRO | 96 | CZ12 | 28.2943 | tons | 2008 | D03-220 |
| GRO | 96 | CZ13 | 29.5612 | tons | 2008 | D03-220 |
| GRO | 96 | CZ16 | 40.2717 | tons | 2008 | D03-220 |

Gas Savings (ΔTh):

| Building type | Bldg Vintage | Climate Zone | Interactive Only? Yes / No | Gas Savings Therms | Deer units | DEER Version | Impact IDs |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GRO | 03 | CZ01 | Yes | 0.08321 | tons | 2008 | D03-220 |
| GRO | 03 | CZ02 | Yes | 0.06278 | tons | 2008 | D03-220 |
| GRO | 03 | CZ03 | Yes | 0.07759 | tons | 2008 | D03-220 |
| GRO | 03 | CZ04 | Yes | 0.06395 | tons | 2008 | D03-220 |
| GRO | 03 | CZ05 | Yes | 0.08166 | tons | 2008 | D03-220 |
| GRO | 03 | CZ11 | Yes | 0.05098 | tons | 2008 | D03-220 |
| GRO | 03 | CZ12 | Yes | 0.06215 | tons | 2008 | D03-220 |
| GRO | 03 | CZ13 | Yes | 0.05139 | tons | 2008 | D03-220 |
| GRO | 03 | CZ16 | Yes | 0.07082 | tons | 2008 | D03-220 |
| GRO | 07 | CZ01 | Yes | 0.08140 | tons | 2008 | D03-220 |
| GRO | 07 | CZ02 | Yes | 0.05995 | tons | 2008 | D03-220 |
| GRO | 07 | CZ03 | Yes | 0.06123 | tons | 2008 | D03-220 |
| GRO | 07 | CZ04 | Yes | 0.04742 | tons | 2008 | D03-220 |
| GRO | 07 | CZ05 | Yes | 0.06034 | tons | 2008 | D03-220 |
| GRO | 07 | CZ11 | Yes | 0.05459 | tons | 2008 | D03-220 |
| GRO | 07 | CZ12 | Yes | 0.04475 | tons | 2008 | D03-220 |
| GRO | 07 | CZ13 | Yes | 0.04301 | tons | 2008 | D03-220 |
| GRO | 07 | CZ16 | Yes | 0.06518 | tons | 2008 | D03-220 |
| GRO | 75 | CZ01 | Yes | 0.07129 | tons | 2008 | D03-220 |
| GRO | 75 | CZ02 | Yes | 0.05523 | tons | 2008 | D03-220 |
| GRO | 75 | CZ03 | Yes | 0.07126 | tons | 2008 | D03-220 |
| GRO | 75 | CZ04 | Yes | 0.04480 | tons | 2008 | D03-220 |
| GRO | 75 | CZ05 | Yes | 0.06988 | tons | 2008 | D03-220 |
| GRO | 75 | CZ11 | Yes | 0.04066 | tons | 2008 | D03-220 |
| GRO | 75 | CZ12 | Yes | 0.05659 | tons | 2008 | D03-220 |
| GRO | 75 | CZ13 | Yes | 0.04853 | tons | 2008 | D03-220 |
| GRO | 75 | CZ16 | Yes | 0.05528 | tons | 2008 | D03-220 |
| GRO | 85 | CZ01 | Yes | 0.07337 | tons | 2008 | D03-220 |
| GRO | 85 | CZ02 | Yes | 0.04970 | tons | 2008 | D03-220 |
| GRO | 85 | CZ03 | Yes | 0.06954 | tons | 2008 | D03-220 |
| GRO | 85 | CZ04 | Yes | 0.06195 | tons | 2008 | D03-220 |
| GRO | 85 | CZ05 | Yes | 0.06883 | tons | 2008 | D03-220 |
| GRO | 85 | CZ11 | Yes | 0.05063 | tons | 2008 | D03-220 |
| GRO | 85 | CZ12 | Yes | 0.04995 | tons | 2008 | D03-220 |
| GRO | 85 | CZ13 | Yes | 0.04429 | tons | 2008 | D03-220 |
| GRO | 85 | CZ16 | Yes | 0.06416 | tons | 2008 | D03-220 |
| GRO | 96 | CZ01 | Yes | 0.07440 | tons | 2008 | D03-220 |
| GRO | 96 | CZ02 | Yes | 0.05008 | tons | 2008 | D03-220 |
| GRO | 96 | CZ03 | Yes | 0.06521 | tons | 2008 | D03-220 |
| GRO | 96 | CZ04 | Yes | 0.05996 | tons | 2008 | D03-220 |
| GRO | 96 | CZ05 | Yes | 0.06930 | tons | 2008 | D03-220 |
| GRO | 96 | CZ11 | Yes | 0.03868 | tons | 2008 | D03-220 |
| GRO | 96 | CZ12 | Yes | 0.05778 | tons | 2008 | D03-220 |
| GRO | 96 | CZ13 | Yes | 0.04180 | tons | 2008 | D03-220 |
| GRO | 96 | CZ16 | Yes | 0.05433 | tons | 2008 | D03-220 |

# References:

2004-2005 Database for Energy Efficiency Resources, Version 2.01, October 26, 2005,  EEM D03-220 http://eega.cpus.ca.gov/deer.

Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls from DEER for Energy-Efficient Resources: Version 2008 found at: http://www.deeresources.com/index.php?option=com_content&view=article&id=65&Itemid=57 Under:  Technology and Measure Cost Data  Tab: NR-Commercial Refrigeration Cell:  E41 and G41.

.

Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls from DEER for Energy-Efficient Resources: Version 2008 found at: http://www.deeresources.com/index.php?option=com_content&view=article&id=65&Itemid=57 Under:  Technology and Measure Cost Data  Tab: NR-Commercial Refrigeration Cell:  E41 and G41.

ii

ii

The DEER Measure Cost Data Users Guide found on www.deeresources.com under DEER2011 Database Format hyperlink, DEER2011 for 13-14, spreadsheet SPTdata_format-V0.97.xls.