Work Paper SCE13CC008

Revision 1

Southern California Edison Company

Commercial Kitchen Exhaust Hoods Demand Controlled Ventilation

# At-a-Glance Summary

| Applicable Measure Codes: | FS-17337 Demand Control Ventilation Hood Control |
| --- | --- |
| Measure Description: | Commercial Kitchen Exhaust Hoods Demand Controlled Ventilation |
| Base Case Description: | Source: SCE and PG&E Case Studies Commercial kitchen hood with “on” or “off” control strategy |
| Energy Impact Common Units: | per HP |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | Source: EUL_Summary_10-1-08.xls 15 (HVAC-EMS) |
| Measure Application Type: | Retrofit – Add-On (REA) |
| Net-to-Gross Ratios: | Source: DEER2011_NTGR_2012-05-16.xls 0.6 (Com-Default>2yrs) |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13CC008.0 | Yes | 12/26/12 | Yun Han/SCE | Updated from WPSCNRCC0008.3 with: - Latest WP template v0.4 - DEER 2011 default NTG - Removed RET, NEW, added REA |
| SCE13CC008.1 | Yes | 03/25/14 | Michael Crayne/PECI | -Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. Updated with: - Latest WP template 2013-14 v0 - Technical description, Non-DEER Study Review, Energy Savings Calculations, and Measure Cost information from PG&E work paper PGECOFST116R3 - Relevant Title 24 2013 requirements |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the replacement of a manual on/off switch and magnetic relay or motor starter ventilation control for commercial kitchen exhaust hoods with a control system that varies the exhaust rate based on the energy and effluent output from the cooking appliances. The measure requires the installation of temperature sensor(s) in the hood exhaust collar  or within the hood, and/or an optic sensor on the end of the hood or within the hood that senses cooking conditions and allows the system to automatically vary the rate of exhaust and make-up (ventilation) air by adjusting unit fan speeds accordingly.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| FS-17337 | Demand Control Ventilation Hood Control |

When installing a control system for their kitchen exhaust hood, customers must use a Demand Control Kitchen Ventilation System (DCKV) system and also either a temperature or optic sensor that senses cooking conditions.  The DCKV system must be used in conjunction with a variable-speed drive (VSD) on the fan motor.

A Project Installation Worksheet must be submitted with the rebate application. Only pre-approved control systems will qualify for an incentive. The incentive applies towards the purchase and installation of a new commercial kitchen exhaust hood control system installed in an existing or new dedicated commercial kitchen exhaust hood and makeup air system. For new hoods, kitchen exhaust hood DCKV may be required by Title 24 2013 [355] in certain circumstances. See Section 1.4.2 Codes and Standards Analysis in this work paper for more details on when kitchen exhaust hood DCKV is required.

The measure described in this WP can only be installed in the building types specified in Table 12.

## 1.2 Technical Description

Modern commercial kitchen ventilation has advanced beyond basic heat and smoke removal at the lowest first cost to systems that are more energy efficient and require less maintenance. In addition, there is a greater emphasis on comfort, kitchen indoor air quality, reduced noise levels and improved fire safety.

Conventional kitchen ventilation controls mainly consist of a manual on/off switch and a magnetic relay or motor starter for each fan. Exhaust and makeup air fans operate either at 100% speed or not at all. Occasionally, two-speed motor systems have been employed, which rely on cooks to manually switch from low to high-speed and vice versa, which is an improvement but not a global solution for the lack of control over kitchen exhaust. Today’s state-of-the-art commercial kitchen demand controlled kitchen ventilation (DCKV) system is essentially a demand-ventilation-based energy management system for commercial kitchen exhaust hoods that minimizes fan energy use by reducing the exhaust and makeup air fan speed and associated energy consumption when little or no cooking is occurring. Furthermore, as a function of the exhaust fan speed and associated airflow reduction, outdoor makeup air heating and cooling energy is also reduced. In addition, the kitchen ambient noise level is significantly decreased.

The DCKV system is equipped with sensors and a microprocessor-based controller used in conjunction with variable speed drives for the fan motors, automatically modulating fan speed based on cooking load and/or time of day. The minimum ventilation rate is based on the energy and effluent output from the cooking appliances (i.e., the more heat and smoke/vapor generated, the more ventilation needed). Determining this involves installing temperature sensor(s) in the hood exhaust collar or within the hood, and/or an optic sensor(s) within the hood that senses cooking conditions, allowing the control system to automatically vary the rate of exhaust to what is needed by adjusting the fan speed accordingly. Effective controller programming, performed during system commissioning, that is tailored for each equipment line and accompanying hood achieves optimal performance and savings. Cost-effectiveness for a particular facility increases proportionally with the ventilation system airflow rate, applied fan power and operating time.

## 1.3 Measure Application Type

Note: See Appendix A for a comparison of the application types used by and incorporated into SCE systems versus the application types available in the newest revision of DEER 2014. Appendix A will serve as a translation between the outputs of this workpaper and application types used by READi.

The delivery method is Financial Support – Down-stream Incentive – Deemed.

The install type is Retrofit Add-on (REA). This is a subtype of RET that is specifically for adding a piece of equipment to an existing system or equipment to make the overall system  or equipment more efficient, i.e. adding an economizer, controls, or a VSD.

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

The 2014 Database for Energy Efficient Resources (DEER) does not contain demand control ventilation for exhaust hood measures. The only kitchen equipment measures contained in DEER are dishwashers, freezers, refrigerators, and technologies for cooking and food-holding equipment. DEER does contain measures for reducing over-ventilation as well as adding VSDs to supply fan motors on damper-controlled VAV systems, however both of these measures pertain to space conditioning systems that do not operate in the same manner as kitchen hood exhaust systems.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER does not contain this type of measure. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | All | 0.6 |

*Denotes that the column is taken from the DEER NTG Table.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | Food Service |
| Measure Case UseSubCats | Cooking |
| Measure Case TechGroups | Food Service Equipment |
| Measure Case TechTypes | Non-DEER |
| Base Case TechGroups | Food Service Equipment |
| Base Case TechTypes | Non-DEER |

### 1.4.2 Codes and Standards Analysis

Current relevant requirements for commercial kitchen ventilation are contained in Title 24 2013 [355], Section 140.9(b)2B. Section 140.9(b)2B gives requirements for kitchens that have greater than 5,000 cfm total Type I and Type II kitchen hood exhaust and lists four compliance options, one of which is installing demand controlled ventilation on 75% of exhaust air. The exact code language is shown below:

These requirements apply to new kitchen exhaust hood installations, while existing hoods are exempt from these requirements.

For new hoods installed in kitchens that have more than 5,000 cfm of total hood exhaust, if a DCKV system is installed and none of the other compliance options are met, the DCKV system would be considered to be required by code. This measure would therefore be at code level and would have no savings beyond code.

In addition to installing DCKV, new kitchens may also comply with code if at least 50% of replacement air is transfer air, energy recovery devices with a minimum sensible effectiveness of 40% are installed on at least 50% of the total exhaust, or at least 75% of makeup air is unheated or heated to a maximum of 60 degrees and uncooled or cooled without mechanical cooling. If one of these alternate compliance options is met, demand controlled kitchen ventilation would not be required by code. However, in these situations the DCKV system would be considered redundant and the energy savings are expected to be reduced.

For new kitchens that have less than 5,000 cfm of total hood exhaust, the code requirements do not apply and DCKV is an applicable measure.

Title 24 2008 [208] and 2014 Title 20 [422] do not contain any relevant language and existing hoods are exempt from the Title 24 2013 [355] requirements, thus this is an applicable REA measure for existing commercial kitchen exhaust hood systems installed under previous code requirements.

These measures do not fall under Federal DOE or EPA Energy Regulations.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2008) | N/A | N/A |
| Title 20 (2014) | N/A | N/A |
| Title 24 (2013) | 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings, Section 140.9(b)2, pg. 200-201 | Jul. 1, 2014 |

### 1.4.3 Non-DEER Study Review

The base case and measure case data used in this work paper were collected from field-monitored case studies conducted by the PG&E Food Service Technology Center (PG&E FSTC) and the Southern California Edison Foodservice Technology Center (SCE FTC) [B] at a total of eleven sites that represent a range of demand controlled ventilation installations. Table 7 shows the nameplate rated exhaust fan horsepower, the Base Case and Measure Case average fan power and fan energy consumption, and the estimated exhaust fan speed (airflow rate) reduction percentage (calculated using the fan affinity laws relating the fan power to the fan speed) for each facility. The daily energy savings for each site were multiplied by 360 days/year to determine the annual energy savings. The averages of these values are used in this work paper to determine the energy savings for this measure.

Table 7 Summary of Demand Controlled Ventilation Case Studies

|  | Institutional Cafeteria | Casual Dining Restaurant | Hotel Main Kitchen | Supermarket | University Dining | University Dining | Hotel Main Kitchen | Hotel Main Kitchen | Quick Service Restaurant | Quick Service Restaurant | Quick Service Restaurant | Average |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated Exhaust Fan Horsepower (HP) | 6 | 3 | 15 | NA | 8 | 20 | 21 | 14 | 3 | 4 | 2.5 | 9.65 |
| Base Case Total Fan Power (kW) | 7.3 | 3.9 | 14.0 | 8.49 | 12.7 | 12.0 | 27.9 | 12.1 | 4.7 | 5.2 | 2.9 | 10.11 |
| Measure Case Total Fan Power (kW) | 1.9 | 2.1 | 5.3 | 2.33 | 5.8 | 6.6 | 10.7 | 5.2 | 2.9 | 2.0 | 1.4 | 4.20 |
| Fan Power Reduction (kW) | 5.4 | 1.8 | 8.7 | 6.16 | 6.9 | 5.4 | 17.2 | 6.9 | 1.8 | 3.2 | 1.5 | 5.91 |
| Estimate Exhaust Fan Speed Reduction (%) | 36 | 19 | 28 | 35 | 23 | 18 | 27 | 25 | 15 | 27 | 22 | 25 |
| Base Case Daily Fan Energy Consumption (kWh/day) | 137.90 | 58.90 | 336.00 | 117.90 | 216.60 | 168.00 | 670.00 | 291.00 | 72.00 | 67.00 | 44.00 | 198.12 |
| Measure Case Daily Fan Energy Consumption (kWh/day) | 34.80 | 31.60 | 127.00 | 30.70 | 97.90 | 77.00 | 257.00 | 125.00 | 45.00 | 26.00 | 23.00 | 79.55 |
| Base Case Annual Fan Energy Consumption (kWh/yr) | 49,644 | 21,204 | 120,960 | 42,444 | 77,976 | 60,480 | 241,200 | 104,760 | 25,920 | 24,120 | 15,840 | 71,323 |
| Measure Case Annual Fan Energy Consumption (kWh/yr) | 12,528 | 11,376 | 45,720 | 11,052 | 35,244 | 27,720 | 92,520 | 45,000 | 16,200 | 9,360 | 8,280 | 28,636 |
| Annual Fan Energy Savings (kWh/yr) | 37,116 | 9,828 | 75,240 | 31,392 | 42,732 | 32,760 | 148,680 | 59,760 | 9,720 | 14,760 | 7,560 | 42,686 |

To better characterize the commercial kitchen exhaust hood market, SCE FTC, PG&E FSTC, and Honeywell/Melink (a manufacturer of kitchen hood DCKV systems) gathered data from a number of additional commercial kitchen sites with exhaust hood DCKV systems. Exhaust fan horsepower, exhaust cfm, operating hours, and DCKV system cost were documented for a total of 72 sites. This data is summarized in attachment [D]. The averages of these values are used in this work paper to determine the gas savings and cost for this measure.

The total data set used for this workpaper includes the eleven case study sites [B] at which energy consumption was measured for the base and measure cases, and the 72 field sites [D] for which DCKV system specifications and costs were documented. Data from both sets was used to inform the savings and cost calculations.

### 1.4.4 Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 8 below identifies the value/methodology used for the measures in this work paper.

Table 8 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-EMS | Non-Residential | HVAC - Miscellaneous | Energy Management System | 15 | 5 |

# Section 2. Energy Savings & Demand Reduction Calculations

### 2.1 Electric Energy Savings Calculation

The electric energy savings for this measure were based on the eleven case studies conducted by PG&E FSTC and SCE FST [B]. The sites were power-meter-monitored with and without the Demand-Controlled Kitchen Ventilation System enabled to obtain Base Case and Measure Case data. The results from the eleven case studies were averaged to obtain the average power reduction values (and estimated average fan speed reduction values to be used later for gas saving calculations). The energy reduction values were divided by the respective rated exhaust fan horsepower values from each site and then averaged to yield a single normalized and unitized savings estimate for incentive simplicity.

The rated exhaust fan horsepower was selected as the single, standard unit of measure because of the larger degree of variance in makeup air system size, type and complexity (e.g., some facilities do not have dedicated make up air units, some have a high percentage of transfer air from rooftop equipment serving areas outside the kitchen, some DCKV systems are installed as exhaust-only controls, etc.) It is important to note that although the energy savings have been normalized to the rated exhaust fan horsepower, the estimated energy savings include both the exhaust fan and the makeup air fan energy of the average system. Note that the electric savings do not account for any coincidental cooling savings due to reduced makeup airflow in the Measure Case.

Fan energy consumption for each case was calculated according to Equation 1.

Equation 1 Annual Energy Consumption

Annual Energy Consumption (kWh/yr) = Power (kW) × Daily Operating Hours × Days Per Year

Energy consumption was calculated for each of the 11 case study sites assuming 360 days per year. The individual and average savings results for the case studies are listed in Table 7.

The normalized fan energy savings estimate is 4,423 kWh/yr/Exh HP, and the normalized fan energy cost savings estimate is $575/yr/Exh HP. The prescriptive normalized energy reduction and energy cost reduction are summarized in Table 9.

Table 9 Summary of Demand Controlled Kitchen Ventilation Fan Energy Savings*

| Average Rated Exhaust Fan Power (HP) | 9.65 |
| --- | --- |
| Average Base Case Total Fan Power (kW) | 10.11 |
| Average Measure Case Total Fan Power (kW) | 4.20 |
| Average Base Case Annual Fan Energy Consumption (kWh/yr) | 71,323 |
| Average Measure Case Annual Fan Energy Consumption (kWh/yr) | 28,636 |
| Average Annual Fan Energy Savings (kWh/yr) | 42,686 |
| Normalized Base Case Fan Energy Consumption (kWh/yr/Exh HP) | 7,391 |
| Normalized Measure Case Fan Energy Consumption (kWh/yr/Exh HP) | 2,968 |
| Normalized Fan Energy Savings (kWh/yr/Exh HP) | 4,423 |
| Applied Electric Rate ($/kWh) | $0.13 |
| Average Base Case Annual Fan Energy Cost ($/yr) | $9,272 |
| Average Measure Case Annual Fan Energy Cost ($/yr) | $3,723 |
| Average Annual Fan Energy Cost Savings ($/yr) | $5,549 |
| Normalized Fan Energy Cost Savings ($/yr/Exh HP) | $575 |

*Based on the average results from eleven case studies

### 2.2 Demand Reduction Calculation

The demand reduction estimation is based on Base Case and Measure Case monitored power data from the eleven PG&E FSTC and SCE FST [B] case study sites. The normalized demand (kW/Exh HP) is based on the average rated exhaust fan horsepower of the eleven case study sites. It is important to note that although the demand reduction has been normalized per rated exhaust fan horsepower, the total system demand reduction reflects the total fan power reduction of the exhaust and makeup air fans of an average system. The normalized demand reduction for the eleven sites was 0.612 kW per rated exhaust fan horsepower. Applying a Coincidence Factor of 0.9 per the DEER methodology [26] yields a Coincident Demand Reduction of 0.551 kW. Table 10 shows the Base Case and Measure Case demand, and average and normalized demand reduction.

Table 10 Summary of Demand Controlled Kitchen Ventilation Fan Demand Savings*

| Average Rated Exhaust Fan Power (HP) | 9.65 |
| --- | --- |
| Average Base Case Total Fan Power (kW) | 10.11 |
| Average Measure Case Total Fan Power (kW) | 4.20 |
| Average Demand Reduction (kW) | 5.91 |
| Normalized Demand Reduction (kW/Exh HP) | 0.612 |
| Coincident Demand Reduction (kWh/Exh HP) | 0.551 |

*Based on the average results from eleven case studies

### 2.3 Gas Energy Savings Calculation

Gas energy savings were determined using data from both the eleven case study sites [B] and the 72 field sites [D].

The average base case outdoor air load thermal requirements determined by using the Outdoor Airload Calculator (OAC) [F] for the 16 climate zones in California and inputting the average airflow rate and operating time values from the 72 field sites documented by PG&E FSTC, SCE FTC and Honeywell/Melink [D]. The average values used from the field data included a 14,000 cfm exhaust airflow rate and 17 hours of operation (input time: 7:00 AM to 12 midnight). The outdoor makeup airflow rate was taken to be 11,200 cfm or 80% of the exhaust airflow rate (specification typical rule of thumb). The inputs also assumed a heating setpoint of 65°F, no dehumidification and no lock-out months. The output is summarized in Attachment [E].

The gas energy savings were based on an assumed heating system efficiency of 80%, and a 25% average reduction in fan speed (and thus airflow rate) as determined from the eleven SCE FTC and PG&E FSTC [B] case study sites.

Equation 2 Annual Gas Savings

Annual Gas Savings (therm)=O.A.C. Heating Output (kBtu)×Average Fan Speed Reduction %Heating System Efficiency×100(kBtutherm)

The normalized natural gas savings are based on savings per rated exhaust fan horsepower (correlating average airflow rate cfm to average rated exhaust fan horsepower). The 72-site average was 14.3 rated exhaust fan horsepower. For incentive simplicity, the facility types and the climate zones were averaged to generate a single normalized gas savings value. The normalized natural gas savings for 16 climate zones averaged 101 therms per rated exhaust fan horsepower and ranged between a minimum of 38 and a maximum of 219 therms per rated exhaust fan horsepower. The normalized gas savings summary is shown in Table 11.

Table 11 Summary of Gas Savings by Climate Zone

| Climate Zone | OAC Output (kBtu/yr) | Base Case Heating Energy (kBtu/yr) | Measure Case Heating energy (kBtu/yr) | Natural Gas Savings (therms/yr) | Natural Gas Savings (therms/yr/Exh HP) |
| --- | --- | --- | --- | --- | --- |
| 1 | 777,247 | 971,559 | 729,457 | 2,421 | 169 |
| 2 | 609,224 | 761,530 | 571,765 | 1,898 | 133 |
| 3 | 510,934 | 638,668 | 479,518 | 1,591 | 111 |
| 4 | 466,873 | 583,591 | 438,167 | 1,454 | 102 |
| 5 | 486,129 | 607,661 | 456,239 | 1,514 | 106 |
| 6 | 296,319 | 370,399 | 278,099 | 923 | 65 |
| 7 | 245,283 | 306,604 | 230,201 | 764 | 53 |
| 8 | 291,176 | 363,970 | 273,273 | 907 | 63 |
| 9 | 260,834 | 326,043 | 244,796 | 812 | 57 |
| 10 | 312,989 | 391,236 | 293,744 | 975 | 68 |
| 11 | 533,354 | 666,693 | 500,560 | 1,661 | 116 |
| 12 | 539,166 | 673,958 | 506,015 | 1,679 | 117 |
| 13 | 427,560 | 534,450 | 401,271 | 1,332 | 93 |
| 14 | 505,617 | 632,021 | 474,528 | 1,575 | 110 |
| 15 | 165,481 | 206,851 | 155,306 | 515 | 36 |
| 16 | 964,179 | 1,205,224 | 904,895 | 3,003 | 210 |
| Average | 462,023 | 577,529 | 433,615 | 1,439 | 101 |

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Economy_cycle-Ret load shape. See Table 12 for a list of all Building Types and Load Shapes. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 12 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Education - Primary School | Small_Office | Economy_cycle-Ret |
| Education - Secondary School | Small_Office | Economy_cycle-Ret |
| Education - Relocatable Classroom | Small_Office | Economy_cycle-Ret |
| Education - Community College | College_University | Economy_cycle-Ret |
| Education – University | College_University | Economy_cycle-Ret |
| Grocery | Small_Office | Economy_cycle-Ret |
| Food Store | Small_Office | Economy_cycle-Ret |
| Health/Medical – Hospital | College_University | Economy_cycle-Ret |
| Health/Medical - Nursing Home | Small_Office | Economy_cycle-Ret |
| Lodging – Hotel | Small_Office | Economy_cycle-Ret |
| Misc – Commercial | Misc._Commercial | Economy_cycle-Ret |
| Office – Large | Large_Office | Economy_cycle-Ret |
| Office – Small | Small_Office | Economy_cycle-Ret |
| Restaurant - Fast-Food | Restaurant | Economy_cycle-Ret |
| Restaurant - Sit-Down | Restaurant | Economy_cycle-Ret |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The Base Case is a standard commercial kitchen ventilation system with single speed exhaust and makeup air fans and a simple on/off control. Since the commercial kitchen ventilation system is required for both standard systems and demand controlled ventilation systems, the Base Case cost for these measures is zero.  Additionally, for REA measures, a base case cost is not used.

## 4.2 Measure Case Cost

The measure cost was based on installed demand controlled ventilation system costs documented by PG&E FSTC, SCE FTC and Honeywell/Melink [D] The costs of the retrofit include the control system, the sensor arrays, and variable speed fan control upgrades (and fan or motor upgrades where required). Installation costs also include the cost of installing the demand ventilation control system and sensor array wiring between the sensors, control system and rooftop fan equipment.

The cost was normalized to the 72-site average rated exhaust system horsepower. Table 13 summarizes the normalized measure cost calculation.

Table 13 Normalized Measure Cost

| Average DCKV System Installed Cost ($) | $28,474 |
| --- | --- |
| Average Rated Exhaust Fan Horsepower (HP) | 14.3 |
| Normalized Incremental Measure Cost ($/HP) | $1,991 |

Costs with climate zone multipliers factored in can be found in attachment 1 [A].

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For REA, GMC is represented by the equation below:

GMC = Measure Equipment Cost + Measure Labor Cost

The Gross Measure Cost is obtained from costs documented by PG&E FSTC, SCE FTC and Honeywell/Melink [D] and is calculated as a cost per exhaust fan horsepower ($/HP). The GMC includes both materials and labor. See Table 13 above for the calculated GMC.

### 4.3.2 Incremental Measure Cost

For REA measures the Incremental Measure Cost is the same as the Gross Measure Cost.

# Attachments

1.

2.

3.

4.

5.

6.

7.

8.

9.

10.

11.

# References

[26]

[31]

[208]

[351]

[355]

[422]

[436]

[A] Attachment 1 - Calculation Template v2.2.xlsm

[B] Attachments 2, 5-8, 11 – Demand Controlled Kitchen Ventilation Field Studies

2.	Demand Control Ventilation for Commercial Kitchen Hoods, Prepared by Design & Engineering Services, Southern California Edison, June 30th, 2009

5. 	Fisher-Nickel, Inc., 2004. Demand Ventilation in Commercial Kitchens—An Emerging Technology Case Study. Melink Intelli-Hood® Controls—Commercial Kitchen Ventilation System Intercontinental Mark Hopkins Hotel.

6. 	Fisher-Nickel, Inc., 2006. Demand Ventilation in Commercial Kitchens—An Emerging Technology Case Study. Melink Intelli-Hood® Controls—Supermarket Application.

7. 	California Energy Commission (CEC), 2006. Public Interest Energy Research (PIER) Program Case Study: Demand Ventilation Control in Commercial Kitchens, UC Berkeley—Clark Kerr Campus.

8. 	California Energy Commission (CEC), 2007. Public Interest Energy Research (PIER) Program Case Study: Demand Ventilation Control in Commercial Kitchens, UC Santa Barbara— Carrillo Dining Commons.

11.	Fisher, Don, 2013. Future of DCV For Commercial Kitchens. ASHRAE Journal, February 2013.

[C] Attachment 3 – SCE Study Savings – savings spreadsheet.xls

[D] Attachment 9 – Exhaust CFM and Cost Field Data

[E] Attachment 10 - Outdoor Airload Calculator Results

[F] Outdoor Airload Calculator. 1999. V1.3. Architectural Energy Corporation

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (NC) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |