Work Paper PGECODHW124

High efficiency DHW Boiler (>75 MBTU/hr)

Revision # 0

Pacific Gas & Electric Company

Customer Energy Solutions Department

High efficiency DHW Boiler (>75 MBTU/hr)

Measure Code DWHC4

# At-A-Glance Summary

| Applicable Measure Codes: |  | DWHC4 |  |
| --- | --- | --- | --- |
| Measure Description: | This measure encourages replacement of hot water boilers with units of over 90% thermal efficiency. Minimum 75 MBtuh input rating. |  |  |
| Energy Impact Common Units: | Per MBtuh input rating |  |  |
| Base Case Description: | Source: CA Title 20 Regulations: 80% Thermal Efficiency |  |  |
| Base Case Energy Consumption: | Source: Source: DEER, D11v4.00-098 & 100 The energy consumption for Large Gas Storage Water Heater per MBtuh with efficiency compliant with Title 20 (Baseline Thermal efficiency of 80%). |  |  |
| Measure Energy Consumption: | Source: Source: DEER, D11v4.00-098 & 100 (Measure Thermal efficiency of 90% and 90%). |  |  |
| Energy Savings (Base Case – Measure) | Source: DEER, D11v4.00-098 & 100 (Measure Thermal efficiency of 90% and 90%). |  |  |
| Costs Common Units: | $ Per MBtuh of rated input |  |  |
| Base Case Equipment Cost ($/unit): | Source: DEER 2008 Cost Values and Summary Documentation. The cost values of High Efficiency Large Gas Storage Water Heater and High Efficiency Large Gas Instantaneous Water Heater were averaged and converted into $/MBtuh units (Cost of $4072.94 and $1619.01 per water heater) A size of 150,000 Btuh was assumed to derive the cost of $20.25/MBtuh |  |  |
| Measure Equipment Cost ($/unit): | Source: DEER 2008 Cost Values and Summary Documentation. The cost values of High Efficiency Large Gas Storage Water Heater and High Efficiency Large Gas Instantaneous Water Heater were averaged. The incremental cost was doubled for the condensing water heater cost of $22.27 /MBtuh |  |  |
| Measure Incremental Cost ($/unit): | Source: DEER 2008 Cost Values and Summary Documentation. The incremental cost values of High Efficiency Large Gas Storage Water Heater and High Efficiency Large Gas Instantaneous Water Heater were averaged and converted into $/MBtuh units and doubled for the condensing water heaters -- $2.02 /MBtuh |  |  |
| Effective Useful Life (years): | Source: DEER 2011 EUL/RUL Values and Documentation (EUL=20/11, EUL: 15 yrs |  |  |
| Program Type: | ROB and NEW |  |  |
| Net-to-Gross Ratios: | 0.60 Source: DEER 2011 NTG Values – Commercial; All other EEMs with no evaluated NTGR; existing EEM programs with same delivery mechanism for more than 2 years |  |  |
| Important Comments: | The energy consumption, savings, and EUL are an average of High Efficiency Large Gas Storage Water Heater and High Efficiency Large Gas Instantaneous Water heater per MBtuh |  |  |

# Work Paper Approvals

| Grant Brohard Manager, Engineering Services | Date |
| --- | --- |
| Carolyn Weiner Manager, Products | Date |

# Document Revision History

Revision # 		Date 		         Description		         Author (Company)

| Revision 0 | 03/25/2014 |  | Charlie Middleton (PG&E) |
| --- | --- | --- | --- |

# Table of Contents

At-A-Glance Summary	i

Work Paper Approvals	iii

Document Revision History	iv

Table of Contents	v

List of Tables	vi

Section 1. General Measure & Baseline Data	1

1.1	Measure Description & Background	1

Technical Description	1

1.2	DEER Differences Analysis	2

Table 2: DEER Use and Technology	2

1.3 Codes & Standards Requirements Analysis	2

1.4 EM&V, Market Potential, and Other Studies	2

1.5 Base Cases for Savings Estimates: Existing & Above Code	3

1.6 Base Cases & Measure Effective Useful Lives	3

1.7 Net-to-Gross Ratios for Different Program Strategies	3

Section 2. Calculation Methods	4

2.1 Electric Energy Savings Estimation Methodologies	4

2.2. Demand Reduction Estimation Methodologies	4

2.3. Gas Energy Savings Estimation Methodologies	4

Section 3. Load Shapes	4

3.1 Base Case Load Shapes	4

3.2 Measure Load Shapes	4

Section 4. Base Case & Measure Costs	5

4.1 Climate Zone Cost Factors	5

4.2 Base Cases Costs	5

4.3 Measure Costs	5

4.4 Incremental & Full Measure Costs	6

Index	7

References	8

# List of Tables

Table 1: Qualification Requirements for Domestic Water Heaters	1

Table 2: DEER Measure Efficiencies	……………………………………………………………. 2

Table 3: DEER Measure Efficiencies	2

Table 4: Title 20 Requirements for Large Water Heaters.	2

Table 5: Domestic Water Heater Base Cases	3

Table 6: Net-to-Gross Ratio	3

Table 7: DEER climate zone multipliers DH50	5

Table 8: Commercial Domestic Water Heaters Base Equipment Costs from DEER	5

Table 9: Commercial Domestic Water Heaters Measure Equipment Costs from DEER…….…...5

Table 10: Commercial Domestic Water Heaters Incremental Costs from DEER	6

- Section 1. General Measure & Baseline Data

  - Measure Description & Background

This work paper documents the rationale for the savings methodologies and assumptions for High Efficiency Domestic Water Heaters, as listed in the Boilers and Water Heating Catalog. The Boilers and Water Heating Catalog is part of Pacific Gas and Electric Company’s Customer Energy Efficiency Program. PG&E offers incentives to non-residential customers for installing qualifying high efficiency equipment.

Catalog Description

The qualifying water boilers must meet the qualifications listed in Table 1.

Table 1: Qualification Requirements for Domestic Water Heaters

| - Measure Code | - Type | - Input Rating | - Required Efficiency |
| --- | --- | --- | --- |
| - DWHC4 | - Large | - >75,000Btuh | - Thermal Efficiency ≥ 90% |

Program Restrictions and Guidelines

Terms and Conditions

Domestic water heaters must meet efficiency requirements based on size and type, as shown above. Include a manufacturer’s specification sheet documenting these characteristics. Domestic water heaters must be used for domestic hot water supply as defined by California Title 20 standards and not for space heating for human comfort.

Market Applicability

This measure is applicable to any large commercial domestic water heater application used for domestic hot water and not applicable to boilers used for process end uses, space heating, pools, or spas. Applicable business types include (but are not limited to) offices, restaurants, retail, school, colleges, hotels, motels, and recreational facilities.

### Technical Description

This measure is for upgrading from minimum to higher efficiency domestic water heaters. It applies to domestic hot water heaters with internal and separate storage tanks.

Domestic water heaters are pressure vessels that transfer heat to water. The heater may heat the domestic water using a heat exchanger that works like an instantaneous water heater, with a separate tank for storage of hot water or may have an integral tank and heat exchanger. Energy efficient units often feature high efficiency and/or low NOX burners, and typically have features such as forced air burners, relatively large heat exchange surfaces, and/or utilize heat recovery from stack gases.

This measure is for domestic water heaters with input rating of >75 MBtuh (kBtu/h). The measure calls for a minimum thermal efficiency of 90%.

  - DEER Differences Analysis

- Table 2: DEER Use and Technology

| Use Category Description | Use Category | Use Sub Category Description | Use Sub Category |
| --- | --- | --- | --- |
| Service and Domestic Hot Water | SHW | Water Heating | SHW-Htg |
| Technology Groups Description | Technology Groups | Technology Types Descriptions | Technology Types |
| Water Heating Equipment | WaterHtg_eq | Et Rated Boiler | BlrThrmEff |

DEER Measure IDs DEER, D11v4.00-097, 098, 099, and 100 include gas energy savings, base and measure equipment costs, incremental equipment costs and lifetimes.  Table 3 lists the DEER efficiencies for boilers.

Table 3: DEER Measure Efficiencies

|  | - DEER Database |  |  |
| --- | --- | --- | --- |
| - Boiler Type | - Base - Efficiency | - DWHC4 Measure Efficiency |  |
| - High Efficiency Large Gas Storage Water Heater | - Thermal Efficiency = 80% | - Thermal Efficiency = 90% |  |
| - High Efficiency Large Gas Instantaneous Water Heater | - Thermal Efficiency = 80% | - Thermal Efficiency = 90% |  |

DEER uses different nomenclature but the same common units from this work paper. DEER refers to 1000Btuh in the scientific method of “kBtuh”. To stay consistent with PG&E rebate units and standard name plate nomenclature 1000Btuh will be referred to as “MBtuh”.

- 1.3 Codes & Standards Requirements Analysis

Table 3 lists the 2010 California Title 20 Appliance Efficiency Regulations, Section 1605.1, Table F-3, Standards for Large Water Heaters.

Table 4: Title 20 Standards for Large Water Heaters

| - Measure Code | - Type | - Minimum Efficiency (%) |
| --- | --- | --- |
| - DWHC4 | - Storage Water Heaters, Instantaneous Water Heaters, and Hot Water Supply Boilers | - Thermal Efficiency ≥ 80% |

- 1.4 EM&V, Market Potential, and Other Studies

No EM&V studies were found that address commercial domestic water heaters.

## 1.5 Base Cases for Savings Estimates: Existing & Above Code

The baseline efficiency is the baseline efficiency used in DEER and/or Title 20.

Table  lists the base case efficiencies used in the work paper and DEER.

Table 5: Domestic Water Heater Base Cases

|  | - DEER Database |
| --- | --- |
| - Boiler Type | - Base Efficiency |
| - Large Gas Storage Water Heater | - Thermal Efficiency = 80% |
| - Large Gas Instantaneous Water Heater | - Thermal Efficiency = 80% |

- 1.6 Base Cases & Measure Effective Useful Lives

The effective useful life for this measure is 15 years. The EUL is the average of the High Efficiency Large Gas Storage Water Heater and High Efficiency Large Gas Instantaneous Water heater as reported in the 2011 DEER database.

- 1.7 Net-to-Gross Ratios for Different Program Strategies

Table 6 shows the applicable Net-to-Gross ratio for this measure according to the NTGR values adopted for 2011.

Table 6:  Net-to-Gross Ratio

| Measure Name* | Target Market* | Delivery Method* | NTG* | Cell Numbers |
| --- | --- | --- | --- | --- |
| All other EEMs with no evaluated NTGR | Commercial | Existing EEM in programs with same delivery mechanism for more than 2 years | 0.60 | U56-58 |

- Section 2. Calculation Methods

- 2.1 Electric Energy Savings Estimation Methodologies

Electric energy savings in this measure were taken from the DEER11 for 13-14 database.

- 2.2. Demand Reduction Estimation Methodologies

Demand reduction in this measure was taken from the DEER11 for 13-14 database.

- 2.3. Gas Energy Savings Estimation Methodologies

Gas energy savings in this measure were taken from the DEER11 for 13-14 database.

- Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.  The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

- 3.1 Base Case Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

- 3.2 Measure Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

- Section 4. Base Case & Measure Costs

- 4.1 Climate Zone Cost Factors

Table 7 lists the climate zone cost multipliers. All costs were weighted for each climate zone referencing the DEER climate multiplier table.

Table 7: DEER Climate Zone Multipliers DH50

| Climate Zone | Reference City |  | Material |  | Installation |
| --- | --- | --- | --- | --- | --- |
| 1 | Eureka |  | 0.959 |  | 1.126 |
| 2 | Santa Rosa |  | 0.959 |  | 1.465 |
| 3 | San Francisco |  | 1.004 |  | 1.478 |
| 4 | San Jose |  | 1.002 |  | 1.352 |
| 5 | San Luis Obispo |  | 0.960 |  | 1.067 |
| 11 | Redding |  | 1.002 |  | 1.083 |
| 12 | Sacramento |  | 1.002 |  | 1.100 |
| 13 | Fresno |  | 1.003 |  | 1.158 |
| 16 | Susanville |  | 0.960 |  | 1.083 |
| Average |  | 0.983 |  | 1.212 |  |

- 4.2 Base Cases Costs

Table 8 lists base equipment cost data from DEER.

Table 8: Commercial Domestic Water Heaters Base Equipment Costs

|  | - Large Domestic Water Heater (>75 MBtuh) |
| --- | --- |
| - DWHC4 Base Equipment Cost | - $20.25/MBtuh |

- 4.3 Measure Costs

Table 9 lists measure equipment cost data from DEER.

Table 9: Commercial Domestic Water Heaters Equipment Costs

|  | - Large Domestic Water Heater (>75 MBtuh) |
| --- | --- |
| - DWHC4 Measure Equipment Cost | - $22.27/MBtuh |

- 4.4 Incremental & Full Measure Costs

DEER indicates ROB/NEW as the type of installation applications for Commercial Domestic Water Heaters.

- Replace on Burnout (ROB): equipment is replaced only when it no longer functions.

- New Construction (NEW): Higher efficiency equipment is installed rather than standard, less efficient equipment in a new construction, alteration, or renovation project. An assumption is made that the less efficient, standard equipment meets current applicable codes requirements.

For ROB or NEW applications, where the choice is typically between a more and less efficient alternative, the cost basis is typically incremental.

Incremental Cost = Measure Equipment Cost – Base Case Equipment Cost

Table 10 lists incremental measure cost data for ROB or NEW.

Table 10: Commercial Domestic Water Heaters from DEER

|  | - Large Domestic Water Heater (>75 MBtuh) |
| --- | --- |
| - DWHC4 Incremental Equipment Cost | - $2.02/MBtuh |

- Index

| DEER Database, 2-6 Title 20, 2 EUL, 3 Net-to-Gross Ratios, 3 | Load Shape, 4 New Construction, 6 Replace on Burnout, 6 |
| --- | --- |

- References

- 2011 Database for Energy Efficiency Resources (DEER) Update Study, prepared by Itron Inc., November 2011

- California Energy Commission Appliances Database; May 10, 2012; http://www.energy.ca.gov/2010publications/CEC-400-2010-012/CEC-400-2010-012.PDF

- 2010 California Title 20 Appliance Efficiency Regulations, Section 1605.1, Table F-3.

- Energy Efficiency Policy Manual Version 4.0, prepared by CPUC, Energy Division, July 2008.

- DEER2011_NTGR_2012-05-16.xls from  DEER Database for Energy-Efficient Resources; Version 2011 4.01 found at :http://www.deeresources.com/index.php?option=com_content&view=article&id=68&Itemid=60 Under: DEER2011 Update Documentation linked at: DEER2011 Update Net-To-Gross table Cells: (U56)

- 2011 DEER Database Entries DEER Database for Energy-Efficient Resources; Version 2011 4.01 found at :http://www.deeresources.com/index.php?option=com_content&view=article&id=68&Itemid=60 READI Tool Version 0.99.7; Measures D11 v4.00 – (97, 98, 99, & 100)

- “Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls”