Work Paper WPSCGNRWH150827A

Revision #2

Southern California Gas Company

Customer Programs Department

Laminar Flow Restrictors
For Hospitals and Health Care Facilities

# At-a-Glance Summary

| Measure Codes | ShwFlr001, ShwFlr002, ShwFlr003, ShwFlr004 |
| --- | --- |
| Measure Description | Laminar Flow Restrictors (LFRs) for health care facilities (0.5 GPM-2.2 GPM flow rates) that are installed at the outlet of faucet spouts to reduce flow rate and thus water consumption |
| Base Case Description | Existing faucet spouts (2.7 GPM) with no flow restriction devices present |
| Units | Per fixture |
| Energy Savings | Average Annual Savings for Climate Zone 9: 15.72 therms per fixture Refer to Excel Calculations (Attachment A) |
| Full Measure Cost ($/unit) | Direct Install Prescriptive Rebate: $14.27/unit Downstream Incentive Prescriptive Rebate: $7.27/unit |
| Incremental Measure Cost ($/unit) | Direct Install Prescriptive Rebate: $14.27/unit Downstream Incentive Prescriptive Rebate: $7.27/unit |
| Effective Useful Life | EUL of faucet: 20 years (EUL ID: WtrHt-WH-Faucet) EUL of aerator: 10 years (DEER EUL ID: WtrHt-WH-Aertr) Measure life = RUL of faucet = 6.67 years |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.7 (DEER NTGR ID: All-Default<=2yrs) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 8/20/15 | Julianna Colwell (SCG) Jesse Martinez (SCG) | Initial work paper write up |
| 1 | 10/12/15 | Julianna Colwell (SCG) Jesse Martinez (SCG) | Revised based on comments from Cal TF |
| 2 | 4/8/16 | Nicole Loo (SCG) | Further revision per Cal TF comments: - Revised savings calculations; consolidated all heating method cases using one calculation method and updated control volume analysis - Tier 2 storage water heater type removed - Equipment efficiencies updated to adopt DEER assumptions - Hot water and steam boiler savings are combined under the same thermal efficiencies - Revised annual hand washing usage time assumptions - Added water savings estimations - References were updated |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |
| 0 | Cal TF | 8/20/15 | 9/24/15 | - Savings calculation approach should factor in entire “straight line” configurations for 145 degree hot water and a 15 pound steam boiler system | - Revised based on comments from Cal TF |
| 1 | Cal TF | 10/12/15 | 10/22/15 | - Cost and methods for validating DEER 0.7 NTG with empirical data - Consolidate Pressure Reducing Valve (PRV) and non-PRV steam use cases into one | - 0.7 was chosen because it is the default NTG value for new measures less than 2 years; NTG for aerators do not apply because those are targeted for residential markets - Steam cases consolidated |

Cal TF website: http://www.caltf.org/

The Cal TF approved Version #1 of this work paper found under the “Approved Measures” section of the website, http://www.caltf.org/approved-measures/

# Table of Contents

At-a-Glance Summary	2

Revision History	3

Commission Staff and Cal TF Comments	3

Table of Contents	4

Section 1. General Measure & Baseline Data	5

1.1 Measure Description & Background	5

1.2 Technical Description	6

1.2.1 Measure Overview	6

1.2.2 Laminar Flow Restrictor Technology	8

1.3 Installation Types and Delivery Mechanisms	9

1.4 Measure Parameters	9

1.4.1 DEER Data	9

1.4.2 Codes and Standards Analysis	12

1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	13

1.5.1 Hot Water Fixture Flow Survey	13

1.5.2 Market Potential	15

Section 2. Calculation Methodology	15

2.1 Overview and Assumptions	15

2.2 Gas Energy Savings Estimation Methodologies	18

2.3 Sample Gas Savings Calculation	21

2.4 Water Savings Estimation Methodologies	21

Section 3. Load Shapes	22

Section 4. Costs	22

4.1 Base Case Cost	22

4.2 Measure Case Cost	22

4.3 Full and Incremental Measure Cost	23

Attachments	24

References	25

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Table 1: Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Laminar Flow Restrictor for Health Care Facilities (0.5 GPM flow rate) |
|  | Laminar Flow Restrictor for Health Care Facilities (1.0 GPM flow rate) |
|  | Laminar Flow Restrictor for Health Care Facilities (1.5 GPM flow rate) |
|  | Laminar Flow Restrictor for Health Care Facilities (2.2 GPM flow rate) |
| Existing Condition | 2.7 GPM flow rate faucet with no flow restriction present |
| Code/Standard | Faucet with no flow restriction device present |
| Industry Standard Practice | 2.7 GPM flow rate faucet with no flow restriction present |

Table 2: Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| ShwFlr001 |  |  |  | 0.5 GPM Flow Rate Laminar Flow Restrictor being installed on a 2.7 GPM Flow Rate Faucet Base Case |
| ShwFlr002 |  |  |  | 1.0 GPM Flow Rate Laminar Flow Restrictor being installed on a 2.7 GPM Flow Rate Faucet Base Case |
| ShwFlr003 |  |  |  | 1.5 GPM Flow Rate Laminar Flow Restrictor being installed on a 2.7 GPM Flow Rate Faucet Base Case |
| ShwFlr004 |  |  |  | 2.2 GPM Flow Rate Laminar Flow Restrictor being installed on a 2.7 GPM Flow Rate Faucet Base Case |

Eligibility requirements

Rebates for this measure are restricted to health care facilities. Only facilities utilizing natural gas powered water heating equipment are eligible for rebates for this measure. Products installed must meet Office of Statewide Health Planning and Development (OSHPD) code and regulation.

Since this is a Retrofit Add-on (REA) measure, rebates do not apply to new construction.

Only LFR models labeled as “Vandal Proof” or are not removable without a proprietary tool are considered for the rebate, with the exception of dialysis and scrub sink locations. There are currently 37 “Vandal Proof” LFRs in the appropriate size options available for purchase.

Implementation and installation requirements

This measure is to be implemented in Health/Medical buildings (hospitals, clinics, and nursing homes) of the Commercial sector as a Retrofit Add-on (REA) measure for existing faucets that do not already have a flow restricting device installed.

Table 3: Sector and Subsector (Building Type)

| Measure ID | Sector | Subsector | Subsector(Building Type) Description |
| --- | --- | --- | --- |
| ShwFlr001 | Com | Cnc | Health/Medical – Clinics |
| ShwFlr001 | Com | Hsp | Health/Medical - Hospital |
| ShwFlr001 | Com | Nrs | Health/Medical – Nursing Home |
| ShwFlr002 | Com | Cnc | Health/Medical – Clinics |
| ShwFlr002 | Com | Hsp | Health/Medical - Hospital |
| ShwFlr002 | Com | Nrs | Health/Medical – Nursing Home |
| ShwFlr003 | Com | Cnc | Health/Medical – Clinics |
| ShwFlr003 | Com | Hsp | Health/Medical - Hospital |
| ShwFlr003 | Com | Nrs | Health/Medical – Nursing Home |
| ShwFlr004 | Com | Cnc | Health/Medical – Clinics |
| ShwFlr004 | Com | Hsp | Health/Medical - Hospital |
| ShwFlr004 | Com | Nrs | Health/Medical – Nursing Home |

Documentation Requirements

Proof of purchase must be provided and must include all of the following:

- Manufacturer’s name and equipment make and model number

- Device flow rate (if not specified in equipment make/model number details)

- Equipment cost

- Quantity installed

- Indication of payment in full

- Purchase date

- Water heater equipment type (storage, instantaneous, hot water/steam boiler)

Terms and Conditions

The LFRs are meant only for the health care industry and facilities that are subject to the Office of Statewide Health Planning and Development (OSHPD) code and regulation/inspection.

General terms and conditions for SCG measures can be found at http://www.socalgas.com/for-your-home/rebates/terms-conditions.shtml

## 1.2 Technical Description

### 1.2.1 Measure Overview

Laminar Flow Restrictors (LFRs), also known as laminar flow devices, are “add-on” devices that are installed at the outlet of the faucet spout to reduce water consumption. In practice, LFRs differ from aerators in that they produce a transparent stream of water without introducing air into the flow. The differences between LFRs and aerators are summarized in Table 4 and Figure 1.

LFRs have specific applications in the health care industry. The health care industry for the purpose of this work paper consists of any facility that adheres to the Office of Statewide Health Planning and Development (OSHPD) regulations in the state of California. These include but are not limited to:

- Hospitals (large regional or local)

- Emergency rooms

- In-patient and outpatient facilities and medical office buildings connected to or free standing from main hospitals

- Doctor’s offices (e.g. general practitioners, pediatricians, optometrists, chiropractors, etc.)

Currently, OSHPD specifically bans the use of aerators in the health care industry due to the aerator’s flow control methods and components. The mixing of air and water within the aerator allows airborne bacteria to become waterborne and, in warm stagnant conditions, promote bacterial growth. The increased surface area of aerator components (e.g. screens) allows hard water deposits and biofilm to accumulate within the device which may further harbor increased bacterial growth.

Table 4: LFR vs. Aerator Comparison Summary

| LFRs | Aerators |
| --- | --- |
| - “Laminar” refers to a stream that flows in parallel layers with no disruption between them - Approved for health care use because of their hygienic advantage: aerosol generation is reduced to a minimum due to the lack of air intake - Water restriction is achieved by using small nozzles (straightening vanes) that are shaped to keep turbulence from forming, preventing air from entering the flow - Flow is clear and transparent | - Use the Venturi effect to introduce air into the water stream - Banned in health care environments, but commonly used in residential and other commercial applications - Restrict water by using screens to introduce air bubbles into the water stream which may allow airborne bacteria to become waterborne - Flow has a white opacity and a soft feel |

Figure 1: LFR (left) vs. Aerator (right)

Gas Investor Owned Utilities (IOUs) would claim their savings via the hot water supply. A reduced flow rate over a similar operating time would result in a reduction of hot water usage by each individual faucet after installation of the LFR.

### 1.2.2 Laminar Flow Restrictor Technology

Straightening Vanes

Straightening vanes are used in the LFRs in lieu of the metal wire mesh that is utilized in traditional aerators. They are introduced in the flow path in order to keep the water flow laminar. Inlet-ends of the vanes are furnished to minimize shear stress. The reduction in shear stress at the inlet of the LFR prevents the development of air bubble entrainment in the exiting water stream. The net result is that the water flow through the LFR remains laminar at every major cross section of the water stream.

Prevention of Bacteria Development

Turbulence in the outlet of an aerator allows airborne bacteria to entrain itself to the water flow. “Bryers and Characklis” (1981) have shown that the rate of overall bacterial film development on surfaces in turbulent flow conditions increases with the biomass concentration dispersed in the bulk phase. The water exiting the LFR sustains a laminar profile, Re < 2100, which significantly mitigates air bubble development within the LFR and drastically reduces the opportunity for bacteria growth within the restrictor.

Some LFRs have silver-zeolite incorporated into the plastic resin which strengthens the restrictor’s ability to kill harmful bacteria on contact. Bacteria that could otherwise develop between uses, is killed by releasing a silver ion onto the moisture film (Figure 2).  This silver zeolite coating is an additional benefit to the environment of health care professionals within hospitals, medical offices, nursing homes, and other health care facilities that are within the purview of OSHPD, but will not be required as an eligibility requirement for the rebate.

Figure 2: Molecular Behavior of Silver Zeolite Coating

## 1.3 Installation Types and Delivery Mechanisms

Table 5: Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Table 6: Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Table 7: Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install (PreRebDI) | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive (PreRebDown) | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

There is no DEER measure for the faucet LFRs. The most similar measure applicable for the LFR is the faucet aerator. In DEER, the faucet aerator EUL ID is WtrHt-WH-Aertr.

There are two Non-DEER work papers that target the installation of faucet aerators:

- Faucet Aerators for Bathroom/Kitchen Sinks in Residential Buildings (WPSCGREWH120618A)

- Therm Savings Kit (SCGWP100309A)

This work paper intends to depart from the Non-DEER faucet aerator work papers since LFRs are not traditional aerators since no outside air is introduced into the water stream (see Section 1.2).

Table 8: DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No (but is referenced) |
| DEER Measure Case | No |
| DEER Building Types | Yes: Clinics, Hospitals, Nursing Homes |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | N/A (IOU Workpaper) |
| Reason for Deviation from DEER | DEER database does not contain this type of measure |
| DEER Measure IDs Used | N/A |

Reason for Deviation from DEER

The DEER baseline hot water consumption in these building types is indicated in Table 9. The work paper estimates include the hot water consumption for faucets only, while the DEER results indicate the total hot water consumption for the buildings (see Attachment G). The results from the DEER eQUEST models are more of an aggregate estimate and thus do not provide an accurate approximation for faucet hot water consumption.

Table 9: DEER Baseline Hot Water Consumption

| Building Type | Size per Facility (sq. ft.) | DEER Annual Hot Water Consumption (therms/yr-facility) |
| --- | --- | --- |
| Clinics | 20,000 | 262.80 |
| Nursing care | 25,000 | 12,606 |
| Hospital | 250,000 | 92,000 |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

Table 10: NTG Values

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | Com | Cnc, Hsp, Nrs | Prescriptive Rebate (PreReb) | 0.7 |

Note: Direct install measures that are not hard-to-reach will use the default NTG value.

NTG values for aerators do not apply because those are targeted for residential markets.

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

LFRs are a relatively new technology and are not currently represented in DEER or as an IOU rebate in California.

GSIA values for residential aerators were not used because they do not realistically represent the commercial health care market.

Vandal proof LFRs will allow installations to remain installed for their entire Effective Useful Life (EUL). A vandal proof LFR requires a proprietary tool to install and/or remove the device which prevents individuals from uninstalling the device without the knowledge of the maintenance staff of the health care facility.

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

Table 11: IR Values

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Com | Cnc, Hsp, Nrs | PreRebDI, PreRebDown | 1 |

Effective and Remaining Useful Life

The Effective Useful Life (EUL) of the LFR is 10 years, based on warranties provided by the manufacturers and installers

Based on the most recent guidance from the CPUC, this measure’s Retrofit Add-on (REA) status dictates that the Remaining Useful Life (RUL) should be used for the savings calculations. The RUL is equal to 1/3 of the EUL of the device being modified by the measure addition, in this case the faucet. The EUL of a faucet is 20 years based on plumbing publications and manufacturer warranties.   From this, the RUL for a LFR is determined to be 6.67 years.

Equation 1—Remaining Useful Life for Retrofit Add-on

RULREA= EULfixture appurtenant *13=20 years*13=6.67 years

Table 12: EUL and RUL Values

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| WtrHt-WH-Faucet | Faucet EUL | Com | Shw | 20 | 6.67 |

### 1.4.2 Codes and Standards Analysis

Table 13: Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 20 (2014) | Section 1605.1(h). Plumbing Fittings | July 1, 2014 |

A code baseline for this technology would be the faucet flow rates stipulated in Title 20 of the California Code of Regulations Table H-1 as seen in Figure 3.

Figure 3: Title 20 Table H-1

It is worth noting that Title 20 is due for a revision in 2016 with new flow rates that are lower than those listed in Figure 3. The upcoming changes to the Title 20 code are listed below in Figure 4.

Figure 4: New Title 20 Standards for Plumbing Fittings and Fixtures

Title 20 code is not considered an appropriate baseline flow rate due to strong evidence of a higher pre-existing/in situ flow rate as defined in Section 1.5.1.

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### 1.5.1 Hot Water Fixture Flow Survey

Overview

The preexisting flow rate of health care faucets has been deemed to be 2.7 GPM from a study completed by Water Saver Solutions. The raw shared survey results are shown in Attachment C. Water Saver Solutions chose 20 hospitals, 1 medical office building and 1 nursing home in SCG territory to make up the shared survey. The shared results can be considered a snap shot of the health care industry in SCG territory. The study results include health care facility locations, faucet counts and types, and the measured flow rates.

Techniques Used

There were three methods used for measuring the existing flow rates: the measuring cup, bag, and digital flow meter.

The most common method utilized was the measuring cup, in which flow rates were taken using a measuring cup and a timer. A 0.25 gallon capacity measuring cup, with indicators in fluid ounces, was placed under the running faucet for 5 seconds to measure the amount of water coming out of the faucet spout.

If the flow rate coming out of the faucet was too high for the measuring cup method, a 1 gallon bag with gallons per minute (GPM) indicators was utilized instead. The bag was also held under the running faucet for 5 seconds.

Over the course of 2015, Water Saver Solutions has shifted their survey methods to digital flow meters that read in gallons per minute. These meters are attached to the end of the faucet and provide a digital reading of the out of faucet flow rate. This device has been used to double check records from the measuring cup and bag methods.

The hand and foot operated faucets were fully engaged when taking flow rate measurements. The sensor operated faucets were constantly engaged when taking flow rate measurements. In cases where a fully engaged hand or foot operated faucet produced too much flow to be considered reasonable for washing hands, the throttling controls (handles or pedals) were turned down until the surveyor believed a person could reasonably wash their hands without excessive splashing or overflow.

Conversions were performed to determine the flow rate in gallons per minute.

Equation 2—Flow Rate (GPM)

Flow rate GPM=x fl. oz.5 s×60 smin×1 gal128 fl. oz.

Faucet and adapter details were recorded (e.g. types, uses, ideal operating flow rates).

Results

2.7 GPM is considered to be the weighted average of the 4,000+ faucets observed across the SCG territory. This flow rate serves as a valid in situ baseline flow rate for existing health care facilities, excluding new construction. The observed faucets include varying quantities of hand, foot, and sensor operated faucet types.

A behavioral factor of 0.7 was added to the hand and foot operated flow rates in order to create a weighted average to account for human behavior in turning on the faucet since not every operator will turn on the faucet to its full potential flow rate. Since sensor operated faucets have no operator flow control, it was not considered necessary to add a behavioral factor to the measured flow rates.

Equation 3—Weighted Average Flow Rate

Weighted Avg
=

(AvgFlowhand ×.7× Counthand+ AvgFlowfoot×.7× Countfoot + AvgFlowsensor× CountsensorCounthand + Countfoot + Countsensor

### 1.5.2 Market Potential

There are currently 15,000 SCG customers that could be considered part of the health care industry.

A rough estimation of available sinks was established using NAICS codes, LA County assessor data, and published bed counts. Bed count estimations assume 1 sink/faucet per every 2 beds reported. Table 14 below breaks down the estimated numbers of sinks/faucets available in the SCG territory.

Table 14: Estimated Market

| Type | NAICS Count | Est. # of Sinks | Est. # of Sinks Rounded |
| --- | --- | --- | --- |
| Outpatient Buildings | 12,000 | 187,897 | 200,000 |
| Nursing Care Facilities | 2,000 | 66,501 | 70,000 |
| Hospitals | 800 | 97,200 | 100,000 |
| Total | 14,800 |  | 370,000 |

These estimations are highly conservative and it is expected that the true market potential will be larger when the program goes through Ex Post review. The data does not include certain operations of health care facilities such as surgery, food service, and public restrooms.

# Section 2. Calculation Methodology

## 2.1 Overview and Assumptions

LFRS are considered a new technology and therefore have no savings values on record in DEER.

The three domestic water heating equipment types considered for savings were the following:

- Storage water heaters

- Hot water boilers

- Steam boilers

The control volume selected, as seen in Figure 5, includes the incoming city make-up water, water heating mode (storage water heater, hot water boiler or steam boiler), and the outgoing heated water being supplied to the faucet.

Figure 5: Process Flow and Control Volume

The temperature of the make-up water supplied to the water heating mode varies by climate zone as seen in the table below.

Table 15: Make-up Water Temperature by Climate Zone

| Climate Zone | Temperature (°F) |
| --- | --- |
| 1 | 51.38 |
| 2 | 57.29 |
| 3 | 57.05 |
| 4 | 59.51 |
| 5 | 55.83 |
| 6 | 61.75 |
| 7 | 62.55 |
| 8 | 63.74 |
| 9 | 63.82 |
| 10 | 64.15 |
| 11 | 63.19 |
| 12 | 60.88 |
| 13 | 64.1 |
| 14 | 62.67 |
| 15 | 75.47 |
| 16 | 51.75 |

The following assumptions were made:

- A mixed water temperature of 105°F is considered an appropriate assumption for handwashing.

- The average annual operating time per faucet was estimated to be 41 hours per year using an average daily usage time of 8 minutes per day per faucet. The 8 minutes per day usage value was taken as the median value of the 4-12 minute range developed by Water Saver Solutions from custom calculated data. A separate study by MWD found a similar average daily usage time of 10 minutes per day per faucet. Clinics are estimated to run close to 260 days a year while hospitals and nursing homes are considered to run close to 365 days a year.

Equation 4—Weighted Average Operating Days per Year (t)

tfacility weighted=daysyear×% of market

tclinic=260daysyear×54%= 141daysyear

tnursing home=365daysyear×19%= 69daysyear 
thospital=365daysyear×27%= 99daysyear

∴ ttotal, weighted=tclinic+tnursing home+thospital=308 daysyear

Where,

% of market=est. # of sinkstotal est. # of sinks taken from Table 14

Equation 5—Annual Operating Time (τ)

∴ τ =8 minday×1 hr60 min×308 days1 yr=41 hryr

- Thermal efficiencies for the domestic water heating equipment are assumed to be the following:

  - Storage type water heaters: 76%

  - Hot water boilers: 75%

  - Steam boilers:  75%

These individual efficiency values are utilized in the energy savings calculations in Attachment A. However, since the efficiencies of all equipment types listed above are similar, the savings value from the storage type water heater is used for all three water heating modes in the Ex-Ante Database (EAD) tables.

## 2.2 Gas Energy Savings Estimation Methodologies

The savings calculation approach for this measure compares the energy consumption of the domestic hot water (DHW) system of the existing condition (faucets without LFRs) with the proposed condition (faucets with LFRs). This analysis is based on the first law of thermodynamics (conservation of energy). The installation of LFRs causes a change in the mass flow rate of water and thus ultimately affects the thermal load of the system.

Figure 6: Existing DHW system before the installation of LFRs

Equation 6 —Annual Energy Consumption of Existing System (no LFR)

ECexisting=DHWother+Ploss+Standingloss+ Faucet Load existingEffth

Where,

ECexisting = annual energy consumption of the existing system, Btuyear

DHWother = annual hot water loads of other hot water using devices (all loads except faucets receiving LFRs), Btuyear

Ploss = piping system distribution losses, Btuyear

Standingloss = standing loss of hot water heating system, Btuyear

Faucet Load existing = existing faucet load (without LFR installed), Btuyear

Effth = thermal efficiency of water heating equipment

Figure 7: Proposed DHW system after the addition of LFRs

Equation 7 —Annual Energy Consumption of Proposed System (with LFR)

ECproposed=DHWother+Ploss+Standingloss+ Faucet Load proposedEffth

The proposed faucet load is similar to the existing faucet load but at the lower flow rate imposed by the LFR installed.

It should be noted that only the Faucet Load in Equation 6 and Equation 7, is affected by the installation of the LFR.

The annual energy savings is the difference between the annual energy consumption of the existing system and the annual energy consumption of the proposed system. The terms for all the loads in Equation 6 and Equation 7, except the Faucet Load, are eliminated when the energy consumption equations are subtracted, resulting in the equation below:

Equation 8 —Annual Energy Savings (ES)

ES= ECexisting-ECproposed= Faucet LoadExisting-Faucet LoadProposedEffth

The faucet load can be determined by applying the energy flux equation, as seen in Equation 10 and 11.

Equation 9—Mass Flow Rate

m= V*ρ

Where,

m = mass flow rate, lbmmin

V = volume flow rate, galmin

ρ = density of water, lbmgal

Equation 10—Energy Flux

Q=m*cp*∆T

Where,

Q = rate of enthalpy (heat) change, Btumin

cp = specific heat at constant pressure, Btulbm∙℉

∆T = temperature difference, ℉

Applying the conversion factors, annual usage time, and water heating equipment efficiency, the heat flux equation becomes:

Equation 11—Faucet Load (Q)

Faucet Load= m*60 minhr*(cp*1 therm100,000 Btu)*Tmixed-Tmu* τξ

Where,

Faucet Load = annual energy consumption per faucet, thermsyear

Tmixed = temperature of mixed water stream, ℉

Tmu= make-up water temperature (climate zone dependent, see Table 15), ℉
τ = annual hand washing time, hryr

ξ= thermal efficiency of equipment, [factor]

The net savings is determined from the difference of the energy consumption of the bare faucet and the energy consumption of the faucet with the LFR installed.

Equation 12—Annual Net Energy Savings

Qnet=Qfaucet-QLFR

## 2.3 Sample Gas Savings Calculation

Assuming that the typical flow rate for the faucet without a LFR is 2.7 gpm, Climate Zone 1, storage type water heater with 76% efficiency, average make-up water temperature of 51.4°F, mixed water temperature coming out of the faucet of 105°F, and typical annual usage of 41 hours per year, the annual hot water load for a faucet without a LFR is:

Qfaucet =Faucet Loadexisting

= 2.7 galmin*8.33lbgal*60 minhr*1Btulb∙℉*1 therm100,000 Btu*105℉-51.4℉*41 hoursyear0.76

=39.13thermsyear

Substituting the 2.7 gpm term for the flow rate of the installed LFR (i.e. 2.2 gpm) and leaving all remaining terms the same, the annual hot water load for a faucet with a LFR is:

QLFR =Faucet Loadproposed = 31.88thermsyear

Thus, the natural gas energy savings for that faucet is:

Qnet=Qfaucet-QLFR=7.25thermsyear

See Attachment A for full savings calculations and results.

## 2.4 Water Savings Estimation Methodologies

Equation 13—Annual Water Consumption (per faucet)

V= V×60 minhr×τ

Where,

V = annual water consumption, gallonsyear
V = volume flow rate, galmin
τ = annual hand washing time, hryr

Equation 14—Annual Net Water Savings

Vnet=Vbare faucet-VLFR

Table 17: LFR Annual Water Savings (per faucet)

| Savings | Units | 2.2 GPM | 1.5 GPM | 1.0 GMP | 0.5 GPM |
| --- | --- | --- | --- | --- | --- |
|  | gal/yr | 1,233 | 2,959 | 4,192 | 5,425 |

See Attachment A for full savings calculations and results.

# Section 3. Load Shapes

The hot water demand load profile for the hospital and nursing home building types can be found in DEER-WaterHeater-Calculator-v1.0 provided by DEER.

# Section 4. Costs

## 4.1 Base Case Cost

Baseline costs are $0 since it is an REA measure and the base case would be to do nothing to the faucet.

## 4.2 Measure Case Cost

The equipment cost was developed using an entire set of vandal proof LFRs from the NEOPERL 2014 Wholesale Price List as seen in Attachment F. The average price for the entire array of vandal proof faucet LFRs is $7.27 per LFR.

The labor/installation cost is based upon the costs charged by third party contractors installing the aerators for the direct install program for residential faucet aerators. The minimum cost charged during the direct install program was $7 per aerator. The cost for installing LFRs was also estimated to be $7 per fixture since the installation procedure for installing aerators is very similar to the procedure for installing LFRs.

The proposed measure cost is detailed in the table below.

Table 18: Proposed Measure Cost

| Description | Equipment Cost | Labor/Installation Cost | Maintenance/Other Costs | Total Measure Cost |
| --- | --- | --- | --- | --- |
| Faucet LFR (Direct Install) | $7.27/fixture | $7/fixture | TBD | $14.27/fixture |
| Faucet LFR (Downstream Prescriptive Rebate) | $7.27/fixture | $0/fixture | TBD | $7.27/fixture |

## 4.3 Full and Incremental Measure Cost

Table 19: Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Table 20: Full and Incremental Costs

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA, Direct Install | $7.27/fixture + $7/fixture = $14.27 per fixture | $14.27 per fixture | N/A |
| REA, Downstream Prescriptive Rebate | $7.27/fixture + $0/fixture = $7.27 per fixture | $7.27 per fixture | N/A |

# Attachments

Attachment A—Savings Calculations

Attachment B—ECM Measure Upload Template and Complete Measure Sheet

Attachment C—Water Saver Solutions Raw Survey Data

Attachment D—Support for Bacteria Entrainment in Turbulent Flow

Attachment E—Care Guard Silver-Zeolite Coating

Attachment F—Price List Sheet

Attachment G—DEER Healthcare Building Type Models

# References

NEOPERL Product Catalogue No. 6, 2015

(2015, May). Section 1226.6. Health Facility Checklist Section 1226 [OSHPD 3] Clinics. http://www.cpca.org/cpca2013/assets/File/Health-Center-Information/Licensing-OSHPD3/OSHPD3-Title%2024/2014-06-27-Primary%20Care%20Clinic_Checklist%20OSHPD%203.pdf

NEOPERL Product Catalogue No. 6, 2015

Fletcher, M., Savage. Section 2.1. Bacterial Adhesion: Mechanisms and Physiological Significance.

Lindeburg, M. R. Section 17 Fluid Mechanics. Mechanical Engineering Reference Manual.

Tamanai-Shacoori, Z., Chandad, F., Rébillard, A., Cillard, J., & Bonnaure-Mallet, M. (2014, October). Silver-Zeolite Combined to Polyphenol-Rich Extracts of Ascophyllum nodosum: Potential Active Role in Prevention of Periodontal Diseases. http://www.ncbi.nlm.nih.gov/pmc/articles/PMC4182675/

Saengmee-anupharb, S., Srikhirin, T., Thaweboon, B., Thaweboon, S., Amornsakchai, T., Dechkunakorn, S., & Suddhasthira, T. (2013, January). Antimicrobial effects of silver zeolite, silver zirconium phosphate silicate and silver zirconium phosphate against oral microorganisms. http://www.ncbi.nlm.nih.gov/pmc/articles/PMC3609392/

National Association of Home Builders, Bank of America Home Equity. (2007, February). Study of Life Expectancy of Home Components, p. 12.

Glacier Bay Faucets. 20 Year Warranty Guarantee.

InterNACHI’s Standard Estimated Life Expectancy Chart for Homes. http://www.nachi.org/life-expectancy.htm

California Energy Commission (2014, March 28). Appliance Efficiency Regulations, Section 1605.1(h). California Code of Regulations TITLE 20, Division 2. http://www.energy.ca.gov/title20/index.html

(2008, January 2). Section 612.5. California Plumbing Code (Part 5, Title 24, California Code of Regulations).http://www.iapmo.org/Code%20Errata/2007%20California%20Plumbing%20Code%20Errata/2007-CPC-Errata%20010208.pdf

DEER DHW Properties Worksheet. DEER-WaterHeater-Calculator-v1.0.

DEER2016, Pre-existing Technology Description, Measure ID: NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset

DEER2016, Pre-existing Technology Description, Measure ID: NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft

NEOPERL Product Catalogue No. 6, 2015