## cost calculation
| ADEC | *Base Labor Rate | 86.93
|  | Hours | Labor | Materials | Total | Source
| AVERAGE TOTAL COST |  | 360.75 | 595.2123 | 955.9623 | PGE3PHVC151 R4 measure cost data
| CO2 Sensor and DCV Setup | Hours | Labor | Materials | Total | Source
| mfgA Distributor Quote with 100% Markup | 1 | 86.93 | 508.78 | 595.71 | See CO2 SENSOR for material; labor based on direct experience
| mfgB Retail Sample with 10% Contractor Discount | 1 | 86.93 | 470.8 | 557.73 | See CO2 SENSOR for material; labor based on direct experience
| mfgC Retail Sample with 10% Contractor Discount | 1 | 86.93 | 198 | 284.93 | See CO2 SENSOR for material; labor based on direct experience
| SENSOR AVERAGE | 1 | 86.93 | 392.5267 | 479.4567
| Field Wiring - Zone to RTU | 2 | 173.86 | 20 | 193.86 | small parts material estimated; labor based on direct experience
| Measure and set min/max ventilation+Functional Test | 1 | 86.93 |  | 86.93 | labor based on direct experience
| AVERAGE TOTAL COST | 4 | 347.72 | 412.5267 | 760.2467
*Base labor rate equivalent to rate used for Draft DEER Measure Cost Update Study
| Measure | Labor | Materials | Total | *Typical Unit Cost/Ton
| Add ADEC and CO2 sensor to XXX | 708.47 | 1007.739 | 1716.209 | 137.2967
| Add CO2 sensor to XXX with ADEC | 347.72 | 412.5267 | 760.2467 | 60.8197
| *Typical Unit Size | 12.5 | Tons
Climate Zone Adjusted IMC Data
|  |  | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit)
| 1 | Add ADEC and CO2 sensor to XXX | 75.782 | 57.6411 | 133.4231
| 2 | Add ADEC and CO2 sensor to XXX | 75.782 | 93.6881 | 169.47
| 3 | Add ADEC and CO2 sensor to XXX | 80.6997 | 94.8216 | 175.5214
| 4 | Add ADEC and CO2 sensor to XXX | 80.6191 | 82.0692 | 162.6883
| 5 | Add ADEC and CO2 sensor to XXX | 75.782 | 59.7949 | 135.5768
| 6 | Add ADEC and CO2 sensor to XXX | 80.6191 | 66.1428 | 146.7619
| 7 | Add ADEC and CO2 sensor to XXX | 80.6191 | 65.2926 | 145.9117
| 8 | Add ADEC and CO2 sensor to XXX | 75.782 | 59.7949 | 135.5768
| 9 | Add ADEC and CO2 sensor to XXX | 80.6997 | 66.1428 | 146.8425
| 10 | Add ADEC and CO2 sensor to XXX | 80.6191 | 66.0861 | 146.7052
| 11 | Add ADEC and CO2 sensor to XXX | 80.6191 | 60.645 | 141.2641
| 12 | Add ADEC and CO2 sensor to XXX | 80.6191 | 67.8998 | 148.5189
| 13 | Add ADEC and CO2 sensor to XXX | 80.6997 | 63.0822 | 143.7819
| 14 | Add ADEC and CO2 sensor to XXX | 75.782 | 56.2242 | 132.0061
| 15 | Add ADEC and CO2 sensor to XXX | 75.782 | 59.7382 | 135.5202
| 16 | Add ADEC and CO2 sensor to XXX | 75.782 | 60.645 | 136.427
Used in work paper | WEIGHTED AVERAGE | Add ADEC and CO2 sensor to XXX | 79.336 | 65.6352 | 144.9713
| 1 | Add CO2 sensor to XXX with ADEC | 31.022 | 28.2905 | 59.3125
| 2 | Add CO2 sensor to XXX with ADEC | 31.022 | 45.9825 | 77.0045
| 3 | Add CO2 sensor to XXX with ADEC | 33.0351 | 46.5388 | 79.574
| 4 | Add CO2 sensor to XXX with ADEC | 33.0021 | 40.2799 | 73.282
| 5 | Add CO2 sensor to XXX with ADEC | 31.022 | 29.3476 | 60.3696
| 6 | Add CO2 sensor to XXX with ADEC | 33.0021 | 32.4631 | 65.4653
| 7 | Add CO2 sensor to XXX with ADEC | 33.0021 | 32.0459 | 65.048
| 8 | Add CO2 sensor to XXX with ADEC | 31.022 | 29.3476 | 60.3696
| 9 | Add CO2 sensor to XXX with ADEC | 33.0351 | 32.4631 | 65.4983
| 10 | Add CO2 sensor to XXX with ADEC | 33.0021 | 32.4353 | 65.4375
| 11 | Add CO2 sensor to XXX with ADEC | 33.0021 | 29.7648 | 62.767
| 12 | Add CO2 sensor to XXX with ADEC | 33.0021 | 33.3255 | 66.3276
| 13 | Add CO2 sensor to XXX with ADEC | 33.0351 | 30.961 | 63.9961
| 14 | Add CO2 sensor to XXX with ADEC | 31.022 | 27.5951 | 58.6171
| 15 | Add CO2 sensor to XXX with ADEC | 31.022 | 29.3198 | 60.3418
| 16 | Add CO2 sensor to XXX with ADEC | 31.022 | 29.7648 | 60.7868
Used in work paper | WEIGHTED AVERAGE | Add CO2 sensor to XXX with ADEC | 32.4769 | 32.214 | 64.6909
From Draft DEER Measure Cost Update:
Table G-1: Statewide RSMeans Cost Indices Weighted by 2010-2012 HVAC Measure Claims
| Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation
| 1 | Eureka | 0.94 | 1.017 | 0.0032678 | 0.0030717 | 0.0033234
| 2 | Santa Rosa | 0.94 | 1.653 | 0.0096952 | 0.0091135 | 0.016026
| 3 | San Francisco | 1.001 | 1.673 | 0.030274 | 0.030304 | 0.050648
| 4 | San Jose | 1 | 1.448 | 0.015286 | 0.015286 | 0.022134
| 5 | San Luis Obispo | 0.94 | 1.055 | 0.00043296 | 0.00040698 | 0.00045677
| 6 | Santa Barbara | 1 | 1.167 | 0.1391 | 0.1391 | 0.16233
| 7 | San Diego | 1 | 1.152 | 0.046714 | 0.046714 | 0.053815
| 8 | Santa Ana | 0.94 | 1.055 | 0.16224 | 0.15251 | 0.17117
| 9 | Los Angeles | 1.001 | 1.167 | 0.2181 | 0.21832 | 0.25453
| 10 | Riverside | 1 | 1.166 | 0.21278 | 0.21278 | 0.2481
| 11 | Redding | 1 | 1.07 | 0.010239 | 0.010239 | 0.010956
| 12 | Sacramento | 1 | 1.198 | 0.036051 | 0.036051 | 0.04319
| 13 | Fresno | 1.001 | 1.113 | 0.021693 | 0.021715 | 0.024144
| 14 | Mojave | 0.94 | 0.992 | 0.034946 | 0.032849 | 0.034666
| 15 | Palm Springs | 0.94 | 1.054 | 0.047199 | 0.044367 | 0.049748
| 16 | Susanville | 0.94 | 1.07 | 0.011973 | 0.011255 | 0.012811
| AVERAGE | Average | 0.97394 | 1.1906 | 1 | 0.98408 | 1.158
1 - Table 21, 22, 23 (Fire Suppression, Plumbing, & HVAC) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed HVAC claims)

## ADEC
From PGE3PHVC151 R4 measure cost data:
Workpaper | Measure | Measure Detail | Rev | Equipment Cost ($/ton) | Labor Cost ($/ton) | Total Cost ($/ton) | Rev | Equipment Cost ($/ton) | Labor Cost ($/ton) | Total Cost ($/ton)
PGE3PHVC151 – Economizer Repair | Economizer Repair | Non-ADEC | R3 | 19.64 | 19.78 | 39.42 | R4 | 21.9883 | 28.01 | 49.9983
|  | ADEC | R3 | 84.78 | 52 | 136.78 | R4 | 69.6053 | 56.87 | 126.4753
[8 empty] | 47.617 | 28.86 | 76.477

## CO2 SENSOR
DISTRIBUTOR QUOTE FOR CONTRACTOR PRICING
100%
LINE NO. | PRICE | CONTRACTOR MARKUP | MATERIAL SUM
1 | 254.39 | 254.39 | 508.78
RETAIL COST |  | 10%
ITEM | PRICE | "DISCOUNT" | MATERIAL SUM
SAMPLE 1 | 428 | 42.8 | 470.8
SAMPLE 2 | 180 | 18 | 198
|  | AVERAGE | 392.5267
DISTRIBUTOR SAMPLE
RETAIL SAMPLE 1
http://www.davis.com/Product/8102_CO2_Sensor_w_Display_Ventostat_Wall_Mount/YX-10101-49
RETAIL SAMPLE 2
http://www.dwyer-inst.com/Product/AirQuality/CarbonDioxideTransmitters/SeriesCDT/Ordering

## DRAFT DEER Comparison
Draft results from DEER Update Study 3/11/2014
Technology | READI Index ID | Match Pair | Description | Measure Type | Sector | Unit | Equipment Cost | Labor Hours | CA Average Labor Rate | Labor Cost | Misc. Costs | Full Installed Cost | Incremental Cost | Equipment Cost per unit | Labor Hours per unit | Labor Cost per Unit | Misc. Costs Per Unit | Misc. Fixed Costs per Project | Full Cost per Unit | Incremental Cost per Unit | Incremental Fixed Cost per Project
Demand Control Ventilation | Example Measures | Basline | No DCV | AddOn | Com | Sensor | 0 | 0 | 0 | 0 | 0 | 0 | -
|  | Measure | Duct Mounted unit single zone | AddOn | Com | Sensor | 529.0485 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2373.1579 | 2373.1579
|  | Measure | Duct Mounted unit with Digital Display and VOC Sensor single zone | AddOn | Com | Sensor | 529.0485 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2373.1579 | 2373.1579
|  | Measure | Duct Mounted unit with Humidity Sensor single zone | AddOn | Com | Sensor | 597.2327 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2441.3421 | 2441.3421
|  | Measure | Duct Mounted unit with Temperature Sensor single zone | AddOn | Com | Sensor | 490.1116 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2334.221 | 2334.221
|  | Measure | Wall Mounted unit single zone | AddOn | Com | Sensor | 356.3478 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2200.4572 | 2200.4572
|  | Measure | Wall Mounted unit with Digital Display single zone | AddOn | Com | Sensor | 440.0806 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2284.19 | 2284.19
|  | Measure | Wall Mounted unit with Humidity Sensor single zone | AddOn | Com | Sensor | 522.1614 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2366.2708 | 2366.2708
|  | Measure | Wall Mounted unit with Temperature Sensor single zone | AddOn | Com | Sensor | 415.0403 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2259.1496 | 2259.1496
|  | Measure | Wall Mounted unit with Temperature Sensor and Digital Display single zone | AddOn | Com | Sensor | 498.773 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2342.8824 | 2342.8824
|  | Measure | Wall Mounted unit with Temperature Sensor and Humidity Sensor single zone | AddOn | Com | Sensor | 580.8539 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2424.9632 | 2424.9632
|  | Measure | Wall Mounted unit with Temperature Sensor, Digital Display, and Humidity Sensor single zone | AddOn | Com | Sensor | 664.5866 | 7.5 | 86.9312 | 651.9844 | 1192.125 | 2508.696 | 2508.696
Measure | Labor | Materials | Total
Add ADEC and CO2 sensor to XXX | 695.44 | 1239.9685 | 1935.4085
difference from DEER |  |  | -348.7815
% difference from DEER |  |  | -15.27%