## cost summary
Full and Incremental Cost Equations
Installation Type | Incremental Measure Cost | Full Measure Cost
|  | 1st Baseline | 2nd Baseline
ROB | (MEC + MLC) - (BEC +BLC) | (MEC + MLC) - (BEC +BLC) | N/A
RET | (MEC + MLC) - (BEC +BLC) | MEC + MLC | (MEC + MLC) - (BEC +BLC)
MEC = Measure Equipment Cost; MLC = Measure Labor Cost
BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost
Full and Incremental Costs
Installation Type | Measure Option | Incremental Measure Cost | Full Measure Cost
|  |  | 1st Baseline | 2nd Baseline | BEC | BLC | MEC | MLC
ROB | 11.00 EER, 3.25 COP | 150.8605 | 150.8605 | N/A | 5582.3333 | 875.146 | 6110.345 | 875.146
ROB | 11.00 EER, 3.25 COP, econ & DCV | 583.7995 | 583.7995 | N/A | 5582.3333 | 875.146 | 7406.845 | 1093.9326
ROB | 11.50 EER, 3.25 COP, econ & DCV | 703.9966 | 703.9966 | N/A | 5582.3333 | 875.146 | 7827.535 | 1093.9326
RET | 10.00 EER, 3.00 COP | 0 | 1844.9941 | 0 | 5582.3333 | 875.146 | 5582.3333 | 875.146
RET | 10.00 EER, 3.00 COP, econ & DCV | 432.939 | 2277.9331 | 432.939 | 5582.3333 | 875.146 | 6878.8333 | 1093.9326
RET | 11.00 EER, 3.25 COP, econ & DCV | 583.7995 | 2428.7936 | 583.7995 | 5582.3333 | 875.146 | 7406.845 | 1093.9326
RET | 11.50 EER, 3.25 COP, econ & DCV | 703.9966 | 2548.9907 | 703.9966 | 5582.3333 | 875.146 | 7827.535 | 1093.9326

## cost calculations
SPVHP Cost Summary
IMC Assumptions
Assumed Unit Size (Tons) | 3.5
Assumed Labor Cost ($/hr)* | 109.3933
Economizer - Avg Cost Premium (MFG A & B) | 988
DCV - Avg Cost Premium (MFG A & B) | 308.5
Controls - AvG Cost Premium (MFG A & B) | 1296.5
* RS MEANS 2017 - Union Shop
Model Variation | Model Variation | Description | Equipment Cost ($) | Labor Cost ($) | MatlCost ($/ton) | Labor ($/ton) | Installed IMC ($/ton)
T1 | Baseline | EER = 10, COP = 3 (<65,000 Btu/h) | 5582.3333 | 875.146 | 1594.9524 | 250.0417 | 1844.9941
T2 | Measure | EER = 11, COP = 3.3, assumed 3.5 Ton | 6110.345 | 875.146 | 1745.8129 | 250.0417 | 1995.8546
T3 | Measure | EER = 11.5, COP = 3.3, assumed 3.5 Ton | 6531.035 | 875.146 | 1866.01 | 250.0417 | 2116.0517
T4 | Measure | EER = 10, COP = 3 (<65,000 Btu/h), economizer, CO2 sensor | 6878.8333 | 1093.9326 | 1965.381 | 312.5522 | 2277.9331
T5 | Measure | EER = 11, COP = 3.25, assumed 3.5 Ton, economizer, CO2 sensor | 7406.845 | 1093.9326 | 2116.2414 | 312.5522 | 2428.7936
T6 | Measure | EER = 11.5, COP = 3.25, assumed 3.5 Ton, economizer, CO2 sensor | 7827.535 | 1093.9326 | 2236.4386 | 312.5522 | 2548.9907
MFG | Type | EER | Ton | Base Cost | $/Ton | Advanced Control Cost | $/Ton
MFG A | HP | 10 | 3 | 4864 | 1621.3333 | 5709 | 1903
MFG A | HP | 10 | 3.5 | 5820 | 1662.8571 | 6735 | 1924.2857
MFG A | HP | 10 | 4 | 6063 | 1515.75 | 6978 | 1744.5
MFG A | HP | 11 | 3 | 5457 | 1819 | 7714 | 2571.3333
MFG A | HP | 11 | 3.5 | 5906 | 1687.4286 | 7221 | 2063.1429
MFG A | HP | 11 | 4 | 6387 | 1596.75 | 7702 | 1925.5
MFG B | HP | 11 | 3 | 5556.9 | 1852.3 | 6129.31 | 2043.1033
MFG B | HP | 11 | 3.5 | 5729.31 | 1636.9457 | 6301.72 | 1800.4914
MFG B | HP | 11 | 5 | 7625.86 | 1525.172 | 8198.27 | 1639.654
MFG B | HP | 11.5 | 2.5 | 5522.41 | 2208.964 | 6094.82 | 2437.928
MFG B | HP | 11.5 | 4 | 7539.66 | 1884.915 | 8112.07 | 2028.0175
MFG | Nominal Tonnage | EER | Unit Cost | Curb | Base Unit Cost | Economizer | DCV | Advanced Control Cost
MFG A | 3 | 10.00 | 4864 | NA | 4864 | 400 | 445 | 5709
MFG A | 3.5 | 10.2 | 5820 | NA | 5820 | 470 | 445 | 6735
MFG A | 4 | 10.00 | 6063 | NA | 6063 | 470 | 445 | 6978
MFG A | 3 | 11.00 | 5457 | Incl | 5457 | 1812 | 445 | 7714
MFG A | 3.5 | 11.00 | 5906 | Incl | 5906 | 870 | 445 | 7221
MFG A | 4 | 11.00 | 6387 | Incl | 6387 | 870 | 445 | 7702
MFG B | 3 | 11.00 | 5556.9 | Included in Unit Cost | 5556.9 | 400 | 172.41 | 6129.31
MFG B | 3.5 | 11.00 | 5729.31 | Included in Base Cost | 5729.31 | 400 | 172.41 | 6301.72
MFG B | 5 | 11.00 | 7625.86 | Included in Base Cost | 7625.86 | 400 | 172.41 | 8198.27
MFG B | 2.5 | 11.50 | 5522.41 | Included in Base Cost | 5522.41 | 400 | 172.41 | 6094.82
MFG B | 4 | 11.50 | 7539.66 | Included in Base Cost | 7539.66 | 400 | 172.41 | 8112.07

## MFG A
Cost Summary - MFG A
Nominal Tonnage | CoolingCapacity95F | EER95F | IPLV | Phase | heatingCapacity47F | COP47F | ModelStatus | Unit Cost | Curb | Economizer | DCV | Total Cost
3 | 34600 | 10.00 |  | 1 | 32000 | 3.00 | Active | 4864 | NA | NA | NA | 4864
3.5 | 40500 | 10.2 |  | 1 | 38500 | 3 | Active | 5820 | NA | NA | NA | 5820
4 | 47000 | 10.00 |  | 1 | 44000 | 3.00 | Active | 6063 | NA | NA | NA | 6063
3 | 35000 | 11.00 | 14.5 | 1 | 31000 | 3.30 | Active | 5457 | incl | 1812 | 445 | 7714
3.5 | 40000 | 11.00 | 14.5 | 1 | 38500 | 3.40 | Active | 5906 | incl | 870 | 445 | 7221
4 | 45500 | 11.00 | 15.0 | 1 | 41500 | 3.40 | Active | 6387 | incl | 870 | 445 | 7702

## MFG B
Cost Summary - MFG A
Nominal Tonnage | CoolingCapacity95F | EER95F | IPLV | Phase | heatingCapacity47F | COP47F | ModelStatus | Unit & Curb Cost | Econo Cost | DCV Cost | Total Cost w/ DCV
2 | 23500 | 11.00 |  | 1 | 33000 | 3.25 | Active | 5160.34 | 400 | 172.41 | 5332.75
3 | 34600 | 11.00 |  | 1 | 33000 | 3.25 | Active | 5556.9 | 400 | 172.41 | 5729.31
3.5 | 40500 | 11.00 |  | 1 | 39000 | 3.25 | Active | 5729.31 | 400 | 172.41 | 5901.72
5 | 56500 | 11.00 |  | 1 | 51000 | 3.00 | Active | 7625.86 | 400 | 172.41 | 7798.27
2.5 | 28000 | 11.50 |  | 1 | 26000 | 3.00 | Active | 5522.41 | 400 | 172.41 | 5694.82
4 | 47000 | 11.50 |  | 1 | 42000 | 3.25 | Active | 7539.66 | 400 | 172.41 | 7712.07
Labor Hours:
[12 empty] | SPVHP install | 8
[12 empty] | DCV install | 2 | 1 | Install sensor | (DCV labor estimates based on Work Paper SCE13HC061 and judgement)
[14 empty] | 1 | Measure and set min/max ventilation + functional test

## RS MEANS_Pkg HVAC Install
HVAC Install Hours
Labor Type | Average Labor Rate ($/ hr) | Avg Labor Rate w/ O&P ($/ hr)
Standard Union | 72.6344 | 109.3933
Open Shop | 53.1813 | 87.6979
Data Release : Year 2017 |  |  |  | Unit Cost Estimate
Quantity | LineNumber | Line Source | Labor Type SubContracted Ind. | Description | Crew | Daily Output | Labor Hours | Unit | Material | Labor | Labor Costs/ Hour | Equipment | Total | Ext. Mat. | Ext. Labor | Ext. Equip. | Ext. Total | Mat. O&P | Labor O&P | Labor O&P ($/ hr) | Equip. O&P | Total O&P | Ext. Mat. O&P | Ext. Labor O&P | Ext. Equip. O&P | Ext. Total O&P | Labor Type | Data Release | CCI Location | Notes
0 | 237433101100 |  | Standard Union | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1656.23 | 72.451 | 0 | 4456.23 | 0 | 0 | 0 | 0 | 3075 | 2500.58 | 109.3867 | 0 | 5575.58 | 0 | 0 | 0 | 0 | STD | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
0 | 237433101120 |  | Standard Union | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1916.03 | 72.5769 | 0 | 5241.03 | 0 | 0 | 0 | 0 | 3650 | 2890.28 | 109.4803 | 0 | 6540.28 | 0 | 0 | 0 | 0 | STD | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
0 | 237433101140 |  | Standard Union | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 2078.4 | 72.8752 | 0 | 6453.4 | 0 | 0 | 0 | 0 | 4800 | 3117.6 | 109.3128 | 0 | 7917.6 | 0 | 0 | 0 | 0 | STD | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
0 | 237433101100 |  | Open Shop | Rooftop air conditioner, single zone, electric cool, gas heat, 3 ton cooling, 60 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.7 | 22.86 | Ea. | 2800 | 1214.57 | 53.1308 | 0 | 4014.57 | 0 | 0 | 0 | 0 | 3075 | 2013.45 | 88.0774 | 0 | 5088.45 | 0 | 0 | 0 | 0 | OPN | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
0 | 237433101120 |  | Open Shop | Rooftop air conditioner, single zone, electric cool, gas heat, 4 ton cooling, 95 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.61 | 26.4 | Ea. | 3325 | 1396.43 | 52.8951 | 0 | 4721.43 | 0 | 0 | 0 | 0 | 3650 | 2305.73 | 87.3383 | 0 | 5955.73 | 0 | 0 | 0 | 0 | OPN | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
0 | 237433101140 |  | Open Shop | Rooftop air conditioner, single zone, electric cool, gas heat, 5 ton cooling, 112 MBH heating, includes, standard controls, curb and economizer | Q5 | 0.56 | 28.52 | Ea. | 4375 | 1526.33 | 53.5179 | 0 | 5901.33 | 0 | 0 | 0 | 0 | 4800 | 2500.58 | 87.6781 | 0 | 7300.58 | 0 | 0 | 0 | 0 | OPN | Year 2017 | CALIFORNIA / SACRAMENTO (942,956-958)
Total | [12 empty] | 30787.99 | 0 | 0 | 0 | 0 |  |  |  |  | 38378.22 | 0 | 0 | 0 | 0