Work Paper SCE13HC031

Revision 1

Southern California Edison Company

Air Handler Variable Speed Motor

# At-a-Glance Summary

| Applicable Measure Codes: | AC-65986 |
| --- | --- |
| Measure Description: | Replace existing blower motors with variable speed motors. |
| Base Case Description: | Nonresidential air handler unit with a permanent split capacitor motor. |
| Energy Impact Common Units: | Per air handler unit |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | 15 years (EUL ID: Motors-Fan) |
| Measure Application Type: | Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | 0.60 (Com-Default>2yrs, Ind-Default>2yrs) |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13HC031.0 | Yes | 6/07/2012 | Ricson Chude/SCE | Modifications from WPSCNRHC0031.0: - Savings based on PGECOHV125 R3 - Updated references and added applicable building types. |
| SCE13HC031.1 | No | 7/03/2014 | Bach Tsan/SCE, Jason Wang/SCE | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - Savings Based on PGECOHVC125 |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the installation of variable speed motors (VSM) of 10 hp or less in conjunction with a new air conditioner or heat pump, split or packaged unit air handler system. The base case for this measure is a nonresidential-type air handler with constant-speed fan motor.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| AC-65986 | Variable Speed Drive on Air Handler Motor Controls |

Measure Requirements

- Supply air blower with a new super-efficient direct replacement brushless permanent magnet blower motor with built-in controller must replace the existing permanent split capacitor motor.

- Motor must be 10 horsepower or less to be eligible for this rebate.

- Motor must be capable of plugging into existing control board.

- A variable frequency drive (VFD) is not eligible for this rebate.

## 1.2 Technical Description

Most existing small-scale commercial heating, ventilation and air conditioning (HVAC) blowers use low cost, low efficiency, single speed motors. These motors usually range in power between 0.3 hp and 2 hp. They turn on and off as required by thermostat control. This results in temperature variations and high energy consumption of the air handler motor.

Most major HVAC manufacturers are now offering variable-speed motor air handlers. These motors have integrated electronic controls that modulate the motor and fan speed based on the cooling or heating load of the system; they run at lower speed most of the time. These motors provide much more efficient operation, and improve the quality of the air distribution; however, they come at a price premium. Please note that variable speed motors are different from variable frequency drives (VFD); a VFD is an electronic drive added to a motor, while a multiple speed brushless motor is a motor with built-in speed-modulating capability.

This measure is designed to encourage the installation of such variable-speed motor air handlers in small commercial buildings. Because of the theoretical cubic relationship between fan power and fan speed, a small reduction in fan speed can result in large energy savings.

## 1.3 Measure Application Type

The delivery methods for this workpaper are:

- Financial Support Downstream Incentive – Deemed

The Program Type for this workpaper is ROB (Replace-on-Burnout)

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

DEER 2014 does not contain an exact match for this measure. The closest similar measure in DEER is for variable-frequency drives (VFDs), but the DEER measure for VFDs does not accurately represent the energy impacts for multi-speed motors applications. Therefore, custom temperature bin calculations have been used to estimate energy savings for multi-speed motors as explained in Section 2 of this workpaper.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | N/A |
| DEER Version | DEER 2014 |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | All | 0.6 |
| Ind-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ind | Any | All | 0.6 |

*Denotes that the column is taken from the DEER NTG Table.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 5 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1.0 |

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measue Case UseCategory | HVAC |
| Measure Case UseSubCats | Space Heating and Cooling |
| Measure Case TechGroups | Motor |
| Measure Case TechTypes | General Purpose |
| Base Case TechGroups | Motor |
| Base Case TechTypes | General Purpose |

### 1.4.2 Codes and Standards Analysis

Title 20: These measures do not fall under Title 20 of the California Energy Regulations.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Federal Standards: The Energy Independence and Security Act (EISA) 2007 [226], effective December 19, 2010, mandates that motors manufactured or imported into the United States must meet at a minimum NEMA Premium™ Efficiency Levels. These levels are defined by the NEMA Standards Publication MG 1-2009, Revision 1-2010, Part 12, Page 35, Table 12-12 for motors 1 to 200 hp, design A&B. The standard applies to NEMA design A and B, integral horsepower, general purpose, ODP and TEFC motors (1200, 1800, and 3600 RPMs) from 1-200 hp.

The applicable codes and standards for these measures do not dictate associated hours of operation, measure or baseline costs, EUL, NTG, or in-service rate for the equipment involved.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Federal Standards | Section 313 | December 19, 2010 |

### Non-DEER Study Review

The following assumptions from other sources were used to estimate savings:

2009 ASHRAE Fundamentals Handbook [444]: Maximum cooling and heating loads were calculated based on climate-zone-specific design heating and cooling temperatures, obtained from climatic design information in the 2009 ASHRAE Fundamentals Handbook pages 14.18 and 14.19.

Energy Consumption Characteristics of Commercial Building HVAC Systems – Volume III: Energy Savings Potential [445]: Proposed case fan speed is equal to the load on the heating or cooling coil as a percentage of total capacity on the heating or cooling coils. Multiple speed brushless fan motors are 10% more efficient than the base case based on this DOE document on variable speed motors, page 4-24.

Hours of Operation: The assumed hours of operation are based on a building operating schedule of 8AM to 6PM Monday through Friday.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 8 below identifies the value/methodology used for the measures in this work paper.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| Motors-Fan | Non-Residential | HVAC | HVAC Fan Motors | 15 | 5 |

# Section 2. Energy Savings & Demand Reduction Calculations

Customized weather temperature bin simulations were used to estimate energy savings. The following assumptions were made:

- The electric savings were estimated using customized weather bin simulations (see Attachment 2 for calculations).

- Air handler fan was assumed to be operating to meet cooling and heating loads.

- Cooling and heating loads were based on climate data and were assumed to vary linearly with outside air temperature.

- Base case fan runtime is equal to the load as a percentage of total capacity on the heating or cooling coils.

- Multiple speed fan motors behave similarly to fan motors equipped with variable frequency drives.

- Assumed 0.5-hp air handler motor and a supply air flowrate of 500 cfm (Attachment 3).

Table 8 BIN Simulation Inputs and Assumptions

## 2.2 Energy Savings Estimation Methodologies

The following relationships between speed and energy consumption were used to determine baseline and measure case energy consumption. The energy savings is calculated as follows:

ES=ECB-ECM

Where:

ES 	= energy savings, kWh

ECB	= baseline energy consumption of the fan per temperature bin, kWh

ECM	= baseline energy consumption of the fan per temperature bin, kWh

Baseline energy consumption for each temperature bin is estimated as follows:

ECB=A+B*SpeedB+CSpeedB2*HP*C*PFeffB*AH

Where:

A	= 0.21976, constant, determined from the CEC Guidebook (Attachment 6), no units

B	= -0.8748, constant, determined from the CEC Guidebook, no units

C	= 1.65259, constant, determined from the CEC Guidebook, no units

SpeedB	= baseline fan speed, % of nominal speed

HP	= 0.5, fan horsepower, hp

C	= 0.746, hp to kW conversion, kW/hp

PF	= 0.80, assumed power factor, no units

effB	= 0.77, baseline efficiency based on the NEMA efficiency tables (Attachment 4), no units

AH	= annual operating hours for temperature bin, hours

The measure case energy consumption for each temperature bin is estimated as follows:

ECM=A+B*SpeedM+CSpeedM2*HP*C*PFeffM*AH

Where:

SpeedM= measure fan speed, % of nominal speed

effM	= 0.85, measure case efficiency assuming a 10% efficiency increase [445], no units

Example for CZ 13:

The baseline and measure energy consumption for one temperature bin is:

ECB=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.77*9

=3.6 kWH

ECM=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.85*9

=3.3 kWH

After summing energy consumption across all temperature bins, the energy savings is estimated as:

ES=391.6 kWh-235.8 kWh=155.7kWh

## 2.2 Demand Reduction Estimation Methodologies

The following relationships between speed and energy consumption were used to determine baseline and measure case energy consumption. The energy savings is calculated as follows:

DR=MDB-MDM

Where:

DR	= demand reduction, kW

MDB	= baseline maximum demand, kW

MDM	= measure maximum demand, kW

The baseline demand for the highest temperature bin is estimated as follows:

MDB=A+B*SpeedB+CSpeedB2*HP*C*PFeffB

The measure case demand for the highest temperature bin is estimated as follows:

MDM=A+B*SpeedM+CSpeedM2*HP*C*PFeffM

Example for CZ 13:

MDB=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.77

=0.387 kW

MDM=0.21976+-0.8748*1.0+1.65259 1.02*0.5*0.746*0.800.85

=0.351 kW

DR    =0.387-0.351=0.036 kW

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  The closest load shape chosen for this measure is the DEER:HVAC_Split-Package_AC load shape. See Table 11 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 9 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Assembly | NON RES | DEER:HVAC_Split-Package_AC |
| Education - Primary School | NON RES | DEER:HVAC_Split-Package_AC |
| Education - Secondary School | NON RES | DEER:HVAC_Split-Package_AC |
| Education - Community College | NON RES | DEER:HVAC_Split-Package_AC |
| Education - University | NON RES | DEER:HVAC_Split-Package_AC |
| Lodging - Hotel | NON RES | DEER:HVAC_Split-Package_AC |
| Lodging - Motel | NON RES | DEER:HVAC_Split-Package_AC |
| Manufacturing - Bio/Tech | NON RES | DEER:HVAC_Split-Package_AC |
| Manufacturing - Light Industrial | NON RES | DEER:HVAC_Split-Package_AC |
| Industrial | NON RES | DEER:HVAC_Split-Package_AC |
| Misc - Commercial | NON RES | DEER:HVAC_Split-Package_AC |
| Office - Large | NON RES | DEER:HVAC_Split-Package_AC |
| Office - Small | NON RES | DEER:HVAC_Split-Package_AC |
| Retail - Multistory Large | NON RES | DEER:HVAC_Split-Package_AC |
| Retail - Single-Story Large | NON RES | DEER:HVAC_Split-Package_AC |
| Retail - Small | NON RES | DEER:HVAC_Split-Package_AC |
| Storage - Conditioned | NON RES | DEER:HVAC_Split-Package_AC |
| Warehouse - Refrigerated | NON RES | DEER:HVAC_Split-Package_AC |
| Transportation - Communication - Utilities | NON RES | DEER:HVAC_Split-Package_AC |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The base case cost is the average of cost estimates for three different air handler models, from two different HVAC installers. The installer estimates included both material and labor. This cost survey was performed in April 2008 and adjusted to account for inflation between 2008 and 2014 (8.6%).

Base Case Cost=Average of Installer Estimates*(1+Inflation)

Base Case Cost=$1,460*1.086=$1,590

## 4.2 Measure Case Cost

The measure case cost is the average of cost estimates for two different air handler models, from two different HVAC installers. The installer estimates included both material and labor. This cost survey was performed in April 2008 and adjusted to account for inflation between 2008 and 2014 (8.6%).

Measure Case Cost=$1,800*1.086=$1,950

Since the material and labor costs were not separated in the estimates from the HVAC installers, it is not assumed that the labor costs are the same in base and measure cases. Therefore, to determine climate zone-specific costs, the costs shown in Section 4.1 and 4.2 were multiplied by an average of the material and labor climate multipliers.

Cost sources are in Attachment 5, and climate zone-specific costs are calculations in Attachment 1.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For ROB measures, the Gross Measure Cost (GMC) is represented by the equation below:

GMC = (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

= ($1,950-$1,590)

= $360

### 4.3.2 Incremental Measure Cost

For ROB measures, the Incremental Measure Cost is the same as the GMC.

# Attachments

# References

| [31] | Load Shape Update Initiative - KEMA / JJ Hirsch and Assoc. / Itron Inc. - November 17, 2006 |
| --- | --- |
| [226] | Energy Independence and Security Act of 2007 |
| [351] | Energy Efficiency Policy Manual-Version 5 |
| [436] | 2014 DEER EUL Table - Update |
| [444] | 2009 ASHRAE Fundamentals Handbook |
| [445] | Energy Consumption Characteristics of Commercial Building HVAC Systems Volume III: Energy Savings Potential |

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |