Workpaper PGECOPRO103

Tank Insulation

Revision 5

Pacific Gas & Electric Company

Customer Energy Efficiency Department

Tank Insulation

Measure Codes H13, H18, H114, H115

# At-A-Glance Summary

| Applicable Measure Codes: | H13 | H115 | H18 | H114 |
| --- | --- | --- | --- | --- |
| Measure Description: | This measure provides incentives for installing 2” thick insulation on a bare tank (120º-170ºF) | This measure provides incentives for installing 1” thick insulation on a bare tank (120º-170ºF) | This measure provides incentives for installing 2” thick insulation on a bare tank (170º-200ºF) | This measure provides incentives for installing 1” thick insulation on a bare tank (170º-200ºF) |
| Energy Impact Common Units: | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation |
| Base Case Description: | Bare uninsulated tank | Bare uninsulated tank | Bare uninsulated tank | Bare uninsulated tank |
| Base Case Energy Consumption: | Source: PG&E/SCG calculations 18.53 therms/yr.ft2 | Source: PG&E/SCG calculations 18.53 therms/yr.ft2 | Source: PG&E/SCG calculations 29.14 therms/yr.ft2 | Source: PG&E/SCG calculations 29.14 therms/yr.ft2 |
| Measure Energy Consumption: | Source: PG&E/SCG calculations 1.30 therms/yr.ft2 | Source: PG&E/SCG calculations 2.30 therms/yr.ft2 | Source: PG&E/SCG calculations 1.99 therms/yr.ft2 | Source: PG&E/SCG calculations 3.52 therms/yr.ft2 |
| Energy Savings (Base Case – Measure) | Source: PG&E/SCG calculations 17.23 therms/yr.ft2 | Source: PG&E/SCG calculations 16.23 therms/yr.ft2 | Source: PG&E/SCG calculations 27.15 therms/yr.ft2 | Source: PG&E calculations 25.62 therms/yr.ft2 |
| Costs Common Units: | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation | sq. ft. of insulation |
| Base Case Equipment Cost ($/unit): | Source: N/A 0. | Source: N/A 0. | Source: N/A 0. | Source: N/A 0. |
| Measure Equipment Cost ($/unit): | Source: MEANS Mechanical Cost 2014 and McMaster Carr catalog $12.04 | Source: MEANS Mechanical Cost 2014 and McMaster Carr catalog $9.49 | Source: MEANS Mechanical Cost 2007 and McMaster Carr catalog $12.04 | Source: MEANS Mechanical Cost 2007 and McMaster Carr catalog $9.49 |
| Measure Incremental Cost ($/unit): | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above | Equal to Measure Equipment Cost above |
| Effective Useful Life (years): | Source: CALMAC 11 years | Source: CALMAC 11 years | Source: CALMAC 11 years | Source: CALMAC 11 years |
| Program Type: | Retrofit Add On (REA) | Retrofit Add On (REA) | Retrofit Add On (REA) | Retrofit Add On (REA) |
| Net-to-Gross Ratios: | 0.60 Source: DEER 2014, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2014, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2014, NTGR_ID: Ind-Default>2yrs | 0.60 Source: DEER 2014, NTGR_ID: Ind-Default>2yrs |

# Work Paper Approvals

The following Manager(s) approved this work paper through the PG&E

| Electronic Data Routing System under Routing Requisition # ___________________________ Grant Brohard Manager, Engineering Services |  |
| --- | --- |
| Carolyn Weiner Manager, Products |  |

# Document Revision History

Revision # 		Date 		         Description		         Author (Company)

| Superseded |  | Pipe-Tank Insulation WP 050503.doc |  |
| --- | --- | --- | --- |
| Revision 0 | 05/22/2008 | Tank Insulation PGECOPRO103 R0.doc | Nicolas Fauchier-Magnan (kW Engineering) |
| Revision 1 | 05/22/2009 | Tank Insulation PGECOPRO103 R1.doc | Steve Fok (PG&E) |
| Revision 2 | 03/05/2010 | Tank Insulation PGECOPRO103 R2.doc Updated NTG | Andrew Wieszczyk (PG&E) |
| Revision 3 | 8/11/11 | Inserted temperature dependent conductivity language and updated catalog language | Brennan Herdt (kW) Andrew Wieszczyk (PG&E) |
| Revision 4 | 6/15/12 | - Changed from RET to ROB - Updated NTGR - Updated cost info to most recent available values. | Andrew Wieszczyk (PG&E) |
|  | 8/29/12 | Nomenclature Update | Justin Westmoreland (PG&E) |
| Revision 5 | 5/15/14 | Update based on SCG 3/21/14 revised WP WPSSCGNRM1050101A R28. PG&E revision included (1) PG&E ten weather-zone-averaged Measure IMC, Base and Measure Case energy savings, (2) new Measure Application Type of REA, EUL and (3) new template and database format. | Steve Fok (PG&E) |

# Table of Contents

At-A-Glance Summary	i

Work Paper Approvals	ii

Document Revision History	iii

Table of Contents	iv

List of Tables	v

List of Figures	v

Section 1. General Measure & Baseline Data	1

1.1	Product Measure Description & Background	1

1.2	Measure Technical Description	1

1.3	Measure Application Type	2

1.4	Product Base Case and Measure Case Data	2

1.4.1 DEER Base Case and Measure Case Information	2

1.4.2 Code and Standards Requirements Analysis	2

1.4.3 EM&V, Market Potential and Other Studies – Base Case and Measure Case	2

Section 2.  Calculation Methods	3

2.1 Electric Energy Savings Estimation Methodologies	3

2.2. Demand Reduction Estimation Methodologies	3

2.3. Gas Energy Savings Estimation Methodologies	3

Section 3. Load Shapes	6

3.1 Base Case Load Shapes	6

3.2 Measure Load Shapes	6

Section 4.  Base Case & Measure Costs	6

4.1  Base Case Cost	6

4.2  Measure Costs	7

4.3  Incremental and Full Measure Costs	8

Index	9

References	10

# List of Tables

Table 1 - Net-to-Gross Ratios	3

Table 2 - Insulation Conductivity	4

Table 3 - Energy Savings Calculations	6

Table 4 - Measure materials costs 6	7

Table 5 - Measure labor costs7	7

Table 6 - Measure total costs	7

# List of Figures

Figure 1- Distribution of Thermal Efficiencies for Hot Water Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database	5

# Section 1. General Measure & Baseline Data

## 1.1	Product Measure Description & Background

Catalog Description Requirements:

- One or two inch diameter of fiberglass or foam insulation must be added to existing bare liquid, solution storage or transfer tanks.

- The tanks must be coupled to gas-fired commercial or industrial equipment that transfers heat to the contained liquid or solution.

- Tanks with pre-existing insulation do not qualify for a rebate.  This rebate cannot be used for the replacement of old or damaged insulation.

- California Building Energy Efficiency Standards (Title 24), Section 123 establishes requirements for tank insulation in the design and installation of space-conditioning and service water heating systems and equipment.  Any tank requiring insulation per these standards does not qualify for a rebate.  Details are available at ww.energy.ca.gov/title24.

- Tanks insulated to prevent burns do not qualify for rebate.  Insulation for exposed hot-water tanks within 7 feet of the floor that are not otherwise guarded in such manner as to prevent contact do not qualify for rebate.

Application Process:

- The insulation thickness and tank solution temperature will determine the rebate amount.

- Must include manufacturer’s name, insulation material type and the material k-value rating.

Program Restrictions and Guidelines

Terms and Conditions

The rebate is downstream provided to the customer at the time of installation upon receipt of application and invoice.  This is not a Direct Install program (See Catalog Description above).

Market Applicability

This measure applies to most commercial and industrial facilities, including, but not limited to, offices, restaurants, retail, schools, colleges, hotels, motels, and recreational facilities.

The customers are not considered Hard to Reach.

## 1.2	Measure Technical Description

Owing to first cost sensitivity and/or a low level of awareness, many commercial and industrial customers – particularly smaller, hard to reach businesses – install tanks and piping systems with no insulation. These measures address cost-effective energy efficiency opportunities in the tank insulation area.

Installing insulation on a bare surface greatly reduces heat losses to ambient air, achieving significant energy savings at a relatively low cost.

## 1.3	Measure Application Type

This measure is classified under Measure Application Type of “Retrofit Add On” (REA).

| Code | Description | Comment |
| --- | --- | --- |
| ER | Early retirement | measure applied while existing equipment still viable, or retrofit of existing equipment |
| ROB | Replace on Burnout | measure applied when existing equipment fails or maintenance requires replacement |
| NC | New Construction | measure applied during construction design phase as an alternative to a code-compliant standard design |
| REA | Retrofit Add On | Single baseline (above pre-existing), full measure costs required. |

## Product Base Case and Measure Case Data

### 1.4.1 DEER Base Case and Measure Case Information

The DEER database does not contain any measure for tank surface insulation.

### 1.4.2 Code and Standards Requirements Analysis

This measure is not governed by either state Title 24 and Title 20 or federal codes and standards.

### 1.4.3 EM&V, Market Potential and Other Studies – Base Case and Measure Case

Measure Effective Useful Life

Currently, there is no DEER measure for this type of insulation installation. There is however pipe insulation measure, Measure ID: WtrHt-PipeIns-Gas (Commercial) from DEER 2013 identifies as having an 11-years life for gas water heater and a life of 13 years for electric water heater.  A value of 11 years is used in this work paper as the EUL for commercial and industrial tank insulation.

- Net-to-Gross Ratios for Different Program Strategies

Table 1 below summarizes all applicable Net-to-Gross ratios for programs that may be used by this measure.  The NTGR for this measure is a default value taken from DEER 2013  equaling 0.60.  This NTGR represents the default for existing industrial measures with no evaluated NTGR that have had the same delivery mechanism for more than two years.

Table 1 - Net-to-Gross Ratios

|  |  |  | DEER Spreadsheet |  |
| --- | --- | --- | --- | --- |
| Program Approach | NTG | NTGR_ID | File name | Cell Number |
| ALL | 0.60 | Ind-Default>2yrs | DEER2013Support Table_NTGR.xlsx | E52 |

- Gross Realization Rate

Gross realization rate of 1.0 was applied for this measure.

# Section 2.  Calculation Methods

## 2.1 Electric Energy Savings Estimation Methodologies

There is no electric energy savings associated with this gas measure.

## 2.2. Demand Reduction Estimation Methodologies

There is no demand reduction associated with this gas measures.

## 2.3. Gas Energy Savings Estimation Methodologies

The savings from this method result from reduced heat losses on the tank surface, resulting in reduced heating load on the connected gas-fired equipment. The savings were calculated as the difference in heat losses between the uninsulated tank surface (base case) and the insulated surface (measure). Average boiler efficiency (calculated from the CEC boiler listing)  was then factored in to translate the reduced heat losses from the tank into reduced gas consumption of the boiler.

Methodology

The annual energy saved by tank insulation can be calculated as follows:

Where:

Q = annual energy savings (in therms)

t = annual operating time, in hours

Qb = Heat Loss from Bare Tank (Btu/hr/ft2)

Qi = Heat Loss from Insulated Tank (Btu/hr/ft2)

Eb = Efficiency (%) of the boiler being used to generate the hot water in the tank

100,000 = conversion factor (1 therm = 100,000 Btu)

Heat loss calculations

The heat loss calculations were performed using industry-accepted software from the North American Insulation Manufacturers Association (NAIMA). The NAIMA 3E Plus v4.1 software  uses the calculation methodology from the most recent version of the ASTM C 680 Standard. The main inputs used in the software were:

- Base case: bare surface (to stay consistent with catalog Terms and Conditions)

- Base tank material: steel – emissivity: 0.8
Steel is the most common material for hot water tanks

- Insulation material: Fiber glass-type insulation (cellular glass BLOCK, Gr1, C552-07). The temperature-dependent thermal conductivity of the fiber glass used by 3E Plus software is shown in Table 2. Foam insulation (the other acceptable type of material in this measure) has similar R-values to fiber glass and provides similar savings to fiberglass, since the savings are driven primarily by the heat losses from the base case (uninsulated tank).

Table 2 - Insulation Conductivity

- Jacket material: Aluminum, new, emittance: 0.04

- Operating hours: 8,760 hours /yr  (assuming continuous tank operation)

- Process temperature (temperature inside the tank): 145ºF for low temperature range and 185ºF for high temperature range. 
Temperatures were chosen as the midpoints of the temperature ranges for each measure. 145ºF = (120 ºF +170 ºF)/2, 185 ºF = (170 ºF +200 ºF)/2

- Zone Weather Conditions:  Conditions of the air surrounding the tank (primarily temperature and wind speed) have to be estimated, as follows:

  - Outdoor ambient conditions, the DEER 2013 Annual average dry-bulb temperatures in degree F and Wind Speed in mph are selected for the 16 weather zones.

  - For Tanks located indoors, the indoor air conditions were assumed with an air temperature of 75ºF and wind speed of 0 mph.

Boiler efficiency

To convert reduced heat losses from the tank into energy savings of the boiler, boiler efficiency needs to be taken into account. To determine representative boiler efficiencies, data from the California Energy Commission (CEC) was examined.3   The CEC lists several hundred steam and hot water boilers. The average efficiency of the boilers in this listing was calculated for hot water boilers, both for small and large boilers listings. We obtained an average efficiency value of 82.5% for hot water boilers and used this value to compute the energy input for hot water.

The figure below shows the distribution of thermal efficiencies based on the CEC listing data.

Figure 1- Distribution of Thermal Efficiencies for Hot Water Boilers (300-2,500 MBtu/hr) in the CEC Appliance Efficiency Database

Results

Table 3 below presents the inputs and the results for the outdoor tank insulation of this measure.

Table 3 - Energy Savings Calculations

| Measure code | Low temperature tank |  | High temperature tank |  |
| --- | --- | --- | --- | --- |
| Tank contents temperature range | 120-170 | 120-170 | 170-200 | 170-200 |
| Tank contents assumed temperature (for calculations) | 145 |  | 185 |  |
| Assumed annual operating hours | 8760 |  |  |  |
| Average boiler efficiency | 82.5% |  |  |  |
| Base case |  |  |  |  |
| Heat loss from 3EPlus software (Btu/hr.ft²) | 125.7 |  | 221.5 |  |
| Yearly energy consumption (therms/ft².yr) | 13.35 |  | 23.52 |  |
| Proposed case - with insulation |  |  |  |  |
| Insulation thickness (inches) | 1 | 2 | 1 | 2 |
| Heat loss from 3EPlus software (Btu/hr.ft²) | 15.47 | 9.11 | 26.21 | 15.25 |
| Yearly energy consumption (therms/ft².yr) | 1.64 | 0.97 | 2.78 | 1.62 |
| Heat loss reduction (Btu/hr.ft²) | 110.23 | 116.59 | 195.29 | 206.25 |
| Annual energy savings (therms/yr.ft²) | 11.70 | 12.38 | 20.74 | 21.90 |

# Section 3. Load Shapes

## 3.1 Base Case Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

## 3.2 Measure Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

# Section 4.  Base Case & Measure Costs

## 4.1  Base Case Cost

There is no base case costs associated with these measures. The base case is existing tanks with no insulation.

## 4.2  Measure Costs

Typical material costs for this measure were estimated using the McMaster-Carr website.  The cost data below was updated to match the McMaster-Carr data as of June 2012.  Different insulation materials meeting the measures requirements were priced for 1 inch and 2 inch thicknesses, and a simple average of these costs was used, as in table-4.

Typical installation labor costs were calculated using the RS Means   and assuming a 25% overhead and profit (O&P). The 2014 version of RS Means Mechanical Cost Data provided the labor cost, as shown in table-5.

Table 4 - Measure materials costs 6

| Material Cost | Material | Material Cost ($ / ft²) |  | McMaster Item |
| --- | --- | --- | --- | --- |
| 1 inch thickness | Rigid fiberglass w. aluminum jacket |  | 1.75 | 9350K1 |
|  | Rigid polystyrene foam |  | 1.71 | 9255K1 |
|  | Fiberglass | 0.72 |  | 9160K4 |
|  | Aluminum insulation jacketing | 1.91 |  |  |
|  | Fiberglass + aluminum jacket - total cost |  | 2.63 |  |
| 2 inch thickness | Rigid fiberglass w. aluminum jacket |  | 2.68 | 9350K3 |
|  | Rigid polystyrene foam |  | 3.27 | 9255K3 |
|  | Fiberglass | 0.83 |  | 9346K38 |
|  | Aluminum insulation jacketing | 1.91 |  |  |
|  | Fiberglass + aluminum jacket - total cost |  | 2.74 |  |
|  | Average cost ($ / ft² ) for 1 inch |  | 2.18 |  |
|  | Average cost ($ / ft² ) for 2 inch |  | 2.85 |  |

Table 5 - Measure labor costs7

| Labor Costs | Labor without O&P ( $ / ft² ) | Labor include O&P ( $ / ft² ) | RS Means Item # |
| --- | --- | --- | --- |
| I inch insulation | $5.85 | $7.31 | 23 07 16.10 2420 |
| 2 inch insulation | $7.35 | $9.19 | 24 07 16.10 2440 |
| % O&P assumed |  | 25% |  |

Table 6 - Measure total costs

| Cost Summary | 1 in insulation | 2 in insulation |
| --- | --- | --- |
| Material costs ($ / ft²) | $2.18 | $2.85 |
| Labor Costs ($ / ft²) | $7.31 | $9.19 |
| Total Cost ($ / ft²) | $9.49 | $12.04 |

## 4.3  Incremental and Full Measure Costs

Incremental costs are equal to measure costs since the base costs are zero. Full measure costs are equal to measure costs.

# Index

3E Plus v4 software	9

ASTM C 680 Standard	9

Boiler efficiency	10

California Energy Commission	See CEC

CEC	10

cellular glass	9

DEER	7

Effective Useful Life	See EUL, See EUL

EUL	8

heat losses	7, 9

Load Shapes	11

Process temperature	10

# References

Technology and Measure Cost Data/Effective and Remaining Useful Life (EUL/RUL) Values.  (“DEER2014 Database for Energy-Efficiency Resources, READI_v1.0.4, Updated for 2014 Codes ( http://www.deeresources.com/).

DEER 2014 Net-To-Gross Ratios (“DEER2013 Database for Energy-Efficiency Resources, READI_v1.0.4, Updated for 2014 Codes (found at http://www.deeresources.com)

? California Energy Commission Appliance Efficiency Database at

http://www.appliances.energy.ca.gov/AdvancedSearch.aspx

3E Plus® v4.1 Insulation Thickness Computer Program - http://www.pipeinsulation.org/

ASTM C 680 Standard Practices for Determination of Heat Gain or Loss and the Surface Temperature of Insulation Piping on Equipment Systems by the Use of a Computer System – www.astm.org

McMaster-Carr catalog, items #9350K1, 9255K1, 9160K4, 9350K3, 9255K3, 9346K38

www.mcmaster.com , retrieved March 2014

2014 RS Means Mechanical Cost Data, item # 23 07 16.10 2420/2440 on page 267

8 Southern California Gas Company, “Tank Insulation Work Paper WPSCGNRM 050101A Revision 2” dated March 21, 2014.