## Tissue
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Tissue Mill
DATE OF SURVEY: |  | Apr 25,05
CONTRACTOR: |  | SteamGard
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 221 | 17 | 33 | 6 | 1 |  | 278
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
[6 empty] | 237 |  |  |  | 3
|  | 50 | 60 | 61 to 99 | 100 | 101-124 | 125 | 150 | 200 | 250+ | Total
|  |  | 3 |  | 3 |  | 11 | 7 |  | 14 | 278
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 278 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 1806
| No. of Traps Tested: |  |  |  | 200 | Tested |  | Average Steam Loss per Trap: |  |  |  | 62.2759
| Traps Leaking |  |  |  | 18 | 9% |  | Maximum Steam Loss per Trap: |  |  |  | 307.8
| Traps Blowing Through: |  |  |  | 11 | 5.5% |  | Minimum Steam Loss per Trap: |  |  |  | 36
| Traps Blocked and Flooded: |  |  |  | 19 | 9.5%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 117 | 89 | 8 | 15 | 2 | 47 | 278

## Pharma
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Pharmaceutical Mfg.
DATE OF SURVEY: |  | 2005-03-25
CONTRACTOR: |  | Spirax Sarco
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 172 | 7 | 7 | 6 | 0 |  | 192
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
| 4 |  |  | 5 |  | 32 |  | 7 | 1 | 3 | 46
|  | 50 | 60 | 61 to 100 | 100 | 101-125 | 125 | 150 | 200 | 250+ | Total
|  | 1 | 5 | 1 | 20 | 59 | 0 | 0 |  | 0 | 184
[10 empty] | No Data | 8
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 192 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 70
| No. of Traps Tested: |  |  |  | 135 | Tested |  | Average Steam Loss per Trap: |  |  |  | 6.3636
| Traps Leaking |  |  |  | 11 | 8.148% |  | Maximum Steam Loss per Trap: |  |  |  | 7.2
| Traps Blowing Through: |  |  |  | 0 | 0% |  | Minimum Steam Loss per Trap: |  |  |  | 5.4
| Traps Blocked and Flooded: |  |  |  | 1 | 0.7407%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 110 | 5 | 0 | 10 | 67 | 0 | 192

## Univ.
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | University
DATE OF SURVEY: |  | 2005-08-15
CONTRACTOR: |  | SteamGard
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR |  | Total
|  |  |  | 301 | 15 | 5 | 12 | 0 |  | 333
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
|  |  | 24 | 106 | 128 | 15 | 37 |  | 16 | 0
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  | 2 | 3 | 2 | [6 empty] | 333
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 333 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 877.8
| No. of Traps Tested: |  |  |  | 200 | Tested |  | Average Steam Loss per Trap: |  |  |  | 30.269
| Traps Leaking |  |  |  | 18 | 9% |  | Maximum Steam Loss per Trap: |  |  |  | 46.8
| Traps Blowing Through: |  |  |  | 11 | 5.5% |  | Minimum Steam Loss per Trap: |  |  |  | 5.7
| Traps Blocked and Flooded: |  |  |  | 19 | 9.5%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 117 | 89 | 8 | 15 | 2 | 102 | 333

## Edible Oil
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Edible Oil Mfg
DATE OF SURVEY: |  | na
CONTRACTOR: |  | Spirax Sarco
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 36 | 21 | 2 | 0 | 0 | 5 | 67
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
[6 empty] | 42 |  |  |  | 1
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  | 1 |  |  | 16 | [5 empty] | 60
[10 empty] | No Data | 7
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 67 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 298
| No. of Traps Tested: |  |  |  | 60 | Tested |  | Average Steam Loss per Trap: |  |  |  | 42.5714
| Traps Leaking |  |  |  | 7 | 11.67% |  | Maximum Steam Loss per Trap: |  |  |  | 45
| Traps Blowing Through: |  |  |  | 0 | 0% |  | Minimum Steam Loss per Trap: |  |  |  | 28
| Traps Blocked and Flooded: |  |  |  | 0 | 0%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 33 | 9 | 14 | 4 | 2 | 5 | 67

## Hosp
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Hosp
DATE OF SURVEY: |  | December, 2002
CONTRACTOR: |  | Armstrong
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 388 | 40 | 45 | 296 | 24 | 42 | 835
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
| 230 |  |  | 400 | 83 | 17 |  |  |  | 3
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  | 2 | 29 | 71 | [6 empty] | 835
[10 empty] | No Data | 0
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 835 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 1701
| No. of Traps Tested: |  |  |  | 640 | Tested |  | Average Steam Loss per Trap: |  |  |  | 9.8895
| Traps Leaking |  |  |  | 48 | 7.5% |  | Maximum Steam Loss per Trap: |  |  |  | 99
| Traps Blowing Through: |  |  |  | 124 | 19.38% |  | Minimum Steam Loss per Trap: |  |  |  | 2
| Traps Blocked and Flooded: |  |  |  | 13 | 2.031%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 276 |  | 447 | 56 | 56 |  | 835

## Paper
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Paper Mill
DATE OF SURVEY: |  | May, 2005
CONTRACTOR: |  | Spirax Sarco
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 17 | 137 | 83 |  |  | 4 | 241
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
[9 empty] | 10 | 19
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  |  |  | 87 | 2 |  | 2 | 46 |  | 12 | 178
[10 empty] | No Data | 63
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 241 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 2574
| No. of Traps Tested: |  |  |  | 181 | Tested |  | Average Steam Loss per Trap: |  |  |  | 73.5429
| Traps Leaking |  |  |  | 35 | 19.34% |  | Maximum Steam Loss per Trap: |  |  |  | 201
| Traps Blowing Through: |  |  |  |  | 0% |  | Minimum Steam Loss per Trap: |  |  |  | 70
| Traps Blocked and Flooded: |  |  |  | 33 | 18.23%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 183 | 23 |  | 30 |  | 5 | 241

## Metal
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Metal Mfg
DATE OF SURVEY: |  | Dec., 2003
CONTRACTOR: |  | Armstrong
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 21 | 12 | 1 | 14 |  | 14 | 62
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
|  |  |  | 4 |  | 48
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  |  |  | 8 |  |  |  |  | 2 |  | 62
[10 empty] | No Data | 0
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 62 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 401
| No. of Traps Tested: |  |  |  | 50 | Tested |  | Average Steam Loss per Trap: |  |  |  | 20.05
| Traps Leaking |  |  |  | 10 | 20% |  | Maximum Steam Loss per Trap: |  |  |  | 82
| Traps Blowing Through: |  |  |  | 10 | 20% |  | Minimum Steam Loss per Trap: |  |  |  | 4
| Traps Blocked and Flooded: |  |  |  | 7 | 14%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 11 | 34 |  | 8 |  | 9 | 62

## Confection
STEAM TRAP SURVEY SUMMARY
CUSTOMER NAME: |  | Confectionery
DATE OF SURVEY: |  | November, 2004
CONTRACTOR: |  | Spirax Sarco
TYPE OF TRAP
|  |  |  | F & T | IB | TD | T | OR | Other | Total
|  |  |  | 223 | 7 | 82 | 51 | 0 | 4 | 367
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
[5 empty] | 38 | 126 |  | 11 | 6 | 44 | 15
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  | 20 | 20 | 6 | 4 | 58 | 1 | 1 |  |  | 350
[10 empty] | No Data | 17
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 367 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 1178
| No. of Traps Tested: |  |  |  | 254 | Tested |  | Average Steam Loss per Trap: |  |  |  | 40.6207
| Traps Leaking |  |  |  | 29 | 11.42% |  | Maximum Steam Loss per Trap: |  |  |  | 55
| Traps Blowing Through: |  |  |  |  | 0% |  | Minimum Steam Loss per Trap: |  |  |  | 28
| Traps Blocked and Flooded: |  |  |  | 28 | 11.02%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 143 | 89 |  | 35 | 43 | 57 | 367

## Total
STEAM TRAP SURVEY SUMMARY
TOTAL
CUSTOMER NAME: |  | TOTAL
DATE OF SURVEY:
CONTRACTOR:
TYPE OF TRAP
|  |  |  | F & T | B | TD | T | OR | Other | Total
|  |  |  | 1379 | 256 | 258 | 385 | 25 | 69 | 2372
PRESSURE PSIG
| <5 | 5 | 6 to 9 | 10 | 11 to 14 | 15 | 16 to 19 | 20 | 25 | 30 | 40
| 234 | 0 | 24 | 515 | 249 | 517 | 37 | 28 | 33 | 73 | 61
|  | 50 | 60 | 61 to 99 | 100 | 101 to 124 | 125 | 150 | 200 | 250+ | Total
|  | 26 | 60 | 175 | 45 | 117 | 14 | 54 | 2 | 26 | 2290
[10 empty] | No Data | 82
STATISTICS
[5 empty] | No. of Traps | Defects as | [5 empty] | LB/HR
| Total Trap Population: |  |  |  | 2372 | Percent of |  | Total Steam Loss as Calculated: |  |  |  | 8905.8
| No. of Traps Tested: |  |  |  | 1720 | Tested |  | Average Steam Loss per Trap: |  |  |  | 26.8247
| Traps Leaking |  |  |  | 176 | 10.23% |  | Maximum Steam Loss per Trap: |  |  |  | 307.8
| Traps Blowing Through: |  |  |  | 156 | 9.07% |  | Minimum Steam Loss per Trap: |  |  |  | 2
| Traps Blocked and Flooded: |  |  |  | 120 | 6.977%
APPLICATIONS
|  |  |  | Drip | Radiator | Controlled Process
[5 empty] | Unit Heater | AHU | HX | Coils | Other
|  |  |  | 990 | 338 | 477 | 173 | 172 | 225 | 2375