## Motor Savings
[12 empty] | Operating Hrs.(5) | % Rewind (8)
[11 empty] | 26 through 50 = | 2222 | 22%
[11 empty] | 51 through 100 = | 2651 | 80%
[11 empty] | 101 through 200 = | 2607 | 82%
[11 empty] | 201 through 500 = | 2924 | 82%
[11 empty] | Lifetime = | 15 years
[11 empty] | Load Factor (3) = | 0.65
[11 empty] | Coincident Diversity Factor (6) = | 0.64
[11 empty] | In Service Rate (ISR) (9) = | 0.8
[6 empty] | ODP (4) | TEFC (4)
[6 empty] | 22.41% | 77.59% | [16 empty] | 35%
Rewind Basecase Savings
Measure Description | HORSEPOWER | NEMA Premium ODP MINIMUM EFFICIENCY REQUIREMENTS AS DECIMAL (1) | NEMA Premium TEFC MINIMUM EFFICIENCY REQUIREMENTS AS DECIMAL (1) | Rewind Basecase Efficiency (NEMA Energy Efficient) As Decimal (ODP) (2) | Rewind Basecase Efficiency (NEMA Energy Efficient) As Decimal (TEFC) (2) | GROSS NON-COINCIDENT PEAK DEMAND REDUCTION PER Motor (ODP) (kW) (3) | GROSS NON-COINCIDENT PEAK DEMAND REDUCTION PER Motor (TEFC) (kW) (3) | Weighted Gross Non-Coincident Peak Demand Reduction per Motor (kW) (4) | GROSS ANNUAL ENERGY SAVINGS PER MOTOR (ODP) (KwH) (5) | GROSS ANNUAL ENERGY SAVINGS PER MOTOR (TEFC) (KwH) (5) | GROSS ANNUAL ENERGY SAVINGS PER MOTOR (kWh) (5) | COINCIDENT PEAK DEMAND REDUCTION PER Motor (ODP) (kW) (6) | COINCIDENT PEAK DEMAND REDUCTION PER Motor (TEFC) (kW) (6) | GROSS COINCIDENT PEAK DEMAND REDUCTION PER MOTOR (kW) (6) | GROSS ANNUAL ENERGY SAVINGS PER HP (kWh) | GROSS COINCIDENT PEAK DEMAND REDUCTION PER HP (kW) | GROSS ANNUAL ENERGY SAVINGS PER HP with ISR (kWh), | GROSS COINCIDENT PEAK DEMAND REDUCTION PER HP with ISR (kW) | Rewind Basecase Cost per HP | NEMA Premium Efficiency Motor Cost per HP | IMC (Incremental Measure Cost) Rewind Basecase (7)
Motor 50 HP - NEMA Premium Efficiency | 50 | 0.943 | 0.943 | 0.93 | 0.92943 | 0.079067 | 0.0015579 | 0.018926 | 175.69 | 3.46 | 42.05 | 0.0506 | 0.001 | 0.0121 | 0.841 | 0.000242 | 0.6728 | 0.0001936 | 33.0219 | 76.5367 | 43.5147 | 0.013 | 0.013573
Motor 60 HP - NEMA Premium Efficiency | 60 | 0.948 | 0.948 | 0.936 | 0.93543 | 0.31477 | 0.33001 | 0.3266 | 834.45 | 874.86 | 865.81 | 0.2015 | 0.2112 | 0.209 | 14.4302 | 0.0034833 | 11.5441 | 0.0027867 | 31.6347 | 86.0452 | 54.4105 | 0.012 | 0.012573
Motor 75 HP - NEMA Premium Efficiency | 75 | 0.948 | 0.951 | 0.939 | 0.93914 | 0.29415 | 0.38648 | 0.36579 | 779.8 | 1024.56 | 969.71 | 0.1883 | 0.2473 | 0.2341 | 12.9295 | 0.0031213 | 10.3436 | 0.0024971 | 29.5719 | 81.1293 | 51.5573 | 0.009 | 0.011864
Motor 100 HP - NEMA Premium Efficiency | 100 | 0.952 | 0.952 | 0.941 | 0.94349 | 0.47633 | 0.36755 | 0.39192 | 1262.75 | 974.37 | 1038.99 | 0.3049 | 0.2352 | 0.2508 | 10.3899 | 0.002508 | 8.3119 | 0.0020064 | 27.225 | 74.0105 | 46.7855 | 0.011 | 0.0085103
Motor 125 HP - NEMA Premium Efficiency | 125 | 0.952 | 0.953 | 0.943 | 0.94435 | 0.49828 | 0.47772 | 0.48233 | 1299.01 | 1245.42 | 1257.42 | 0.3189 | 0.3057 | 0.3087 | 10.0594 | 0.0024696 | 8.0475 | 0.0019757 | 25.6004 | 71.831 | 46.2306 | 0.009 | 0.0086501
Motor 150 HP - NEMA Premium Efficiency | 150 | 0.956 | 0.957 | 0.948 | 0.94952 | 0.52648 | 0.49082 | 0.49881 | 1372.53 | 1279.56 | 1300.39 | 0.3369 | 0.3141 | 0.3192 | 8.6693 | 0.002128 | 6.9354 | 0.0017024 | 24.725 | 68.8227 | 44.0977 | 0.008 | 0.0074779
Motor 200 HP - NEMA Premium Efficiency | 200 | 0.956 | 0.961 | 0.948 | 0.95 | 0.70197 | 0.95817 | 0.90076 | 1830.04 | 2497.94 | 2348.28 | 0.4493 | 0.6132 | 0.5765 | 11.7414 | 0.0028825 | 9.3931 | 0.002306 | 23.2474 | 69.8123 | 46.5649 | 0.008 | 0.011
Motor 250 HP - NEMA Premium Efficiency | 250 | 0.958 | 0.961 | 0.947 | 0.95038 | 1.2053 | 1.1556 | 1.1667 | 3524.2 | 3379.03 | 3411.56 | 0.7714 | 0.7396 | 0.7467 | 13.6462 | 0.0029868 | 10.917 | 0.0023894 | 22.6965 | 72.6614 | 49.9649 | 0.011 | 0.010618
Motor 300 HP - NEMA Premium Efficiency | 300 | 0.958 | 0.962 | 0.954 | 0.95335 | 0.52208 | 1.1251 | 0.98996 | 1526.55 | 3289.73 | 2894.64 | 0.3341 | 0.7201 | 0.6336 | 9.6488 | 0.002112 | 7.719 | 0.0016896 | 21.9344 | 79.754 | 57.8196 | 0.004 | 0.0086501
Motor 350 HP - NEMA Premium Efficiency | 350 | 0.958 | 0.962 | 0.954 | 0.95335 | 0.60909 | 1.3126 | 1.155 | 1780.97 | 3838.02 | 3377.08 | 0.3898 | 0.8401 | 0.7392 | 9.6488 | 0.002112 | 7.719 | 0.0016896 | 21.0898 | 92.0461 | 70.9563 | 0.004 | 0.0086501
Motor 400 HP - NEMA Premium Efficiency | 400 | 0.958 | 0.962 | 0.954 | 0.954 | 0.6961 | 1.3864 | 1.2317 | 2035.4 | 4053.87 | 3601.57 | 0.4455 | 0.8873 | 0.7883 | 9.0039 | 0.0019707 | 7.2031 | 0.0015766 | 20.1518 | 99.7054 | 79.5536 | 0.004 | 0.008
Motor 450 HP - NEMA Premium Efficiency | 450 | 0.962 | 0.962 | 0.958 | 0.954 | 0.7766 | 1.5597 | 1.3842 | 2270.78 | 4560.6 | 4047.5 | 0.497 | 0.9982 | 0.8859 | 8.9944 | 0.0019687 | 7.1956 | 0.0015749 | 20.1518 | 99.7054 | 79.5536 | 0.004 | 0.008
Motor 500 HP - NEMA Premium Efficiency | 500 | 0.962 | 0.962 | 0.958 | 0.958 | 0.86289 | 0.86289 | 0.86289 | 2523.09 | 2523.09 | 2523.09 | 0.5522 | 0.5522 | 0.5522 | 5.0462 | 0.0011044 | 4.0369 | 0.00088352 | 20.1518 | 99.7054 | 79.5536 | 0.004 | 0.004
1) Values from 'Measure Case NEMA Prem. Eff' tab
2) Values from 'Base Case NEMA Energy Eff.' tab
3) Non Coincident Demand is 0.746 * hp * 0.65 load factor * (1/ NEME Energy Eff - 1/ NEMA Prem Eff)
The assumed load factor is 65 percent based on the CPUC Energy Division Phase 2 Workpaper Review and Measure Disposition (December 9, 2011)
4) Motor type weighting factors from 'ODP and TEFC Program Breakdown' tab
5) Operating hours from 'Operating Hours' tab, based on Attachment B of the CPUC Energy Division Phase 2 Workpaper Review and Measure Disposition (December 9, 2011)
6) Coincident Peak Demand is non-coincident peak demand times coincident diversity factor of 0.64. Per
the CPUC Energy Division Phase 2 Workpaper Review and Measure Disposition (December 9, 2011)
7) The IMC for Rewind measures is equal to the cost difference between a new NEMA Premium Efficiency motor and the cost to rewind an existing motor
8) Values from Section 3.1 of the CPUC Energy Division Phase 2 Workpaper Review and Measure Disposition (December 9, 2011). The % rewind of motors above 200 HP is assumed to be similar to that of a 200 HP motor.
9) An in service rate of 0.8 was applied to the calculated savings per the CPUC Energy Division Phase 2
Workpaper Review and Measure Disposition (December 9, 2011)

## Cost Data
| 3600 RPM |  |  |  | 1800 RPM |  |  |  | 1200 RPM
| ODP |  | TEFC |  | ODP |  | TEFC |  | ODP |  | TEFC
HP | Premium Efficient | Stator Rewind | Premium Efficient | Stator Rewind | Premium Efficient | Stator Rewind | Premium Efficient | Stator Rewind | Premium Efficient | Stator Rewind | Premium Efficient | Stator Rewind | Weighted Premium Efficient | Weighted Stator Rewind | Weighted Premium Efficient / HP | Weighted Stator Rewind /HP | IMC /HP
50 | 2956 | 1497 | 3980 | 1796 | 3084 | 1360 | 3347 | 1632 | 4730 | 1657 | 6293 | 1988 | 3826.8336 | 1651.0966 | 76.5367 | 33.0219 | 43.5147
60 | 3741 | 1724 | 5591 | 2069 | 3884 | 1566 | 4816 | 1879 | 5827 | 1894 | 7639 | 2273 | 5162.7123 | 1898.0829 | 86.0452 | 31.6347 | 54.4105
75 | 4906 | 2009 | 6504 | 2411 | 4767 | 1828 | 5632 | 2194 | 7058 | 2221 | 8898 | 2665 | 6084.6954 | 2217.8947 | 81.1293 | 29.5719 | 51.5573
100 | 5245 | 2457 | 8316 | 2948 | 5546 | 2233 | 6994 | 2680 | 7769 | 2771 | 10737 | 3325 | 7401.0497 | 2722.5017 | 74.0105 | 27.225 | 46.7855
125 | 6582 | 2900 | 10279 | 3480 | 6803 | 2637 | 8658 | 3164 | 8391 | 3208 | 12631 | 3850 | 8978.8705 | 3200.0504 | 71.831 | 25.6004 | 46.2306
150 | 8119 | 3363 | 12094 | 4036 | 7557 | 3057 | 9959 | 3668 | 9881 | 3714 | 14467 | 4457 | 10323.4056 | 3708.7567 | 68.8227 | 24.725 | 44.0977
200 | 9201 | 4245 | 14495 | 5094 | 9443 | 3858 | 14351 | 4630 | 12989 | 4547 | 17849 | 5456 | 13962.4589 | 4649.4729 | 69.8123 | 23.2474 | 46.5649
250 |  |  | 22631 | 6102 | 10590 | 4621 | 18896 | 5545 | 16716 | 5327 | 27247 | 6392 | 18165.3523 | 5674.1239 | 72.6614 | 22.6965 | 49.9649
300 |  |  | 33075 | 7180 | 16149 | 5438 | 26044 | 6526 | 18683 | 6238 | 27517 | 7486 | 23926.207 | 6580.3203 | 79.754 | 21.9344 | 57.8196
350 |  |  | 39700 | 8029 |  |  | 31252 | 7298 |  |  |  |  | 32216.1254 | 7381.4251 | 92.0461 | 21.0898 | 70.9563
400 |  |  | 46466 | 8765 |  |  | 39034 | 7970 |  |  |  |  | 39882.1747 | 8060.7291 | 99.7054 | 20.1518 | 79.5536
450 | * No data available from Vaughen's Motor Price Guide for motors > 400 HP. Cost per HP is assumed to be similar to a 400 HP motor | [11 empty] | 39882.1747 | 8060.7291 | 99.7054 | 20.1518 | 79.5536
500 | * No data available from Vaughen's Motor Price Guide for motors > 400 HP. Cost per HP is assumed to be similar to a 400 HP motor | [11 empty] | 39882.1747 | 8060.7291 | 99.7054 | 20.1518 | 79.5536
* Costs from Vaughen's Motor and Pump Repair Price Guide, 2016 Edition
Enclosure | RPM | Total Motors | Percentage of Total
ODP | 1200 | 322 | 7.37%
| 1800 | 622 | 14.24%
| 3600 | 35 | 0.8011%
| ODP Total | 979 | 22.41%
TEFC | 1200 | 551 | 12.61%
| 1800 | 2515 | 57.56%
| 3600 | 324 | 7.416%
| TEFC Total | 3390 | 77.59%
Total |  | 4369 | 100%

## Measure Case NEMA Prem. Eff
NEMA Premium Efficiency - Minimum Nominal Full Load Efficiency (1)
| Open Motors |  |  |  | Closed Motors
| 6 pole | 4 pole | 2 pole | Weighted Efficiency | 6 pole | 4 pole | 2 pole | Weighted Efficiency | Enclosure | RPM | Total Motors | Percentage of Total
hp | 1200 | 1800 | 3600 |  | 1200 | 1800 | 3600 |  | ODP | 1200 | 322 | 7.37%
50 | 94.1 | 94.5 | 93 | 94.3 | 94.1 | 94.5 | 93 | 94.3 |  | 1800 | 622 | 14.24%
60 | 94.5 | 95 | 93.6 | 94.8 | 94.5 | 95 | 93.6 | 94.8 |  | 3600 | 35 | 0.8011%
75 | 94.5 | 95 | 93.6 | 94.8 | 94.5 | 95.4 | 93.6 | 95.1 |  | ODP Total | 979 | 22.41%
100 | 95 | 95.4 | 93.6 | 95.2 | 95 | 95.4 | 94.1 | 95.2 | TEFC | 1200 | 551 | 12.61%
125 | 95 | 95.4 | 94.1 | 95.2 | 95 | 95.4 | 95 | 95.3 |  | 1800 | 2515 | 57.56%
150 | 95.4 | 95.8 | 94.1 | 95.6 | 95.8 | 95.8 | 95 | 95.7 |  | 3600 | 324 | 7.416%
200 | 95.4 | 95.8 | 95 | 95.6 | 95.8 | 96.2 | 95.4 | 96.1 |  | TEFC Total | 3390 | 77.59%
250 | 95.8 | 95.8 | 95 | 95.8 | 95.8 | 96.2 | 95.8 | 96.1 | Total |  | 4369 | 100%
300 |  | 95.8 | 95.4 | 95.8 |  | 96.2 | 95.8 | 96.2
350 |  | 95.8 | 95.4 | 95.8 |  | 96.2 | 95.8 | 96.2
400 |  | 95.8 | 95.8 | 95.8 |  | 96.2 | 95.8 | 96.2
450 |  | 96.2 | 96.2 | 96.2 |  | 96.2 | 95.8 | 96.2
500 |  | 96.2 | 96.2 | 96.2 |  | 96.2 | 95.8 | 96.2
(1) NEMA Standards Publication MG 1- 2011, Table 12-12 Efficiency Levels for NEMA Premium Motors 600 volts or less.

## Base Case NEMA Energy Eff.
NEMA Energy Efficient - Minimum Nominal Full Load Efficiency (1)
| Open Motors |  |  |  | Closed Motors
| 6 pole | 4 pole | 2 pole | Weighted Efficiency | 6 pole | 4 pole | 2 pole | Weighted Efficiency | Enclosure | RPM | Total Motors | Percentage of Total
hp | 1200 | 1800 | 3600 |  | 1200 | 1800 | 3600 |  | ODP | 1200 | 322 | 7.37%
50 | 93 | 93 | 92.4 | 93 | 93 | 93 | 92.4 | 92.9427 |  | 1800 | 622 | 14.24%
60 | 93.6 | 93.6 | 93 | 93.6 | 93.6 | 93.6 | 93 | 93.5427 |  | 3600 | 35 | 0.8011%
75 | 93.6 | 94.1 | 93 | 93.9 | 93.6 | 94.1 | 93 | 93.9136 |  | ODP Total | 979 | 22.41%
100 | 94.1 | 94.1 | 93 | 94.1 | 94.1 | 94.5 | 93.6 | 94.349 | TEFC | 1200 | 551 | 12.61%
125 | 94.1 | 94.5 | 93.6 | 94.3 | 94.1 | 94.5 | 94.5 | 94.435 |  | 1800 | 2515 | 57.56%
150 | 94.5 | 95 | 93.6 | 94.8 | 95 | 95 | 94.5 | 94.9522 |  | 3600 | 324 | 7.416%
200 | 94.5 | 95 | 94.5 | 94.8 | 95 | 95 | 95 | 95 |  | TEFC Total | 3390 | 77.59%
250 | 95.4 | 94.4 | 94.5 | 94.7 | 95 | 95 | 95.4 | 95.0382 | Total |  | 4369 | 100%
300 | 95.4 | 95.4 | 95 | 95.4 | 95 | 95.4 | 95.4 | 95.335
350 | 95.4 | 95.4 | 95 | 95.4 | 95 | 95.4 | 95.4 | 95.335
400 |  | 95.4 | 95.4 | 95.4 |  | 95.4 | 95.4 | 95.4
450 |  | 95.8 | 95.8 | 95.8 |  | 95.4 | 95.4 | 95.4
500 |  | 95.8 | 95.8 | 95.8 |  | 95.8 | 95.4 | 95.8
(1) NEMA Standards Publication MG 1- 2011, Table 12-11 Efficiency Levels for NEMA Energy Efficient Motors 600 volts or less.

## Operating Hours
Full-Load Motor Runtimes for Industrial Motors (2) |  |  | Full-Load Motor Runtimes for Commercial Motors (1) |  |  |  | Full-Load Motor Runtimes for Agricultural Motors (1)
Motor hp | All SIC Numbers |  | Motor hp | Runtime | Part Load Estimate | Equivalent Full Load Hours | Motor hp | Runtime
1 to 5 | 2745 |  | ≤15 hp | 2076 | 0.36 | 747 | All Sizes | 1750
6 to 15 | 3391 |  | >15 hp | 2820 | 0.36 | 1015
16 to 20 | 3391
21 to 50 | 4067
51 to 100 | 5329
101 to 200 | 5200
201 to 500 | 6132
Relative Energy Use By Sector (1)
Sector | %Energy Use By Sector | % Energy Used By Motors Per Sector | % of Motor Energy Usage By Sector
Commercial | 69% | 22% | 43%
Industrial | 21% | 57% | 34%
Agriculture | 10% | 80% | 23%
Hours Weighted by Sector
Motor hp | Weighted Hours
1 to 5 | 1657
6 to 15 | 1877
16 to 20 | 1992
21 to 25 | 2222
26 to 50 | 2222
51 to 100 | 2651
101 to 200 | 2607
201 to 500 | 2924
(1) Attachment B of the CPUC Energy Division Phase 2 Workpaper Review and Measure Disposition (December 9, 2011)
(2) “United States Industrial Electric Motor Systems Market Opportunities Assessment,” Prepared by Xenergy Inc. for U.S. DOE, Burlington, MA, Dec.2002, Table 1-15, page 42.

## ODP and TEFC Program Breakdown
Average of Motors Types (1) | [5 empty] | Percentage of Motors (1)
HP | ODP Motors | TEFC Motors | Total Motors | Average of ODP Motors per hp | Average of TEFC Motors per hp | Enclosure | RPM | Total Motors | Percentage of Total
1 | 15 | 412 | 427 | 4% | 96% | ODP | 1200 | 322 | 7.37%
1.5 | 31 | 138 | 169 | 18% | 82% |  | 1800 | 622 | 14.24%
2 | 34 | 183 | 217 | 16% | 84% |  | 3600 | 35 | 0.8011%
3 | 48 | 217 | 265 | 18% | 82% |  | ODP Total | 979 | 22.41%
5 | 111 | 421 | 532 | 21% | 79% | TEFC | 1200 | 551 | 12.61%
7.5 | 96 | 321 | 417 | 23% | 77% |  | 1800 | 2515 | 57.56%
10 | 65 | 410 | 475 | 14% | 86% |  | 3600 | 324 | 7.416%
15 | 113 | 210 | 323 | 35% | 65% |  | TEFC Total | 3390 | 77.59%
20 | 52 | 295 | 347 | 15% | 85% | Total |  | 4369 | 100%
25 | 67 | 126 | 193 | 35% | 65%
30 | 22 | 163 | 185 | 12% | 88%
40 | 189 | 103 | 292 | 65% | 35%
50 | 79 | 75 | 154 | 51% | 49%
60 | 9 | 60 | 69 | 13% | 87%
75 | 13 | 131 | 144 | 9% | 91%
100 | 17 | 71 | 88 | 19% | 81%
125 | 6 | 12 | 18 | 33% | 67%
150 | 6 | 18 | 24 | 25% | 75%
200 | 3 | 19 | 22 | 14% | 86%
250 | 2 | 3 | 5 | 40% | 60%
300 | 1 | 1 | 2 | 50% | 50%
400 |  | 1 | 1 | 0% | 100%
Total | 979 | 3390 | 4369 | 22% | 78%
(1) Based on 2010 PG&E Upstream Motors Paid Applications