Work Paper PGECOREF124

Advanced Refrigeration Control Walk-In

Revision # 0

Pacific Gas & Electric Company

Customer Energy Solutions

Advanced Refrigeration Control for Walk-In Cooler and Walk-In Freezer

Measure Codes RC117, RC118

January 15, 2014

# At-A-Glance Summary

| Applicable Measure Codes: | RC117, RC118 |
| --- | --- |
| Measure Description: | This measure installs advanced controls on refrigeration systems for walk-in coolers and freezers. The measure must continuously monitor the following data: evaporator coil temperature, space temperature, evaporator fan use, defrost element use, and compressor use. The controller must optimize operation of the evaporator fans, defrosting system and compressors |
| Energy Impact Common Units: | Cap-Tons |
| Base Case Description: | Refrigeration systems for walk-in coolers and freezers without advanced control. |
| Base Case Energy Consumption: | Depends on climate zone and vintage. |
| Measure Energy Consumption: | Depends on climate zone and vintage. |
| Energy Savings (Base Case – Measure) | Depends on climate zone. |
| Costs Common Units: | Per controller |
| Base Case Equipment Cost ($/unit): | There is no advanced controller for the refrigeration system. $0.0 |
| Measure Equipment Cost ($/unit): | Source: cost data obtained from various pilot studies $2,190 |
| Measure Incremental Cost ($/unit): | Source: cost data obtained from various pilot studies $2,190, includes equipment and labor |
| Effective Useful Life (years): | Source: DEER 2008, 1Oct08: D03-210 16 years |
| Program Type: | Retrofit Add-On (REA) |
| Net-to-Gross (NTG) Ratio: | Source: DEER 2011, 16May2012 All-Default<=2yrs: 0.7 |
| Important Comments: | Energy savings credit can only be taken if the existing evaporator fans operate continuously at constant volume, except during defrosting; existing defrosting’s controlled by timer. |

# At-A-Glance Measure List

|  |  |  |  |  |  |  | 1st Baseline |  |  |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Code | Measure Description | Measure Application Type | Building Type | Building Vintage | Climate Zone | Unit Definition | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | (EUL) LIFE CYCLE | Base Case* Cost ($) | Measure Cost* ($) | Labor Cost* ($/Controller) | IMC Incremental Measure Cost* ($/Controller) | KW Peak Electric Demand Reduction | KWh Electric Savings | THM Gas Savings | LIFE CYCLE | Base Case Cost ($/unit) | Measure Cost ($/unit) | Labor Cost ($/unit) | IMC Incremental Measure Cost ($/unit) | GRR_ kW | GRR_ kWh | GRR_ therm | NTG | Implementation Method [UP, DOWN, DI] | ISR |
| RC117 | Advanced Refrigeration Control Refrigerator/Cooler, PGE | ROB | GRO | EX | Z01 | CAP-TONS | 0 | 8,380 | 0 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |
| RC117 | Advanced Refrigeration Control Refrigerator/Cooler, PGE | ROB | GRO | EX | Z02 | CAP-TONS | 0 | 8,351 | 0 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |
| RC117 | Advanced Refrigeration Control Refrigerator/Cooler, PGE | ROB | GRO | EX | Z03 | CAP-TONS | 0 | 8,333 | 0 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |
| RC118 | Advanced Refrigeration Control Freezer, PGE | ROB | GRO | EX | Z01 | CAP-TONS | 0 | 8,667 | 14 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |
| RC118 | Advanced Refrigeration Control Freezer, PGE | ROB | GRO | EX | Z02 | CAP-TONS | 0 | 8,744 | 10 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |
| RC118 | Advanced Refrigeration Control Freezer, PGE | ROB | GRO | EX | Z03 | CAP-TONS | 0 | 8,687 | 14 | 16 | $0.00 | $2,190 | $0.0 | $2,190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0.7 | DOWN | 1 |

*Cost per advanced refrigeration controller.

# Work Paper Approvals

The following Manager(s) approved this work paper through the PG&E Electronic Data Routing System under Routing Requisition # 2013-97640

Grant Brohard Manager, Technical Product Support

Carolyn Weiner Manager, CES Core Products

# Document Revision History

| Revision # | Date | Section by Section Description of Revisions | Author (Company) |
| --- | --- | --- | --- |
| Revision 0 | 01/15/2014 | Original Workpaper | Yin Yin Wu, PE (BASE Energy, Inc) Jim Wyatt PG&E |

# Table of Contents

At-A-Glance Summary	i

At-A-Glance Measure List	ii

Work Paper Approvals	iii

Document Revision History	iv

Table of Contents	v

Section 1. General Measure & Baseline Data	1

1.1 Product Measure Description & Background	1

1.2 Product Technical Description	2

1.3 Measure Application Type	3

1.4 Product Base Case and Measure Case Data	3

1.4.1 DEER Base Case and Measure Case Information	3

1.4.2 Codes & Standards Requirements Base Case and Measure Information	4

1.4.3  EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	4

1.4.4  Assumptions and Calculations from other sources – Base and Measure Cases	5

1.4.5  Time-of-Use Adjustment Factor	5

1.5  Summary of Inputs for Savings Calculations	6

Section 2. Calculation Methods	7

2.1 Electric Energy Savings Estimation Methodologies	7

2.2. Demand Reduction Estimation Methodologies	9

2.3. Gas Energy Savings Estimation Methodologies	9

Section 3. Load Shapes	10

Section 4. Base Case & Measure Costs	11

4.1 Base Case(s) Costs	11

4.2 Measure Case Costs	11

4.3 Incremental & Full Measure Costs	11

References	12

Attachments	12

# Section 1. General Measure & Baseline Data

## 1.1 Product Measure Description & Background

Catalog Description:

Advanced Refrigeration Control technology monitors operating conditions of major components of a refrigeration system and adjusts the system parameters driven by a real time expert system.  The control algorithm optimizes the system performance by adapting to actual changing conditions that result in: 1) decreasing compressor cycle 2) decreasing defrost cycle, 3) decreasing evaporator fan run cycle, and 4) decreasing temperature & humidity fluctuations. The main benefits are improved system efficiency, stable humidity & temperature and substantial energy savings.  This measure incents customers for installing expert system controllers to walk in coolers and freezers at commercial retail facilities and applies to both low temperature (“freezer” – below 32F) and medium temperature (“cooler” – above 32F).

Requirements:

Table 1 Measure Names

| Measure Code | Measure name |
| --- | --- |
| RC117 | ADV REFRIGERATION CNTRL MED‐TEMP |
| RC118 | ADV REFRIGERATION CNTRL LOW‐TEMP |

This measure applies to non-residential buildings that utilize a walk-in cooler or a walk-in freezer. The measure is applicable to any commercial retail facility, including (but not limited to) supermarkets, grocery stores, hotels, restaurants and convenience stores. The facility must install a programmable logic controller to continuously monitor and control various refrigeration components to achieve desired space conditions. Details of requirements are outlined below:

- The installed advanced refrigeration control must include a programmable logic controller that meets the following requirements:

  - The advanced controller will override control of the compressors, evaporator fans, defrosting, and setpoint temperature,

  - sense the evaporator coil temperature and space temperature, and

  - continuously monitor these temperatures and evaporator fan, defrosting and compressor use.

- Requirements of the control of the evaporator fans:

  - The evaporator fans are controlled by cycling fans on/off.

  - The advanced control can delay the evaporator fans operation. Once the space temperature setpoint is reached, the compressors may be turned off but the evaporator fans can stay on as long as cooling can be extracted from the cooling coil.

  - The minimum duty cycle is 0.1 (i.e. 6 minutes run time per hour if no load).

  - The evaporator fans are turned off during defrosting

- Requirements of the control of defrosting system:

  - Defrosting is controlled based on demand,

  - initiated based on coil temperature/demand, and

  - terminated based on temperature.

- Requirements of the control of compressors:

  - The controller has the option to define the differential temperature, which is the difference between the space temperature setpoint and the temperature that enables the refrigeration cycle.

  - The compressor is enabled when the space temperature increases and reaches setpoint plus differential.

- This measure cannot be used in conjunction with either evaporator fan control or defrost by demand control.

- Energy savings credit can only be taken if the existing evaporator fans operate continuously at constant volume, except during defrosting; existing defrosting’s controlled by timer.

- The walk-in freezer setpoint is under 32 oF, and the walk-in cooler setpoint is above 32 oF.

- The advanced refrigeration control must be installed by an authorized product representative, where the installer can verify that the advanced control is compatible with the refrigeration system so that they do not degrade system performance.

- Must install an advanced controller on refrigeration system of an existing walk-in cooler or freezer to decrease energy consumption by optimized control.

Market Applicability:

This measure applies to walk-in storage for both medium temperature (“cooler” – above 32F) and low temperature (“freezer” – below 32F) refrigeration systems. Calculations for both low and medium temperature walk-in freezers and coolers are carried out for all California climate zones.

## 1.2 Product Technical Description

The advanced refrigeration controller is a programmable logic controller that optimizes the refrigeration operation based on real-time monitored data. The advanced controller continuously monitors the following data:

- Evaporator coil temperature,

- Space temperature,

- Evaporator fan use,

- Defrost element use, and

- Compressor use.

The controller optimizes operation of the evaporator fans, defrosting system and compressors. Detailed discussions of the optimized operation are listed below.

- The controller cycles evaporator fans on/off based on cooling demand instead of running the fans continuously. Cycling the fan reduces the evaporator fans’ operation, resulting in electrical energy savings.

- The controller controls defrosting based on demand instead of timer control. The defrosting system is activated by demand and it is terminated based on temperature. This optimized control will reduce the defrosting operation, resulting in less heat gain to the space.

- The reduced evaporator fans operation and defrost time will reduce the heat gain to the space, resulting in reduced compressor cycling.

- The real time monitoring system will result in a tighter control of space temperature, thus preventing over cooling the space. This optimization will reduce the compressor operation.

Installing the advanced refrigeration controller will reduce operations of the evaporator fans, defrosting and compressors, resulting in electrical energy savings.

## 1.3 Measure Application Type

The Base Case of this work paper is considered to be the refrigeration system without advanced control for coolers and freezers. The Measure Case is considered to be adding the advanced control on the existing refrigeration system. Therefore, the measure application type is considered to be retrofit add-on.

Because of PG&E data systems limitations, we use Replace On Burnout (ROB) measure application type in the savings spreadsheet. Both measure application types yield a single baseline with identical results.

## 1.4 Product Base Case and Measure Case Data

## 1.4.1 DEER Base Case and Measure Case Information

The Database for Energy Efficient Resources (DEER) 2014 does not address advanced refrigeration control for walk-in coolers and walk-in freezers.

DEER does not address installing advanced controllers on refrigerated walk-in coolers and freezers for data monitoring, evaporator fan control, defrosting control and compressor control.  DEER does contain measure D03-210 which addresses evaporator fan control of Walk-in coolers and Freezers. This measure differs from the advanced refrigeration controller which is the subject of this work paper. No other DEER measures address advanced refrigeration controllers.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | Yes |
| Deviation from DEER | DEER does not include the measure of installing advanced refrigeration controllers |
| DEER Version | DEER 05, DEER 2014 |
| DEER Run ID and Measure Name (Sample) | D03-210 – Evaporator Fan Control |

Table 3 DEER USE and TECHNOLOGY TABLE

The Effective Useful Life is an estimate of the median number of years that the measures installed under the program are still in place and operable.

DEER11 documentation provides EUL and RUL information to be used for the 13-14 program cycle on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value.

To obtain the EUL value the DEER08 documentation, EUL_Summary_10-1-08.xls, was consulted. Since the Advanced Refrigeration Control measure is not included in the EUL summary table, the EUL of the Evaporator Fan Controller for Walk-In Coolers measure is used for this work paper. Table 4 below identifies the value/methodology used for the measures in this work paper.

Table 4 DEER EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- |
| Non-Residential | Refrigeration | Advanced Refrigeration Controls* | 16 | 5 |

* EUL of the Evaporator Fan Controller for Walk-In Coolers measure is used for this work paper.

The NTG value was obtained from the “DEER2011 Update Net-To-Gross table” on the DEER. The relevant NTGR for this measure is shown in Table 5 below.

Table 5:  Net-to-Gross Ratios [1]

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID* | NTG* |
| --- | --- | --- | --- | --- | --- |
| All-Default<=2yrs | All other EEMs with no evaluated NTGR; new technology in program for 2 or fewer years | All | Any | All | 0.7 |

*Denotes that the column is taken from the DEER NTG Table.

## 1.4.2 Codes & Standards Requirements Base Case and Measure Information

Title 20: These measures do not fall under Title 20 of the California Energy Regulations.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Federal Standards: These measures do not fall under Federal DOE or EPA Energy Regulations.

## 1.4.3  EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

- According to the California Commercial End-Use Survey, refrigeration is the second highest end use of electricity in commercial buildings, using 15% of total commercial building electric consumption in the PG&E territory, emphasizing the significant potential for energy-efficiency measures involving various types of refrigeration [2].

The measure of installing advanced controllers in walk-in coolers and freezers is also evaluated in the following studies:

- Adaptive Refrigerator and Freezer Controls for Commercial Applications, San Diego Gas and Electric Company, Emerging Technologies Program, Project ID ET11SDEGEC, November 23, 2012.

- Evaluation of an Internet-Based Refrigeration Monitoring and Control System, Southern California Edison, Design & Engineering services, December 4, 2009.

- Adaptive Refrigeration controls Study– Commercial & Industrial Systems, National Energy & Conservation, 2010 and 2011.

- Technical Analysis Study & Verification Report for Refrigeration Controls, Sponsored by EnergyTrust of Oregon, Inc., August 23, 2011.

## 1.4.4  Assumptions and Calculations from other sources – Base and Measure Cases

There are no further data or calculations provided for the support of the measures in this work paper.

## 1.4.5  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0.

Table 6 TOU Summary Table

| Measure | % |
| --- | --- |
| Freezer Advanced Refrigeration Controls | 0 |
| Cooler Advanced Refrigeration Controls | 0 |

## 1.5  Summary of Inputs for Savings Calculations

The following table provides references to sections that document the inputs for calculation:

| Input Variable | Variations | Base Case 1 Average Value | Base Case 2 Average Value | Measure Case Average Value | Reference Section |
| --- | --- | --- | --- | --- | --- |
| Electric Savings | CZ, BT, BV | various | NA | various | Section 2.1 |
| Gas Savings | CZ, BT, BV, IE | various | NA | various | Section 2.3 |
| Hours of operation | CZ, BT, BV | 8760 | NA | 8760 | Section 2 |
| Full Cost | ER, ROB, NC | $0 | NA | $2190 | Section 4 |
| Incremental Cost | ER, ROB, NC | $0 | NA | $2190 | Section 4 |
| EUL /RUL | ER, ROB, NC | NA | NA | 16 | Section 1.4.1 |
| NTG | One | NA | NA | 0.7 | Section 1.4.1 |
| ISR | Applies -- No | NA | NA | 1.0 | NA |
| TOU Factor | A/C projects only | NA | NA | NA | Section 1.4.5 |

# Section 2. Calculation Methods

## 2.1 Electric Energy Savings Estimation Methodologies

The following assumptions were made for the calculations of this work paper:

- The building simulation models were generated for a Grocery Store with multiplex-compressor systems for the refrigeration walk-in coolers and freezers. Single-compressor systems are less efficient than multiplex-compressor systems. According to the DEER Report [3], single-compressor systems were typically designed prior to 1980. To be conservative, it is assumed that the generated energy savings for this work paper will also be applied to walk-in cooler and freezer with single-compressor systems. The refrigeration compressors and condensers are considered to be outdoor and not included as internal load in the building simulation.

- This work paper is applied to walk-in coolers and freezers located inside a space which has space cooling (and space heating). The unit energy savings is represented per ton of rated capacity of the walk-in cooler and freezer. The building simulation models were generated for a Grocery Store. Since the heat gain of a cooler/freezer mainly depends on the temperature maintained for the cooler/freezer and the surrounding space temperature, it is assumed that the building types would not have significant impact on the energy savings. Thus, the resulting savings for Grocery Store is applied to all other building types considered in this work paper with weighted building vintages. The assumption has been verified through sensitivity analysis. Refer to the end of this section for Sensitivity Study on other building types.

The energy savings for this work paper is based on installing controllers on the existing refrigeration system on medium temperature walk-in coolers and low temperature walk-in freezers. The walk-in coolers and freezers are applicable to, but not limited to, grocery stores. A set of sensitivity analyses for two additional building types (Fast Food Restaurant and Small Retail) at two extreme weather conditions for one Building Vintage are performed. Refer to the end of this section for discussion.

The baseline of this work paper is the refrigeration system with no advanced control. Installing advanced control on the refrigeration system will reduce the evaporator fans’ operating hours, optimize defrost control, and stabilize space temperature, resulting in savings on the refrigeration cooling load.

The measures are weather sensitive and the building energy simulation tool eQuest was used to determine the annual impacts of different climate zones. The built-in, DEER building prototypes of grocery store were used for the simulations. The DEER building prototypes consider multiplex-compressor systems as the refrigeration type. The baseline models consider no control on the evaporator fans, defrosting by timer control and no optimized control of the compressors. Inputs of the DEER building prototypes have been reviewed and some components are modified in the baseline models. Details of the modified baseline components are discussed below:

- The baseline evaporator fans operate at constant volume continuously.

- The design evaporator fan power is modified since the built-in power rating is much lower than typical rating identified from typical walk-in coolers, and values provided in a Department of Energy (DOE) study for supermarket walk-in energy consumption. Based on the DOE study for commercial refrigeration [4], the power consumption is 2.3 W/ft2 for walk-in freezers, and 3.3 W/ft2 for walk-in coolers.

- The floor to ceiling height is modified to be 8 ft.

- Since the current eQuest version does not have defrosting input option for walk-in freezer, the defrosting power consumption is included as part of the internal energy input power to the walk-in freezer. According to the DOE study for commercial refrigeration [4], the electric defrost power consumption is 25 W/ft2 with a duty cycle of 4% for walk-in freezer.

The proposed models are generated by modifying the baseline model with advanced refrigeration control. Details of the modified components in the measure models are discussed below:

- The proposed evaporator fans are controlled by on/off cycling. Refer to the DEER [3] measure ID D03-210 for details of the simulation methodology for evaporator fan control on walk-in coolers and freezers.

- Implementing the advanced refrigeration control will optimize the space temperature control, resulting in savings in the refrigeration compressors. Based on measurement and verification in various pilot studies [5] [6] [7] of implementing the advanced refrigeration control in walk-in coolers and freezers, the measured room temperatures were maintained to be higher with the advanced control. This practice is included in the measure models by modifying the suction temperature setpoints of the refrigeration system.

- The proposed defrosting in a walk-in freezer is controlled by demand. The reduced defrosting electrical energy consumption is modified in the internal energy input power in the freezer.

The modified components to the DEER prototypes are summarized in Table 7 below.

Table 7 Summary of Modified Components to the DEER Prototypes

| Component | Freezer | Cooler |
| --- | --- | --- |
| Baseline Model |  |  |
| Evaporator Fan Control | Constant Volume | Constant Valume |
| Design Evaporator Fan Power* | 0.000328 kW/cfm | 0.000867 kW/cfm |
| Floor to Ceiling Height | 8 ft | 8 ft |
| Internal Energy Input Power** | 19,900.6 Btu/hr | N/A££ |
| Proposed Model |  |  |
| Supply Fan Control | Cycling | Cycling |
| Suction Temperature Setpoint£ | -21 oF | 15 oF |
| Internal Energy Input Power** | 18,514.1 Btu/hr | N/A££ |

* Modified based on the W/ft2 power consumption [4], freezer or cooler area and total design supply flow rate in the DEER prototype.

** Electrical power consumption of defrosting is included to the internal energy input power in the freezer model.

£ The proposed model considers a 3 oF suction temperature increase for the freezer, and a 1 oF suction temperature increase for the cooler based on measured space temperature from various pilot studies.

£ No electric defrosting system considered for walk-in coolers.

Once the base case and measure case model simulations were completed, the energy savings could be determined. Comparing the total electrical energy consumption of both models, the total energy savings were determined. The unit energy savings, in kWh/ton for electricity, were calculated by dividing the total energy savings by the total cooling capacity of the refrigeration system.

Once the unit energy savings were determined for each vintage and climate zone, the weighted average savings for each climate zone was determined for each building type. DEER2008 Commercial Building Weights per vintages were used to calculate the weighted average savings for each climate zone. The weighted average savings were calculated for the following building types: Grocery, Food Store, Restaurant-Sit Down, Restaurant-Fast Food, Retail-Multistory Large, Retail-Single-Story Large, and Retail-Small. The weighted average savings of all the aforementioned building types were calculated for all 16 climate zones associated with each of the following three utility companies: Southern California Edison (SCE), Pacific Gas and Electric (PGE), and San Diego Gas & Electric (SDGE). Savings summary for all utility companies can be seen in Attachment - A.

Discussion of Sensitivity Study

This workpaper is applicable to building types listed in Table 7. The energy savings evaluated by the eQuest DEER prototype is based on the building type of Grocery. A sensitivity study is included to validate the savings estimated for other building types. The sensitivity study includes eQuest simulation runs for a Fast Food Restaurant and a Small Retail in two extreme climate zones (climate zones 1 and 15) for both measures.

According to the eQuest Refrigeration Manual [8], a refrigeration fixture experiences heat gains from the surrounding exterior space depending on the space temperature and humidity ratio. Therefore, the Fast Food Restaurant and Small Retail eQuest models with a walk-in cooler and a walk-in freezer were created by modifying the following components to the Grocery prototype model based on the DEER prototypes of Fast Food Restaurant and Small Retail:

- cooling and heating design temperatures,

- occupancy schedule profile,

- area per person,

- cooling and heating temperature setpoint schedules, and

- fan schedule.

As a result, the study shows that the savings estimated by the Fast Food Restaurant and Small Retail models are within 3% discrepancy compared to savings estimated by the Grocery models for the same building vintage.  Refer to Attachment - C for details of eQuest modifications and savings outputs on the Fast Food Restaurant and a Small Retail models.

## 2.2. Demand Reduction Estimation Methodologies

Since the refrigeration system is expected to be operating at full capacity during peak demand period, no demand reduction is expected for this measure.

## 2.3. Gas Energy Savings Estimation Methodologies

The natural gas energy savings is estimated based on the eQuest building simulation outputs. Please refer to Section 2.1 for details of the eQuest models. Once the base case and measure case model simulations were completed, the energy savings could be determined. Comparing the total natural gas energy consumption of both models, the gas energy savings were determined. The unit energy savings, in therm/ton for natural gas, were calculated by dividing the total energy savings by the total cooling capacity of the refrigeration system. Once the unit energy savings were determined for each vintage and climate zone, the weighted average savings for each climate zone was determined for each building type.

Note that implementing the advanced refrigeration control will result in a tighter control of space temperature, thus preventing over cooling the coolers and freezers. As a result, there is a minimal impact to the surrounding space when the doors of the coolers and freezers are open. Based on the eQuest simulation output, implementing the advanced refrigeration control will not affect the natural gas consumption for coolers, and it will result in minimal gas savings for freezers.

# Section 3. Load Shapes

This section of the work paper explains the measure’s load shape, which indicates what fraction of annual energy usage and savings occurs in each time period of the year.

For purposes of the net benefits estimates in the E3 calculator, the difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Refrigeration load shape.  See Table 8 for a list of all Building Types and Load Shapes.

Table 8 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Grocery | Grocery_Store | Refrigeration |
| Food Store | Food_Store | Refrigeration |
| Restaurant - Fast-Food | Fast_Food_Restaurant | Refrigeration |
| Restaurant - Sit-Down | Sit_Down_Restaurant | Refrigeration |
| Retail - Multistory Large | Retail - Multistory Large | Refrigeration |
| Retail - Single-Story Large | Retail - Single-Story Large | Refrigeration |
| Retail - Small | Retail - Small | Refrigeration |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case(s) Costs

The base case considers the walk-in coolers and freezers with no advanced  refrigeration controller.  Therefore, no cost is associated with the base case at time of purchase ($0.00).

## 4.2 Measure Case Costs

The measure case considers implementing advanced refrigeration control on walk-in coolers and freezers. Based on cost data obtaining from various pilot studies, the average implementation cost, including material and installation costs, is $2,190 per controller for applying to a freezer or cooler.

## 4.3 Incremental & Full Measure Costs

Based on cost data obtained from various pilot studies [5] [6] [7], the average implementation cost, including material and installation costs, is $2,190 per controller for applying to a freezer or cooler.

# References

[1] DEER2011_NTGR_2012-05-16.xls from  DEER Database for Energy-Efficient Resources; Version 2011 4.01 found at: http://www.deeresources.com/index.php?option=com_content&view=article&id=68&Itemid=60

Under: DEER2011 Update Documentation linked at: DEER2011 Update Net-To-Gross table

[2] “California Commercial End-Use Survey,” California Energy Commission. 2006.  p 187.

[3] 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study, Prepared for Southern California Edison, Prepared by Itron, Inc., December 2005.

[4] Energy Savings Potential & R&D Opportunities for Commercial Refrigeration by Navigant Consulting for DOE, Sep 2009

[5] Adaptive Refrigerator and Freezer Controls for Commercial Applications, San Diego Gas and Electric Company, Emerging Technologies Program, Project ID ET11SDEGEC, November 23, 2012.

[6] Evaluation of an Internet-Based Refrigeration Monitoring and Control System, Southern California Edison, Design & Engineering services, December 4, 2009.

[7] Adaptive Refrigeration controls Study– Commercial & Industrial Systems, National Energy & Conservation, 2010 and 2011.

[8] DOE-2.2R, Building Energy Use and Cost Analysis Program, Volume 2r: Dictionary – Refrigeration Simulation, James J. Hirsch & Associates, August 2013

# Attachments

[A] PGECOREF124 R0 execsumm.xlsm

[B] Savings Spreadsheet_Advanced Control.xlsm

[C] RFF-RTS_Sensitivity Study_eQuest Modification_Savings.xlsm