Work Paper SCE13CS006

Revision 1

Southern California Edison Company

Classroom HVAC Occupancy Sensor

# At-a-Glance Summary

| Applicable Measure Codes: | AC-68775 AC-72229 |
| --- | --- |
| Measure Description: | Install Occupancy Controls to only run classroom HVAC equipment if the classroom is occupied and requires heating/cooling. |
| Base Case Description: | 900 ft2 classroom heated/cooled by 2013 Title 24 Code Standard Efficiency Packaged HVAC equipment (2 cases: Heat Pump and DX w/Furnace). HVAC is controlled with simple programmable thermostat with setback temperature control. |
| Energy Impact Common Units: | The work paper units are per classroom. |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | $406/classroom |
| Measure Incremental Cost ($/unit): | $406/classroom |
| Effective Useful Life (years): | Source: DEER14 (2/5/2014) 11 Years |
| Measure Application Type: | Retrofit Add-on (REA) |
| Net-to-Gross Ratios: | Source: DEER11 (5/16/2012) 0.70 |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. Major changes for Rev. 1 include updating the occupancy savings factor to be 15%, eQuest models per 2013 Title 24 standards and updating the weather files per DEER2014 CZ2010 weather data files. Additionally, all 16 California climate zones were included in this revision. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13CS006.0 | No | 05/24/2012 | Ricardo Sfeir/BASE Energy | This is the original work paper for the 2013-14 bridge period. All data used in the work paper for the previous cycle has been transposed to this new template. Saving methodologies and numbers have not been changed. |
| SCE13CS006.1 | Yes | 4/30/2014 | Jordan Hester /BASE Energy | - This work paper updated all building models to 2013 Title-24 compliance - Updated peak demand savings based on DEER2014 Peak-Demand period definitions - Updated the eQuest model weather files per DEER2014 CZ2010 weather data files - Included savings for 16 climate zones - Work paper updated for reporting period, effective 07/01/14-12/31/14 - The occupancy savings factor is updated to be 15% per the Customized Calculated Savings Guidelines for Non Residential Programs, 01/31/2014, Version 10.0 |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the estimated electrical and natural gas energy and peak demand savings for a classroom with an occupancy sensor controlled HVAC system.  The base and measure cases are as follows:

Base Case:  Thermostat controlled (not EMS controlled) packaged  HVAC system between 1.4 and 4.3  tons (depending on room type and climate zone) providing heating or cooling to one classroom with fan on/off cycling (throughout the day) and setback temperature control during closed hours (evenings, weekends, furlough days and holidays).

Measure Case:  Thermostat and occupancy sensor controlled packaged HVAC systems between 1.4 and 4.3 tons (depending on room type and climate zone)1, providing heating or cooling with fan on/off cycling for one classroom only when classroom is occupied.

This work paper considers the following two types of packaged HVAC systems (up to 5.4 Tons [359]):

DX Furnace:		packaged single zone direct expansion coils with furnace

(electric cooling and natural gas heating)

Heat Pump		packaged single zone heat pump

(electric cooling and heating)

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| AC-68775 | Classroom DX Furnace Occupancy Sensor Control |
| AC-72229 | Classroom Heat Pump Occupancy Sensor Control |

The measure is only for a single classroom in primary school, secondary school, community college, university, and relocatable classrooms.

The measure requires installation of an occupancy sensing thermostat HVAC control in the classroom. This control equipment includes, but is not limited to:

- An occupancy sensing thermostat

- An occupancy sensor (wired or wireless)

- Wiring (if wired)

- Signal receiver  and power pack (if wireless)

The thermostat should have the capability to only cycle the HVAC equipment when the classroom is occupied and has a thermal load.

## 1.2 Technical Description

Energy Savings from this measure are a result of a reduced run time of the HVAC system (fans, compressors, furnaces) due to the system only supplying heating/cooling energy to each classroom when it is occupied. An occupancy sensor in the classroom will control the thermostat regulated HVAC system to only operate if the room is occupied during school hours. The HVAC system will turn off during classroom breaks, which is approximately 15% of the time based on the Customized Calculated Savings Guidelines for Non Residential Programs, 01/31/2014, Version 10.0 (see attachment F).  According to the first approach of the Guidelines, occupancy sensors deliver (a) 15% reduction or less in lighting operating time (energy savings), and (b) 0% reduction in peak demand.

## 1.3 Measure Application Type

The delivery method is Financial Support – Direct Install and the measure install type is Retrofit Add-on (REA).

## 1.4 Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER does not contain this type of measure. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | All | Any | All | 0.7 |

*Denotes that the column is taken from the DEER NTG Table.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the work papers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex-ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | HVAC |
| Measure Case UseSubCats | Space Heating and Cooling |
| Measure Case TechGroups | HVAC Technology |
| Measure Case TechTypes | Motion Sensor |
| Base Case TechGroups | HVAC Technology |
| Base Case TechTypes | Time Clock |

### 1.4.2 Codes and Standards Analysis

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | 2013 Non-Residential Compliance Manual, Section 4.2.5 Thermostat Requirements | 07/01/2014 |
| Title 24 (2013) | 2013 Non-Residential Compliance Manual, Section 4.3.2 Mechanical Ventilation, Tables 4-13 and 4-14 | 07/01/2014 |
| ASHRAE | Standard 90.1-2013 | 2013 |

In Chapter 4.5.1 of California’s Title 24 2013 Non-Residential Compliance Manual [359], Section B requires that zone thermostatic controls must be provided for each space-conditioning zone to control the supply of heating and cooling energy within that zone.  The setpoint may be adjustable either locally or remotely, by continuous adjustment or by selection of sensors.

Section E requires that each space-conditioning system must be provided with controls that can automatically turn off the equipment during unoccupied hours.  The control device can be an automatic time switch, manual override abilities, an occupancy sensor, etc.

Section F requires that when shut down, the controls shall automatically restart the system to maintain:

1. A setback heating thermostat setpoint, if the system provides mechanical heating.

Thermostat setback controls are not required in nonresidential buildings in areas where the Winter Median of Extremes outdoor air temperature is greater than 32°F

§120.2(e)2A and Exception.

2. A setup cooling thermostat setpoint, if the system provides mechanical cooling.

Thermostat setup controls are not required in nonresidential buildings in areas where the Summer Design Dry Bulb 0.5 percent temperature is less than 100°F §120.2(e)2B and Exception.

From the ASHRAE Standard 90.1-2013 [], the thermostat must be capable of temperature setback down to 55°F and a temperature setup of 90°F during unoccupied hours.

ASHRAE HVAC Applications 2003 handbook [103] states that science classrooms (or school laboratories) may require fume hoods with special exhaust systems.  If there are no fume hoods, a room exhaust system is recommended for odor removal, depending on the type of experiments conducted in the room and whether animals are kept within the room.  Any associated storage and preparation rooms are generally exhausted continuously to remove odors and vapors emanating from stored materials.

### 1.4.3  Non-Deer Study Review

All data was taken from either DEER or Title 24 code standards.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2015 program cycle extension on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, EUL_Summary_10-1-08.xls [213], was consulted. Table 7 below identifies the value/methodology used for the measures in this work paper.

Table 7 DEER08 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-Timeclocks | Non-Residential | HVAC Misc. | Time Clocks Heating/Cooling | 11 | 3.7 |

# Section 2. Energy Savings & Demand Reduction Calculations

This work paper details the estimated electrical and natural gas energy savings and peak demand savings for a classroom with an occupancy sensor controlled HVAC system.

Energy Savings Methodology

The HVAC system operation is primarily affected by climate and occupancy; therefore, eQuest version 3-65 software was used to model and calculate the base and measure case electrical and natural gas energy consumptions. The following key inputs were updated in the eQuest models to comply with 2013 Title 24:

Window Performances (U-factor and Solar Heat Gain Coefficient, SHGC), Figure 1

DEER2014 CZ2010 weather data files

Note that according to 2013 Title 24, economizers are not required for individual space-conditioning system under 54,000 Btu/h, thus the update of high limit shut off control temperature for dry-bulb economizer in 2013 Title 24 does not apply to the classroom models in this work paper. Also, there are no updates on the efficiencies for air conditioners and heat pumps less than 54,000 Btu/hr in 2013 Title 24.

Figure 1 – Window Performance Inputs

The calculated electrical and natural gas energy consumption is for the whole HVAC system (compressors, furnaces and fans).  The energy savings is the base case energy consumption minus the measure case energy consumption.

Electrical and natural gas energy savings result from turning off the HVAC system (compressors, furnaces and fans) when a classroom is unoccupied.  A classroom is closed during the evenings, weekends, furlough days, and holidays.  Table 8 includes the operating schedule per classroom (building) type.

Table 8.  eQuest Building Operating Schedule

| Work Paper Building | eQuest Building | School Session Dates* | Daily Operating Hours** |
| --- | --- | --- | --- |
| Education – Primary School | K-6 | 9/13 – 11/9, 11/29 – 12/17, 1/10 – 4/15, 4/25 – 6/24 []*** | Mon – Fri, 8AM-3PM |
| Education – Secondary School | Secondary |  |  |
| Education – Relocatable Classroom | Relocatable |  |  |
| Education – Community College | College/University | 4/22 – 11/24, 11/26 – 12/11, 1/3 – 3/20, 3/28 – 6/11, 6/20 – 9/3 [] | Mon – Fri, 8AM-5PM |
| Education – University | College/University |  |  |

*Closed: Saturday, Sunday, furlough days and Holidays,

**From eQuest,

***eQuest does not recognize furlough days and in order to consider furlough days in the eQuest models the Los Angeles Unified School District reduced single track instructional calendar was chosen over other tracks because the furlough days occur in the beginning and at the end of school sessions.

In addition, an HVAC system will turn off during classroom breaks, which is approximately 15% of the time according to the Customized Calculated Savings Guidelines for Non Residential Programs, 01/31/2014, Version 10.0 (see attachment F).  Because eQuest software only includes hourly inputs, the estimated time that the HVAC system will turn off for breaks is conservatively set as 1 hour for all classroom types.  This hour was taken from 10 A.M. – 11 A.M as shown in Figure 3.

All classroom types are considered to be a typical classroom size of 900 ft2 with a single packaged HVAC unit up to 5.4 tons (depending on climate zone based on eQuest data).  Figure 2 is the 900 ft2 eQuest classroom model used for the analyses in this work paper.  The classroom model considers that only one wall and the roof is exposed to the ambient.  The three walls that are not exposed to the ambient have outside emissivity and inside solar absorptance values of 1 and 0, respectively.  In eQuest, the wall insulation R-value cannot be changed per wall.  The default wall R-value is R-19, which has a heat flow reduction efficiency of about 96%.

Figure 2. eQuest Classroom Model

Figure 3. Modified HVAC Schedule in an eQuest Measure Model

The variations in modeled energy consumptions per building type depend on the following default parameters used in eQuest:

Construction materials

Loading type

The eQuest models are provided in Attachment C.

An occupancy sensor will save electrical energy and natural gas by preventing the HVAC system from operating during unoccupied hours (classroom breaks, evenings, weekends, furlough days and holidays).  The estimated energy savings is the base case energy consumption minus the measure case energy consumption.

This work paper considers two HVAC packaged unit types: DX w/Furnace and Heat Pump.  The DX w/Furnace type has electric cooling and natural gas heating and the Heat Pump has electric cooling and heating.  The estimated Heat Pump electrical energy savings per each type of classroom and climate zone are provided in Table 9.  The estimated electrical energy savings per each type of classroom and climate zone for a DX with Furnace is provided in Table 10.  The estimated natural gas energy savings per each type of classroom and climate zone for a DX with Furnace is provided in Table 11.

Table 9  Summary of Heat Pump Measure Case Electrical Energy Savings

| Classroom | eQuest Building | CZ | eQuest City | Base Case EEC | Measure Case EEC | EES |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | (kWh/yr) | (kWh/yr) | (kWh/yr) |
| Primary School | K-6 | 1 | Arcata | 4,939 | 4,598 | 341 |
| Primary School | K-6 | 2 | Santa Rosa | 5,059 | 4,657 | 402 |
| Primary School | K-6 | 3 | Oakland | 4,483 | 4,235 | 248 |
| Primary School | K-6 | 4 | San Jose | 4,766 | 4,446 | 320 |
| Primary School | K-6 | 5 | Santa Maria | 4,650 | 4,385 | 265 |
| Primary School | K-6 | 6 | Torrance | 4,657 | 4,389 | 268 |
| Primary School | K-6 | 7 | San Diego | 4,456 | 4,228 | 228 |
| Primary School | K-6 | 8 | Fullerton | 4,778 | 4,489 | 289 |
| Primary School | K-6 | 9 | Burbank | 4,841 | 4,536 | 305 |
| Primary School | K-6 | 10 | Riverside | 4,986 | 4,650 | 336 |
| Primary School | K-6 | 11 | Red Bluff | 5,416 | 4,793 | 623 |
| Primary School | K-6 | 12 | Sacramento | 5,183 | 4,710 | 473 |
| Primary School | K-6 | 13 | Fresno | 5,375 | 4,783 | 592 |
| Primary School | K-6 | 14 | Palmdale | 5,500 | 4,893 | 607 |
| Primary School | K-6 | 15 | Palm Springs | 7,122 | 5,265 | 1,857 |
| Primary School | K-6 | 16 | Blue Canyon | 6,485 | 5,437 | 1,048 |
| Secondary School | Secondary | 1 | Arcata | 4,818 | 4,259 | 559 |
| Secondary School | Secondary | 2 | Santa Rosa | 4,556 | 4,178 | 378 |
| Secondary School | Secondary | 3 | Oakland | 3,973 | 3,727 | 246 |
| Secondary School | Secondary | 4 | San Jose | 4,207 | 3,946 | 261 |
| Secondary School | Secondary | 5 | Santa Maria | 4,117 | 3,870 | 247 |
| Secondary School | Secondary | 6 | Torrance | 3,929 | 3,753 | 176 |
| Secondary School | Secondary | 7 | San Diego | 3,738 | 3,595 | 143 |
| Secondary School | Secondary | 8 | Fullerton | 4,045 | 3,845 | 200 |
| Secondary School | Secondary | 9 | Burbank | 4,147 | 3,929 | 218 |
| Secondary School | Secondary | 10 | Riverside | 4,275 | 4,032 | 243 |
| Secondary School | Secondary | 11 | Red Bluff | 4,778 | 4,321 | 457 |
| Secondary School | Secondary | 12 | Sacramento | 4,629 | 4,219 | 410 |
| Secondary School | Secondary | 13 | Fresno | 4,708 | 4,299 | 409 |
| Secondary School | Secondary | 14 | Palmdale | 4,921 | 4,425 | 496 |
| Secondary School | Secondary | 15 | Palm Springs | 6,185 | 4,665 | 1,520 |
| Secondary School | Secondary | 16 | Blue Canyon | 6,557 | 5,119 | 1,438 |
| Relocatable Classroom | Relocatable | 1 | Arcata | 5,207 | 4,588 | 619 |
| Relocatable Classroom | Relocatable | 2 | Santa Rosa | 5,565 | 4,781 | 784 |
| Relocatable Classroom | Relocatable | 3 | Oakland | 4,817 | 4,359 | 458 |
| Relocatable Classroom | Relocatable | 4 | San Jose | 5,230 | 4,613 | 617 |
| Relocatable Classroom | Relocatable | 5 | Santa Maria | 5,051 | 4,560 | 491 |
| Relocatable Classroom | Relocatable | 6 | Torrance | 4,959 | 4,551 | 408 |
| Relocatable Classroom | Relocatable | 7 | San Diego | 4,673 | 4,369 | 304 |
| Relocatable Classroom | Relocatable | 8 | Fullerton | 5,076 | 4,631 | 445 |
| Relocatable Classroom | Relocatable | 9 | Burbank | 5,267 | 4,681 | 586 |
| Relocatable Classroom | Relocatable | 10 | Riverside | 5,575 | 4,795 | 780 |
| Relocatable Classroom | Relocatable | 11 | Red Bluff | 6,467 | 4,909 | 1,558 |
| Relocatable Classroom | Relocatable | 12 | Sacramento | 5,886 | 4,828 | 1,058 |
| Relocatable Classroom | Relocatable | 13 | Fresno | 6,459 | 4,916 | 1,543 |
| Relocatable Classroom | Relocatable | 14 | Palmdale | 6,598 | 5,042 | 1,556 |
| Relocatable Classroom | Relocatable | 15 | Palm Springs | 8,055 | 5,352 | 2,703 |
| Relocatable Classroom | Relocatable | 16 | Blue Canyon | 6,903 | 5,424 | 1,479 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

| Table 9 Summary of Heat Pump Measure Case Electrical Energy Savings (cont.) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Classroom | eQuest Building | CZ | eQuest City |  | Base Case | Measure Case | EES |
|  |  |  |  |  | EEC (kWh/yr) | EEC (kWh/yr) | (kWh/yr) |
| Community College | College/University | 1 | Arcata | 6,058 |  | 5,740 | 318 |
| Community College | College/University | 2 | Santa Rosa | 6,210 |  | 5,919 | 291 |
| Community College | College/University | 3 | Oakland | 5,436 |  | 5,278 | 158 |
| Community College | College/University | 4 | San Jose | 5,900 |  | 5,674 | 226 |
| Community College | College/University | 5 | Santa Maria | 5,505 |  | 5,363 | 142 |
| Community College | College/University | 6 | Torrance | 5,682 |  | 5,508 | 174 |
| Community College | College/University | 7 | San Diego | 5,431 |  | 5,285 | 146 |
| Community College | College/University | 8 | Fullerton | 5,995 |  | 5,776 | 219 |
| Community College | College/University | 9 | Burbank | 6,209 |  | 5,969 | 240 |
| Community College | College/University | 10 | Riverside | 6,448 |  | 6,116 | 332 |
| Community College | College/University | 11 | Red Bluff | 6,936 |  | 6,532 | 404 |
| Community College | College/University | 12 | Sacramento | 6,576 |  | 6,200 | 376 |
| Community College | College/University | 13 | Fresno | 7,006 |  | 6,581 | 425 |
| Community College | College/University | 14 | Palmdale | 7,093 |  | 6,648 | 445 |
| Community College | College/University | 15 | Palm Springs | 8,563 |  | 7,654 | 909 |
| Community College | College/University | 16 | Blue Canyon | 8,138 |  | 7,363 | 775 |
| University | College/University | 1 | Arcata | 6,058 |  | 5,740 | 318 |
| University | College/University | 2 | Santa Rosa | 6,210 |  | 5,919 | 291 |
| University | College/University | 3 | Oakland | 5,436 |  | 5,278 | 158 |
| University | College/University | 4 | San Jose | 5,900 |  | 5,674 | 226 |
| University | College/University | 5 | Santa Maria | 5,505 |  | 5,363 | 142 |
| University | College/University | 6 | Torrance | 5,682 |  | 5,508 | 174 |
| University | College/University | 7 | San Diego | 5,431 |  | 5,285 | 146 |
| University | College/University | 8 | Fullerton | 5,995 |  | 5,776 | 219 |
| University | College/University | 9 | Burbank | 6,209 |  | 5,969 | 240 |
| University | College/University | 10 | Riverside | 6,448 |  | 6,116 | 332 |
| University | College/University | 11 | Red Bluff | 6,936 |  | 6,532 | 404 |
| University | College/University | 12 | Sacramento | 6,576 |  | 6,200 | 376 |
| University | College/University | 13 | Fresno | 7,006 |  | 6,581 | 425 |
| University | College/University | 14 | Palmdale | 7,093 |  | 6,648 | 445 |
| University | College/University | 15 | Palm Springs | 8,563 |  | 7,654 | 909 |
| University | College/University | 16 | Blue Canyon | 8,138 |  | 7,363 | 775 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

| Table 10. Summary of DX and Furnace Measure Case Electrical Energy Savings |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Classroom | eQuest Building | CZ | eQuest City | Base Case* EEC | Measure Case EEC | EES |
|  |  |  |  | (kWh/yr) | (kWh/yr) | (kWh/yr) |
| Primary School | K-6 | 1 | Arcata | 3,786 | 3,758 | 28 |
| Primary School | K-6 | 2 | Santa Rosa | 4,119 | 4,064 | 55 |
| Primary School | K-6 | 3 | Oakland | 3,930 | 3,883 | 47 |
| Primary School | K-6 | 4 | San Jose | 4,151 | 4,085 | 66 |
| Primary School | K-6 | 5 | Santa Maria | 3,992 | 3,945 | 47 |
| Primary School | K-6 | 6 | Torrance | 4,300 | 4,203 | 97 |
| Primary School | K-6 | 7 | San Diego | 4,170 | 4,088 | 82 |
| Primary School | K-6 | 8 | Fullerton | 4,411 | 4,304 | 107 |
| Primary School | K-6 | 9 | Burbank | 4,412 | 4,312 | 100 |
| Primary School | K-6 | 10 | Riverside | 4,504 | 4,394 | 110 |
| Primary School | K-6 | 11 | Red Bluff | 4,404 | 4,307 | 97 |
| Primary School | K-6 | 12 | Sacramento | 4,340 | 4,250 | 90 |
| Primary School | K-6 | 13 | Fresno | 4,459 | 4,355 | 104 |
| Primary School | K-6 | 14 | Palmdale | 4,384 | 4,291 | 93 |
| Primary School | K-6 | 15 | Palm Springs | 5,350 | 5,122 | 228 |
| Primary School | K-6 | 16 | Blue Canyon | 3,999 | 3,953 | 46 |
| Secondary School | Secondary | 1 | Arcata | 3,478 | 3,297 | 181 |
| Secondary School | Secondary | 2 | Santa Rosa | 3,664 | 3,480 | 184 |
| Secondary School | Secondary | 3 | Oakland | 3,395 | 3,289 | 106 |
| Secondary School | Secondary | 4 | San Jose | 3,621 | 3,465 | 156 |
| Secondary School | Secondary | 5 | Santa Maria | 3,443 | 3,320 | 123 |
| Secondary School | Secondary | 6 | Torrance | 3,604 | 3,455 | 149 |
| Secondary School | Secondary | 7 | San Diego | 3,426 | 3,299 | 127 |
| Secondary School | Secondary | 8 | Fullerton | 3,709 | 3,534 | 175 |
| Secondary School | Secondary | 9 | Burbank | 3,782 | 3,597 | 185 |
| Secondary School | Secondary | 10 | Riverside | 3,883 | 3,679 | 204 |
| Secondary School | Secondary | 11 | Red Bluff | 3,970 | 3,710 | 260 |
| Secondary School | Secondary | 12 | Sacramento | 3,835 | 3,615 | 220 |
| Secondary School | Secondary | 13 | Fresno | 3,984 | 3,733 | 251 |
| Secondary School | Secondary | 14 | Palmdale | 4,010 | 3,733 | 277 |
| Secondary School | Secondary | 15 | Palm Springs | 5,891 | 4,414 | 1,477 |
| Secondary School | Secondary | 16 | Blue Canyon | 3,878 | 3,426 | 452 |
| Relocatable Classroom | Relocatable | 1 | Arcata | 4,121 | 3,789 | 332 |
| Relocatable Classroom | Relocatable | 2 | Santa Rosa | 4,679 | 4,187 | 492 |
| Relocatable Classroom | Relocatable | 3 | Oakland | 4,313 | 4,000 | 313 |
| Relocatable Classroom | Relocatable | 4 | San Jose | 4,626 | 4,204 | 422 |
| Relocatable Classroom | Relocatable | 5 | Santa Maria | 4,416 | 4,085 | 331 |
| Relocatable Classroom | Relocatable | 6 | Torrance | 4,673 | 4,330 | 343 |
| Relocatable Classroom | Relocatable | 7 | San Diego | 4,489 | 4,206 | 283 |
| Relocatable Classroom | Relocatable | 8 | Fullerton | 4,808 | 4,808 | 0 |
| Relocatable Classroom | Relocatable | 9 | Burbank | 4,924 | 4,419 | 505 |
| Relocatable Classroom | Relocatable | 10 | Riverside | 5,153 | 4,497 | 656 |
| Relocatable Classroom | Relocatable | 11 | Red Bluff | 5,545 | 4,391 | 1,154 |
| Relocatable Classroom | Relocatable | 12 | Sacramento | 5,043 | 4,327 | 716 |
| Relocatable Classroom | Relocatable | 13 | Fresno | 5,658 | 4,454 | 1,204 |
| Relocatable Classroom | Relocatable | 14 | Palmdale | 5,576 | 4,426 | 1,150 |
| Relocatable Classroom | Relocatable | 15 | Palm Springs | 7,760 | 5,168 | 2,592 |
| Relocatable Classroom | Relocatable | 16 | Blue Canyon | 4,686 | 4,006 | 680 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

| Table 10. Summary of DX and Furnace Measure Case Electrical Energy Savings (cont.) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Classroom | eQuest Building | CZ | eQuest City | Base Case EEC | Measure Case EEC | EES |
|  |  |  |  | (kWh/yr) | (kWh/yr) | (kWh/yr) |
| Community College | College/University | 1 | Arcata | 4,642 | 4,531 | 111 |
| Community College | College/University | 2 | Santa Rosa | 5,305 | 5,146 | 159 |
| Community College | College/University | 3 | Oakland | 4,845 | 4,758 | 87 |
| Community College | College/University | 4 | San Jose | 5,340 | 5,183 | 157 |
| Community College | College/University | 5 | Santa Maria | 4,838 | 4,763 | 75 |
| Community College | College/University | 6 | Torrance | 5,448 | 5,284 | 164 |
| Community College | College/University | 7 | San Diego | 5,264 | 5,123 | 141 |
| Community College | College/University | 8 | Fullerton | 5,767 | 5,563 | 204 |
| Community College | College/University | 9 | Burbank | 5,900 | 5,684 | 216 |
| Community College | College/University | 10 | Riverside | 6,108 | 5,867 | 241 |
| Community College | College/University | 11 | Red Bluff | 6,148 | 5,864 | 284 |
| Community College | College/University | 12 | Sacramento | 5,792 | 5,553 | 239 |
| Community College | College/University | 13 | Fresno | 6,318 | 6,012 | 306 |
| Community College | College/University | 14 | Palmdale | 6,220 | 5,910 | 310 |
| Community College | College/University | 15 | Palm Springs | 8,353 | 7,467 | 886 |
| Community College | College/University | 16 | Blue Canyon | 5,270 | 4,955 | 315 |
| University | College/University | 1 | Arcata | 4,,642 | 4,531 | 111 |
| University | College/University | 2 | Santa Rosa | 5,305 | 5,146 | 159 |
| University | College/University | 3 | Oakland | 4,845 | 4,758 | 87 |
| University | College/University | 4 | San Jose | 5,340 | 5,183 | 157 |
| University | College/University | 5 | Santa Maria | 4,838 | 4,763 | 75 |
| University | College/University | 6 | Torrance | 5,448 | 5,284 | 164 |
| University | College/University | 7 | San Diego | 5,,264 | 5,123 | 141 |
| University | College/University | 8 | Fullerton | 5,767 | 5,563 | 204 |
| University | College/University | 9 | Burbank | 5,900 | 5,684 | 216 |
| University | College/University | 10 | Riverside | 6,108 | 5,867 | 241 |
| University | College/University | 11 | Red Bluff | 6,148 | 5,864 | 284 |
| University | College/University | 12 | Sacramento | 5,792 | 5,553 | 239 |
| University | College/University | 13 | Fresno | 6,318 | 6,012 | 306 |
| University | College/University | 14 | Palmdale | 6,220 | 5,910 | 310 |
| University | College/University | 15 | Palm Springs | 8,353 | 7,467 | 886 |
| University | College/University | 16 | Blue Canyon | 5,270 | 4,955 | 315 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

| Table 11. Summary of DX and Furnace Natural Gas Energy Savings |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Classroom | eQuest Building | CZ | eQuest City | Base Case GEC | Measure Case GEC | GES |
|  |  |  |  | (therms/yr) | (therms/yr) | (therms/yr) |
| Primary School | K-6 | 1 | Arcata | 171 | 159 | 12 |
| Primary School | K-6 | 2 | Santa Rosa | 130 | 124 | 6 |
| Primary School | K-6 | 3 | Oakland | 107 | 104 | 3 |
| Primary School | K-6 | 4 | San Jose | 102 | 98 | 4 |
| Primary School | K-6 | 5 | Santa Maria | 115 | 112 | 3 |
| Primary School | K-6 | 6 | Torrance | 74 | 73 | 1 |
| Primary School | K-6 | 7 | San Diego | 65 | 65 | 0 |
| Primary School | K-6 | 8 | Fullerton | 70 | 70 | 0 |
| Primary School | K-6 | 9 | Burbank | 77 | 76 | 1 |
| Primary School | K-6 | 10 | Riverside | 80 | 79 | 1 |
| Primary School | K-6 | 11 | Red Bluff | 118 | 111 | 7 |
| Primary School | K-6 | 12 | Sacramento | 114 | 109 | 5 |
| Primary School | K-6 | 13 | Fresno | 106 | 101 | 5 |
| Primary School | K-6 | 14 | Palmdale | 117 | 112 | 5 |
| Primary School | K-6 | 15 | Palm Springs | 52 | 52 | 0 |
| Primary School | K-6 | 16 | Blue Canyon | 223 | 206 | 17 |
| Secondary School | Secondary | 1 | Arcata | 332 | 275 | 57 |
| Secondary School | Secondary | 2 | Santa Rosa | 245 | 220 | 25 |
| Secondary School | Secondary | 3 | Oakland | 214 | 201 | 13 |
| Secondary School | Secondary | 4 | San Jose | 201 | 188 | 13 |
| Secondary School | Secondary | 5 | Santa Maria | 223 | 206 | 17 |
| Secondary School | Secondary | 6 | Torrance | 155 | 154 | 1 |
| Secondary School | Secondary | 7 | San Diego | 145 | 144 | 1 |
| Secondary School | Secondary | 8 | Fullerton | 148 | 147 | 1 |
| Secondary School | Secondary | 9 | Burbank | 158 | 154 | 4 |
| Secondary School | Secondary | 10 | Riverside | 160 | 156 | 4 |
| Secondary School | Secondary | 11 | Red Bluff | 221 | 198 | 23 |
| Secondary School | Secondary | 12 | Sacramento | 221 | 200 | 21 |
| Secondary School | Secondary | 13 | Fresno | 202 | 185 | 17 |
| Secondary School | Secondary | 14 | Palmdale | 229 | 202 | 27 |
| Secondary School | Secondary | 15 | Palm Springs | 116 | 115 | 1 |
| Secondary School | Secondary | 16 | Blue Canyon | 439 | 308 | 131 |
| Relocatable Classroom | Relocatable | 1 | Arcata | 99 | 94 | 5 |
| Relocatable Classroom | Relocatable | 2 | Santa Rosa | 107 | 74 | 33 |
| Relocatable Classroom | Relocatable | 3 | Oakland | 71 | 54 | 17 |
| Relocatable Classroom | Relocatable | 4 | San Jose | 77 | 54 | 23 |
| Relocatable Classroom | Relocatable | 5 | Santa Maria | 85 | 65 | 20 |
| Relocatable Classroom | Relocatable | 6 | Torrance | 38 | 31 | 7 |
| Relocatable Classroom | Relocatable | 7 | San Diego | 24 | 22 | 2 |
| Relocatable Classroom | Relocatable | 8 | Fullerton | 34 | 29 | 5 |
| Relocatable Classroom | Relocatable | 9 | Burbank | 44 | 35 | 9 |
| Relocatable Classroom | Relocatable | 10 | Riverside | 51 | 39 | 12 |
| Relocatable Classroom | Relocatable | 11 | Red Bluff | 108 | 67 | 41 |
| Relocatable Classroom | Relocatable | 12 | Sacramento | 98 | 63 | 35 |
| Relocatable Classroom | Relocatable | 13 | Fresno | 91 | 57 | 34 |
| Relocatable Classroom | Relocatable | 14 | Palmdale | 118 | 72 | 46 |
| Relocatable Classroom | Relocatable | 15 | Palm Springs | 24 | 19 | 5 |
| Relocatable Classroom | Relocatable | 16 | Blue Canyon | 255 | 137 | 118 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

| Table 11. Summary of DX and Furnace Natural Gas Energy Savings (cond.) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Classroom | eQuest Building | CZ | eQuest City | Base Case | Measure Case | GES |
|  |  |  |  | GEC (therms/yr) | GEC (therms/yr) | (therms/yr) |
| Community College | College/University | 1 | Arcata | 330 | 296 | 34 |
| Community College | College/University | 2 | Santa Rosa | 233 | 215 | 18 |
| Community College | College/University | 3 | Oakland | 205 | 195 | 10 |
| Community College | College/University | 4 | San Jose | 188 | 179 | 9 |
| Community College | College/University | 5 | Santa Maria | 213 | 204 | 9 |
| Community College | College/University | 6 | Torrance | 141 | 140 | 1 |
| Community College | College/University | 7 | San Diego | 130 | 129 | 1 |
| Community College | College/University | 8 | Fullerton | 135 | 133 | 2 |
| Community College | College/University | 9 | Burbank | 146 | 143 | 3 |
| Community College | College/University | 10 | Riverside | 149 | 149 | 0 |
| Community College | College/University | 11 | Red Bluff | 209 | 195 | 14 |
| Community College | College/University | 12 | Sacramento | 211 | 195 | 16 |
| Community College | College/University | 13 | Fresno | 191 | 177 | 14 |
| Community College | College/University | 14 | Palmdale | 216 | 199 | 17 |
| Community College | College/University | 15 | Palm Springs | 103 | 102 | 1 |
| Community College | College/University | 16 | Blue Canyon | 429 | 358 | 71 |
| University | College/University | 1 | Arcata | 330 | 296 | 34 |
| University | College/University | 2 | Santa Rosa | 233 | 215 | 18 |
| University | College/University | 3 | Oakland | 205 | 195 | 10 |
| University | College/University | 4 | San Jose | 188 | 179 | 9 |
| University | College/University | 5 | Santa Maria | 213 | 204 | 9 |
| University | College/University | 6 | Torrance | 141 | 140 | 1 |
| University | College/University | 7 | San Diego | 130 | 129 | 1 |
| University | College/University | 8 | Fullerton | 135 | 133 | 2 |
| University | College/University | 9 | Burbank | 146 | 143 | 3 |
| University | College/University | 10 | Riverside | 149 | 149 | 0 |
| University | College/University | 11 | Red Bluff | 209 | 195 | 14 |
| University | College/University | 12 | Sacramento | 211 | 195 | 16 |
| University | College/University | 13 | Fresno | 191 | 177 | 14 |
| University | College/University | 14 | Palmdale | 216 | 199 | 17 |
| University | College/University | 15 | Palm Springs | 103 | 102 | 1 |
| University | College/University | 16 | Blue Canyon | 429 | 358 | 71 |

CZ = climate zone,  EEC = electrical energy consumption, EES = electrical energy savings

Peak Demand Savings Methodology

According to the first approach of the Guidelines in Attachment F, occupancy sensors deliver (a) 15% reduction or less in lighting operating time (energy savings), and (b) 0% reduction in peak demand.  Hence, no peak demand savings is evaluated for this workpaper.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the “Occupancy Sensor” load shape.  See Table 15 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure. The closest load shape chosen

Table 15 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Education – Primary School | K_thru_12_School | Occupancy Sensor |
| Education – Secondary School | K_thru_12_School | Occupancy Sensor |
| Education – Relocatable Classroom | K_thru_12_School | Occupancy Sensor |
| Education – Community College | K_thru_12_School | Occupancy Sensor |
| Education – University | K_thru_12_School | Occupancy Sensor |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The base case of this measure means that there is no occupancy control technology installed in the classroom. Thus the base case cost is $0.

## 4.2 Measure Case Cost

The measure case gross material and installation costs were taken from the 2014 RSMeans Electrical Cost Data Guidebook and include all labor, overhead, and profit costs associated with the implementation of the measure.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

The measure case is an occupancy sensing thermostat controlled packaged 1.4 to 4.3-ton HVAC system providing heating or cooling with fan on/off cycling for one classroom only when classroom is occupied.  The difference between the measure and base case is the upgraded occupancy sensing thermostat. For this there are two options: wireless and wired. In wireless systems, a battery powered occupancy sensor sends a wireless signal to a receiver connected to the thermostat. This system requires less labor cost because signal wiring does not need to be installed, though the material cost is significantly more. With wired systems, an occupancy sensor sends the signal to the thermostat though a low voltage signal wire. The labor cost is slightly more than the wireless system because wires need to be installed. However, the material costs are significantly less. The measure cost is the material and installation for one occupancy sensing thermostat with the required peripheral equipment.  The measure costs for the wireless and wired systems are estimated to be $488 and $323, respectively, and are summarized in Table 16. The gross measure cost for this measure was taken to be the average cost of the two different technologies, or $406.

Table 16  Measure Case Cost

| Equipment | Measure Case Material Cost | Measure Case Installation Cost* | Measure Case Total Cost |
| --- | --- | --- | --- |
| Wireless Occupancy Sensor |  |  |  |
| (1) Occupancy Sensing Thermostat (includes mounting bracket) | $129 | $30 | $159 |
| (1) Wall Mounted Wireless Occupancy Sensor | $129 | $60 | $189 |
| (1) 2-Channel Receiver for Wireless Occupancy Sensor | $115 | $5 | $120 |
| (1) 12 Volt Power Supply | $15 | $5 | $20 |
| Total | $388 | $100 | $488 |
| Wired Occupancy Sensor |  |  |  |
| (1) Occupancy Sensing Thermostat (includes mounting bracket) | $129 | $30 | $159 |
| (1) Wall Mounted Wired Occupancy Sensor | $39 | $60 | $99 |
| (1) 50ft Section of Control Wiring | $13 | $52 | $65 |
| Total | $181 | $142 | $323 |
| Average of Two Technologies | $285 | $121 | $406 |

*Installation includes labor, overhead and profit

### 4.3.2 Incremental Measure Cost

The incremental measure cost is the same as the gross measure costs as this is a retrofit add on type of measure.

# Attachments

# References

[31] [103] [213] [351] [359]

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |

[]	ASHRAE Standard 90.1-2013

[] 	Los Angeles Unified School District 2010-2011 Calendar, see Attachment D

[] 	UCLA and CSU LA 2010-2012 Academic Calendars, see Attachment E

These system tonnages were estimated using eQuest v. 65’s auto size function. Note that the eQuest sized cooling capacities are larger than the values provided in the last revision. This is mainly due to the new DEER2014 CZ2010 weather data files used in the simulation. The average and peak temperatures during the new peak demand periods are generally higher than those based on the previous weather files.