Work Paper SCE13CS011

Revision 0

Southern California Edison Company

Demand Controlled Ventilation + Demand Based Fan Control

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Measure RunID | Solution Code | CZ | Building Type | Load Shape | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | kWh Saving per unit (kWh/unit) | kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % TOU |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 06 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 127.10 | 0.0000 | 21.41 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 08 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 193.31 | 0.0143 | 22.33 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 09 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 225.78 | 0.0484 | 21.32 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 10 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 229.42 | 0.0326 | 26.76 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 13 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 282.64 | 0.0234 | 40.07 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 14 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 221.97 | 0.0193 | 47.57 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 15 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 490.17 | 0.0212 | 13.06 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |  | AX-1XXXX | 16 | Assembly | Reduce_Cooling_Load-Ret | 10.0 | Ton | REA | Yes | 110.63 | 0.0136 | 87.55 | 10.0 | 0.00 | 0.0000 | 0.00 | 0.00 | 0.00 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | Installation Rate | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 6 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 8 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 9 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 10 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 13 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 14 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 15 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | AX-1XXXX | 16 | Ton | REA | Yes | 0.85 | 0 | 0 | 1.00 | From Program | $0.00 | $0.00 | Financial Support / Direct Install |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 12/12/2012 | Andres Fergadiotti/SCE | Developed workpaper on measure. Methodology for estimating DCV + fan cycling energy and demand savings based on surveyed occupancy per defaulted DOE2 Fitness Center building in 2008 Title-24 Compliance |

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

### 1.1a Measure Description

The basecase mechanical (HVAC) systems are single zone packaged DX-cooling/gas heating (PSZ-AC) constant volume mechanical systems.  These are equipped with fully functional air-side economizers controlled by drybulb temperature sensors that meet minimum Title-24 2008 [208] ventilation requirements. The analysis additionally includes single zone packaged heat pump (PSZ-HP), constant volume, mechanical systems with same operating conditions as the PSZ-AC.

The measure adds (a) demand controlled ventilation (DCV) and (b) fan cycling controls to mechanical systems in buildings that under the baseline do not utilize this control strategy. The measure requires the installation of CO2 (space) sensors for sequencing and controlling the operation of the mechanical systems upon occupancy.

With demand control ventilation (DCV), the measure saves energy and demand by limiting the amount of ventilation delivered into the building based upon concentration levels of CO2.  Reducing ventilation provides energy and demand savings by reducing the amount of cooling and/or heating energy required in the space.

With fan cycling, the measure saves demand and energy by slightly reducing fan operation when occupancy in the building is limited and there are no cooling and/or heating requirements in the space.  While the 2008 California Building Energy Efficiency Standards require [208] that ventilation be continuous during normally occupied hours, some exceptions allow for the ventilation to be disrupted for short times.

The target market participants for this measure are fitness centers with high-occupancy areas and high occupancy variations. Whole building simulations for this work paper is based on DOE2 (eQuest 3.64) defaulted 2008 CA Title-24 [208] compliant Fitness Centers with exercising centers and gymnasium occupancies.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| AX-1#### | Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) |
| AX-2#### | Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 24 hour (PSZ-AC) |
| AX-3#### | Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-HP) |
| AX-4#### | Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 24 hour (PSZ-HP) |

### 1.1b Delivery and Incentive Mechanism

The measures outlined in this work-paper are for Retrofit-Add On (REA) applications. This is a subtype of RET that is specifically for adding a piece of equipment to an existing system or equipment to make the overall system or equipment more efficient.

The delivery/incentive method is Financial Support – Direct Install.

### 1.1c Measure Requirements

Details are based upon contractual agreements with implementers receiving payments to provide the direct installation services.

The measure requires installation of CO2 sensor(s) in the space and new sequences of operation for demand control ventilation and short-term fan cycling during very low occupancy periods based on CO2 concentration.  The measure shall include alarms on high CO2 concentration levels and operating limits limiting short-term fan cycling durations and number of events.

The measure will require outdoor airflow verification. The total quantity of outdoor air to air handlers of supply air shall be measured in minimum outdoor air mode. If measured minimum airflow rates are less than the design minimum rate, they shall be adjusted or modified to bring them to the minimum design rate or evaluated to determine if the measured rates are in compliance with Code.

The measure can be executed by re-programming existing unitary DDC controller (if available and granted control point capacity is available) or by installing a new DDC controller. The new unitary DDC controllers shall be consistent and compatible with existing DDC controllers, protocol, and energy management system in the building. The measure (including but not limited to installation of CO2 sensors, controllers, and new sequence of operation) shall comply with all applicable codes and regulations including but not limited to California Title-24 2008 [208], CMC, and NEC.

## 1.2  DEER Differences Analysis

This specific measure is not included in the Database for Energy Efficient Resources Version 2011 or 2008.2.05 [49].  Although there is an over-ventilation measure in DEER 2005 [26], it is not a good representation of the technology being evaluated in this document.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No (Building type not included in DEER Building Prototypes). Whole building energy simulation models are based on DOE2.2/eQuest 3.64 Health Fitness Center defaulted prototype |
| Deviation from DEER | DEER does not contain this type of measure. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

## 1.3  Code Analysis

Title 24 2008 [208], California's energy-efficiency standard, requires demand control ventilation (DCV) in all spaces where an HVAC single-zone system includes an economizer and where there is an occupant density greater than or equal to 25 people per 1,000 sq. ft., with some exceptions.

Additionally, according to the Title 24 2008 [208], Section 121, California's energy-efficiency standard the specific requirements must be taken into consideration:

“Required Demand Control Ventilation. HVAC systems with the following characteristics shall have demand ventilation controls complying with 121(c)4:

A. They have an air economizer; and

B. They serve a space with a design occupant density, or a maximum occupant load factor for egress purposes in the CBC, greater than or equal to 25 people per 1000 ft2 (40 square foot per person); and

C. They are either:

i. 	Single zone systems with any controls; or

ii. 	Multiple zone systems with Direct Digital Controls (DDC) to the zone level.

EXCEPTION 1 to Section 121(c)3: Classrooms, call centers, office spaces served by multiple zone systems that are continuously occupied during normal business hours with occupant density greater than 25 people per 1000 ft2 per Section 121(b)2B, healthcare facilities and medical buildings, and public areas of social services buildings are not required to have demand control ventilation.

EXCEPTION 2 to Section 121(c)3: Where space exhaust is greater than the design ventilation rate specified in Section 121(b)2B minus 0.2 cfm per ft2 of conditioned area.

EXCEPTION 3 to Section 121(c)3: Spaces that have processes or operations that generate dusts, fumes, mists, vapors, or gases and are not provided with local exhaust ventilation, such as indoor operation of internal combustion engines or areas designated for unvented food service preparation, or beauty salons shall not install demand control ventilation.

EXCEPTION 4 to Section 121(c)3: Spaces with an area of less than 150 square feet, or a design occupancy of less than 10 people per Section 121(b)2B.

4. Demand Control Ventilation Devices.

A. For each system with demand control ventilation, CO2 sensors shall be installed in each room that meets the criteria of Section 121(c)3B with no less than one sensor per 10,000 ft² of floor space. When a zone or a space is served by more than one sensor, signal from any sensor indicating that CO2 is near or at the setpoint within a space, shall trigger an increase in ventilation to the space;

B. CO2 sensors shall be located in the room between 3 ft and 6 ft above the floor or at the anticipated height of the occupant’s heads.

C. Demand ventilation controls shall maintain CO2 concentrations less than or equal to 600 ppm plus the outdoor air CO2 concentration in all rooms with CO2 sensors;

EXCEPTION to Section 121(c)4C: The outdoor air ventilation rate is not required to be larger than the design outdoor air ventilation rate required by Section 121(b)2 regardless of CO2 concentration.

D. Outdoor air CO2 concentration shall be determined by one of the following:

i. CO2 concentration shall be assumed to be 400 ppm without any direct measurement; or

ii. CO2 concentration shall be dynamically measured using a CO2 sensor located within 4 ft of the outdoor air intake.

E. When the system is operating during hours of expected occupancy, the controls shall maintain system outdoor air ventilation rates no less than the rate listed in TABLE 121-A times the conditioned floor area for spaces with CO2 sensors, plus the rate required by Section 121(b)2 for other spaces served by the system, or the exhaust air rate whichever is greater;

F. CO2 sensors shall be certified by the manufacturer to be accurate within plus or minus 75 ppm at a 600 and 1000 ppm concentration when measured at sea level and 25°C, factory calibrated or calibrated at start-up, and certified by the manufacturer to require calibration no more frequently than once every 5 years. Upon detection of sensor failure, the system shall provide a signal which resets to supply the minimum quantity of outside air to levels required by Section 121(b)2 to the zone serviced by the sensor at all times that the zone is occupied.

G. The CO2 sensor(s) reading for each zone shall be displayed continuously, and shall be recorded on systems with DDC to the zone level. “

4.3.2 Mechanical Ventilation §121(b)2 and (d)

For each space requiring mechanical ventilation the ventilation rates must be the greater of either:

1. The conditioned floor area of the space, multiplied by the applicable minimum ventilation rate from the Standards in Table 121-A (Table 4-1).

2. 15 cfm per person, multiplied by the expected number of occupants. For spaces with fixed seating (such as a theater or auditorium), the expected number of occupants is the number of

fixed seats. For spaces without fixed seating, the expected number of occupants is assumed to be no less than one-half that determined for egress purposes in the California Building Code (CBC). The Standards specify the minimum outdoor ventilation rate to which the system must be designed.

4.3.8 Fan Cycling

While Section §121(c)1 of the Code requires that ventilation be continuous during normally occupied hours, Exception No. 2 allows the ventilation to be disrupted for not more than 5 minutes out of every hour. In this case the ventilation rate during the time the system is ventilating must be increased so the average rate over the hour is equal to the required rate.

This restriction limits the duty cycling of fans by energy management systems to not more than 5 minutes out of every hour.  In addition, when a space-conditioning system that also provides ventilation is controlled by a thermostat incorporating a fan “On/Auto” switch, the switch should be set to the “On” position. Otherwise, during mild conditions, the fan may be off the majority of the time.

## California Energy Commission Response to Demand Controlled Ventilation & Fan Cycling Methodology

The CEC provided interpretation and approval regarding the applicable 2008 Building Energy Efficiency Standards requirement for the proposed measure.  In general terms, the CEC indicated that many demand response programs in California have been using the duty-cycling of air-conditioning systems as a way to reduce coincident peak demand during critical utility peak periods while maintaining acceptable indoor air quality levels, and that the proposed demand control ventilation with demand based fan control measure and controls, complies with the 2008 Energy Standards.

Further, CEC indicated that due to the fact that the installation of the measure and controls as proposed in the reviewed documentation is not considered or defined as an alteration under the Standards, there are no other applicable requirements beyond what is proposed in the measure. Attachment 4 includes communication with the CEC.

## ASHRAE 62.1 – 2010 Ventilation for Acceptance Indoor Air Quality

The ASHRAE 62.1 Standard specifies minimum ventilation rates and other measures intended to provide indoor air quality that is acceptable to human occupants and that minimizes adverse health effects.  The Standard is intended for regulatory applications to new buildings, additions to existing buildings, and those changes to existing buildings.

In relation to this project, the Standard includes provisions for fan cycling allowing intermittent ventilation as long as the average outdoor airflow is not less than the breathing zone outdoor (prescriptive) airflow. Based on provided clarifications of the Standard, ventilation fans may be turned off for up to 30 minutes, when a zone is occupied, as long as the ventilation rate is increase during fan operation and average ventilation is maintained in compliance with the Standard. Further documentation in Section 2 details fan-cycle off durations allowed in the analysis.

Table 3 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2008) | 2008 Non-Residential Compliance Manual, Mechanical Ventilation §121(b)2 and (d); Demand Controlled Ventilation §121(c) 3; and Fan Cycling – Section 4.3.8. | 2008 |
| Standard ASHRAE 62.1-2010 | Ventilation for Acceptable Indoor Air Quality | 2010 |

## 1.4  Measure Effective Useful Life

DEER11 documentation provides EUL and RUL information to be used for the 13-14 program cycle on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER08 documentation, EUL_Summary_10-1-08.xls [213], was consulted. Table 4 below identifies the value/methodology used for the measures in this work paper.

This work paper uses DEER EUL_ID HVAC-RedcOverVent.

Table 4 DEER08 EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- |
| Non-Residential | HVAC - Miscellaneous | Reducing Overventilation | 10 | N/A |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 4 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [132]. The relevant NTGR for this measure is shown in Table 5 below.

Table 5 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default-HTG-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Com | Any | DirInstalled | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

The installation rate (IR) is identified in the calculation attachment. This value is obtained from a spreadsheet created by the DEER team titled ““GrossSavingsAdjustments.xlsx”. The installation rate varies by end use, sector, technology, application, and delivery method.

## Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0. Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 6  TOU Summary Table

| Measure | % |
| --- | --- |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-AC) | 0 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 24 hour (PSZ-AC) | 0 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 17 hour (PSZ-HP) | 0 |
| Demand Control Ventilation + Demand Based Fan Control (Fitness Center) Control – 24 hour (PSZ-HP) | 0 |

*Note:  Check Section 3 if a measure appears to require a non-zero percentage but is assigned zero.  If the load shape is a DEER08 load shape, a TOU of 0 is correct.

# Section 2. Energy Savings & Demand Reduction Calculations

## 2.1 Energy Savings

The energy savings calculations associated with the measure including demand controlled ventilation and fan cycling are based on whole building energy simulations of a defaulted DOE2 (eQuest 3.64) Fitness Center with exercising centers and gymnasium occupancies under 2008 Title 24 [208] compliance.

The baseline mechanical system consists of a constant volume single zone packaged dx-cooling/gas heating (PSZ-AC) with air-economizer controlled by outdoor air (drybulb) temperature.  Additionally, the model  includes a constant volume single zone packaged heat pump (PSZ-HP).  Operating parameters on the mechanical and lighting systems including operating schedules, mechanical efficiencies, temperature setpoints, lighting power densities, and equipment (plug) loads are per the defaulted DOE2 model.  Table 7 summarizes general parameters defaulted and/or user-defined programmed in the building simulation.

Table 7 General Input Parameters in Whole Building Energy Simulation

|  | Input Parameter | Input Parameter Description | Remark |
| --- | --- | --- | --- |
|  | Building Description | Fitness Center | DOE2 Default |
|  | Building Area | 20,000 sqft | DOE2 Default |
|  | Building Envelop Constructions | All Per 2008 Title 24 | DOE2 Default |
|  | Typical Operating Schedule | 17 Hours (Adjusted for 24 hours) | DOE2 Default |
|  | Primary occupancies | Exercising Centers and Gymnasium | DOE2 Default |
|  | Average LPD | 0.94 W/sqft | DOE2 Default |
|  | Average equipment load | 0.13 W/sqft | DOE2 Default |
|  | HVAC system types | (PSZ-AC) (PSZ-HP) | DOE2 Default |
|  | Cooling setpoint/setback | 74.0 deg F / 82.0 deg F | User defined |
|  | Heating setpoint/setback | 68.0 deg F / 64.0 deg F | DOE2 Default |
|  | Mechanical system efficiencies | PSZ-AC: 8.5 EER ; 80.6% thermal effic. PSZ-HP: 8.5 EER ; 3.28 COP | DOE2 Default |
|  | Air Economizer | Drybulb controlled ; 70 deg. F high limit | DOE2 Default |
|  | Ventilation - OSA/Person | 15 cfm | User defined |
|  | Design outside air ratio | 0.31 (outdoor air to system flow) | DOE2 Default |
|  | Max. occupancy density | 57.0 sqft/occ | DOE2 Default |
|  | Max. occupancy | 353 occupants | DOE2 Default |
|  | Total heat gain per occupant | 1,070 Btu/h (255 sensible + 815 latent) Btu/h | DOE2 Default |

Cooling Load and DEER (Peak) Demand

Peak cooling load and DEER (peak) demand on the two studied building occupancies (17-hour and 24-hour) were assumed to be comparable.  This is expected since both building occupancies during the peak demand period have identical thermal performance and building characteristics including occupancy and internal loads.  Additionally, the design cooling capacity is expected to be the same in both cases since cooling peak loads on the two buildings are comparable.  In a few cases, it was noticed from the simulated results that there were some small variations on peak demand (e.g., < 2.0%) between the two buildings as reported by DOE2.2/eQuest.

Occupancy Schedule

Methodology for modeling demand control ventilation and fan cycling is connected to the occupancy in the building. Specifically, demand controlled ventilation is modeled based on the occupancy (fraction) schedule and the Standard’s minimum ventilation rate of 15.0 cfm per occupant. Peak occupancy density in the building was defaulted per DOE2; however, occupancy (fraction) profiles were extracted from hourly clock in data acquired and surveyed from a chain fitness center customer and programmed into the model. Figure 1 describes utilized weekdays and weekend occupancy (fraction) profiles for 17 hour operation.

Figure 1 Occupancy Schedule Fraction

The daytime occupancy schedule of a 24hr fitness center approximate that of a 17hr fitness center with late night occupancy fractions averaging 0.052 with lowest fraction of 0.0035 at 2:00 a.m. Occupancy fraction schedules pre-determined for the work paper and used in the analysis are included in Attachment 5.

Fan Cycling Control Strategy

This control strategy is based on the Energy Standard and ASHRAE Standard 62.1 2010 - Ventilation for Acceptable Indoor Air Quality, both allowing short-term interruption of ventilation granted the average ventilation levels are maintained equal to prescriptive limits. This strategy requires ventilation rates to be increased over the prescriptive rates during fan operation.  See reference information provided in previous Section 1.3.

Prescriptive ventilation requirements defaulted by the energy model (as per the Energy Standards) average 0.31 – the fraction of outdoor air to total system flow. This value represents the average prescriptive ventilation to be maintained during fan operation and to be met if introducing fan cycling.

The fan cycling control strategy is optimized during mild weather conditions when economizer operation is maximized.  Contrary, this control strategy is limited (in some cases prohibited) during extreme weather conditions when economizing operation is limited and ventilation rates are controlled by occupancy (e.g., DCV).

Based on economizer operation expected for this occupancy and prescriptive ventilation rates, it is conservatively estimated that fan cycle-off operation will accumulatively approximate to no more than 2 hours per day (or 11.8% of daily operation) on the 17-hr fitness center and 3 hours per day (or 12.5% of daily operation) on the 24-hrs fitness center.  These fan cycle-off accumulative durations comply with ASHRAE Standard 62.1, but slightly exceed those in the Code limiting every event to no more than 5 minutes (or 8.3% of daily operation).

Based on economizer operation and demand controlled ventilation presumed for this occupancy, it is expected that on average, prescriptive ventilation limits will be met by the measure and control strategy.

Demand controlled ventilation and fan cycling are both occupancy and weather dependent.  In all cases, time and durations for fan off-cycle shall be project specific and determined per ASHRAE Standard 62.1 2010 in compliance with the Energy Standards.

A sample energy savings estimate for 17-hr Fitness Center facility in climate zone 6 is shown in Table 8 as calculated using Equation 1. Same methodology was used in both facilities and all climate zones.

Table 8 Energy Savings for 17-hr Fitness Center facility

| Facility | Design Cooling Capacity (Tons) | Climate Zone | Base Energy Consumption [kWh] | Measure Energy Consumption [kWh] | Energy Savings [kWh/ton] |
| --- | --- | --- | --- | --- | --- |
| 17-hr (PSZ-Ac) | 47.9 | 06 | 57,736 | 51,651 | 127.1 |

[Equation 1]

## 2.1.2 Demand Reduction

The energy savings calculations associated with the measure including demand controlled ventilation and fan cycling are based on whole building energy simulations of a defaulted DOE2 Fitness Center with exercising centers and gymnasium occupancies under Title 24 compliance.

A sample demand savings estimate for 17-hr Fitness Center facility in climate zone 10 using PSZ-AC is shown in Table 9 as calculated per equation 2. The DEER peak demand methodology was used to establish the demand reductions.  The same methodology was used in both facilities, mechanical systems, and all climate zones.

Table 9 Demand Savings for 17-hr Fitness Center facility

| Facility | Design Cooling Capacity (Tons) | Climate Zone | Base Demand [kW] | Measure Demand [kW] | Demand Savings [kW/ton] |
| --- | --- | --- | --- | --- | --- |
| 17-hr (PSZ-AC) | 47.9 | 10 | 79.46 | 77.89 | 0.033 |

[Equation 2]

Attachment 1 [Calculation Template v2.2.xlsm] includes detail energy and demand savings estimates for both facilities using both mechanical systems in all climates zones.  Additionally, this attachment includes detailed gas savings documentation on the (PSZ-AC) measure.  Attachment 3 [Fitness Center eQuest.zip] includes DOE2-based whole building energy simulations used for energy and demand savings estimates on the measure.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Reduce_Cooling_Load-Ret load shape.  See Table 10 for Building Type and Load Shape. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 10 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Assembly | Large_Office | Reduce_Cooling_Load-Ret |

# Section 4. Base Case & Measure Costs

Direct install programs record their actual purchase and installation costs associated with their HVAC systems.

## 4.1 Base Case Cost

For this measure category, the base case cost is assumed to be zero because these are discretionary modifications (Retrofit-Add On) to the customers’ existing equipment. Their alternative is to make no changes to their existing system.

## 4.2 Gross Measure Cost

SCE directly utilizes one or more contractors as part of the program.  The actual cost can vary by contractor, the date in which the work occurred, and by the volume of business.  Contractor costs are confidential information and are based upon contractually agreed upon pricing as established in their purchase order with SCE; therefore, the SCE program tracking system is the only source for this data.

## 4.3 Incremental Measure Cost

See Section 4.2.

# Attachments

# References

[26]

[31]

[49]

[132]

[208]

[213]