Work Paper SCE13HC012

Revision 5

Southern California Edison

Unitary Air Cooled Commercial Air Conditioning and Heat Pump Units Under 65 kBtuh

For Work Paper Reviewer Use Only

List all major comments that occurred during the review. This table may only be removed during management review.

| Major Comment | Reviewer Name | Date | Outcome/Resolution |
| --- | --- | --- | --- |
| E.g. Please remove measure LT-12345 (LD123) from this work paper because it is no longer eligible for incentives. | Reviewer 1 | 6/1/15 | E.g. Comment incorporated. LT-12345 was removed. |

# At-a-Glance Summary

| Measure Codes | Refer to Section 1.1 |
| --- | --- |
| Measure Description | Air cooled air conditioning or heat pump units with cooling capacities less than 65 kBtuh, for use in non-residential buildings, meeting the minimum efficiency requirements listed in Section 1.1. |
| Base Case Description | Air cooled air conditioning or heat pump units with cooling capacities less than 65 kBtuh, for use in non-residential buildings, meeting the federal minimum efficiency standard of 14 SEER. |
| Units | Per ton |
| Energy Savings | Refer to Excel Calculation Attachment [A] |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment [A] |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment [A] |
| Effective Useful Life | 15 years (DEER EUL ID: HVAC-airAC, HVAC-airHP) |
| Measure Installation Type | Above Code measures: New Construction (NEW) and Replace on Burnout (ROB) To-Code measures: Retrofit (RET) |
| Net-to-Gross Ratio | 0.75 (DEER NTGR ID: NonRes-sAll-mHVAC-DX-up) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 5/16/2012 | Alex MacCurdy/Elizabeth Joyce (Energy Solutions) | Updated to SCE Work Paper Template 2013 v0.1 Updated scaling factor calculation for Tiers 2, 3 and 4. Added Heat Pump Units |
| 1 | 11/18/2013 | Alfredo Gutierrez (SCE) | Updated the work paper with the following: - New delivery early retirement delivery method which includes Added RET for all existing measures - Savings and Costs for RET are actually RET-ROB values in order to prevent the HVAC Upstream program from double counting the savings |
| 2 | 1/27/2014 | Alfredo Gutierrez (SCE) | Added in the following building type to be consistent with the ED filed REV 0 of this work paper: - Miscellaneous Commercial - RET Measures have been separated into two new solution codes. |
| 3 | 4/17/2014 | Jason Wang (SCE) | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14 - Updated savings and scaling factors using DEER 2014 values - Split measures into the <55 kBtuh and 55-64 kBtuh ranges - Added SEER 14.5 HP measures (SCE13HC019 was merged into this work paper) - Added SEER 18 AC and HP measures - Added the Com building type for PG&E - - Added all building types available from DEER that were not already present in the work paper |
| 4 | 1/1/2015 | Jason Wang (SCE) | Updated work paper for DEER 2015 measures and federal code 430.32: - Most measures now using DEER savings directly; SEER 15, 16, 17, and 18 measures were added to DEER 2015. - Removed SEER 14 AC, SEER 14 HP, and SEER 14.5 HP measures due to code and DEER direction. - Created new capacity ranges to accommodate EER and two-speed fan requirements. These align with DEER measures. - Used scaling of DEER measures to determine SEER 18 Packaged HP savings. - Calculated To Code savings using DEER measures (RET savings minus ROB savings). - Updated costs with values from WO017. |
| 5 | 10/14/2015 | Ryan Cho (SCE) | - Updated work paper for DEER 2016 NTG value, NTG value changed from 0.85 to 0.75 - Updated WP template and Calculation template - Removed Agricultural, Food Store, Health/Medical – Clinic, Industrial, Misc-Commercial, Transportation – Communication – Utilities Building Types - Reporting period, effective 1/1/16 - Updated costs with values from READI |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Air cooled air conditioning or heat pump units with cooling capacities less than 65 kBtuh, for use in non-residential buildings, meeting the minimum efficiency requirements listed in Table under Efficiency Requirements below. |
| Existing Condition | Existing units identified through the HVAC optimization program only |
| Code/Standard | Air cooled air conditioning or heat pump units with cooling capacities less than 65 kBtuh, for use in non-residential buildings, meeting the federal minimum efficiency standard of 14 SEER. |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| N/A | N/A | AC-50375 | N/A | <55kBtuh 15 SEER (12 EER) Packaged Air Conditioner |
| N/A | N/A | AC-81566 | N/A | <55kBtuh 16 SEER (12.4 EER) Packaged Air Conditioner |
| N/A | N/A | AC-37735 | N/A | <55kBtuh 17 SEER (13 EER) Packaged Air Conditioner |
| N/A | N/A | AC-31588 | N/A | <55kBtuh 18 SEER (14 EER) Packaged Air Conditioner |
| N/A | N/A | AC-87532 | N/A | 55to65kBtuh 15 SEER (12 EER) Packaged Air Conditioner |
| N/A | N/A | AC-77878 | N/A | 55to65kBtuh 16 SEER (12.4 EER) Packaged Air Conditioner |
| N/A | N/A | AC-22408 | N/A | 55to65kBtuh 17 SEER (13 EER) Packaged Air Conditioner |
| N/A | N/A | AC-75087 | N/A | 55to65kBtuh 18 SEER (14 EER) Packaged Air Conditioner |
| N/A | N/A | AC-46105 | N/A | <45kBtuh 15 SEER (12.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-83486 | N/A | <45kBtuh 16 SEER (13 EER) Split System Air Conditioner |
| N/A | N/A | AC-26490 | N/A | <45kBtuh 17 SEER (13.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-50319 | N/A | <45kBtuh 18 SEER (14 EER) Split System Air Conditioner |
| N/A | N/A | AC-70613 | N/A | 45to55kBtuh 15 SEER (12.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-97648 | N/A | 45to55kBtuh 16 SEER (13 EER) Split System Air Conditioner |
| N/A | N/A | AC-66543 | N/A | 45to55kBtuh 17 SEER (13.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-96580 | N/A | 45to55kBtuh 18 SEER (14 EER) Split System Air Conditioner |
| N/A | N/A | AC-69747 | N/A | 55to65kBtuh 15 SEER (12.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-86967 | N/A | 55to65kBtuh 16 SEER (13 EER) Split System Air Conditioner |
| N/A | N/A | AC-61866 | N/A | 55to65kBtuh 17 SEER (13.5 EER) Split System Air Conditioner |
| N/A | N/A | AC-87169 | N/A | 55to65kBtuh 18 SEER (14 EER) Split System Air Conditioner |
| N/A | N/A | AC-97980 | N/A | <55kBtuh 15 SEER (12 EER) Packaged Heat Pump |
| N/A | N/A | AC-92105 | N/A | <55kBtuh 16 SEER (12.4 EER) Packaged Heat Pump |
| N/A | N/A | AC-59729 | N/A | <55kBtuh 17 SEER (13 EER) Packaged Heat Pump |
| N/A | N/A | AC-65475 | N/A | <55kBtuh 18 SEER (14 EER) Packaged Heat Pump |
| N/A | N/A | AC-99784 | N/A | 55to65kBtuh 15 SEER (12 EER) Packaged Heat Pump |
| N/A | N/A | AC-60134 | N/A | 55to65kBtuh 16 SEER (12.4 EER) Packaged Heat Pump |
| N/A | N/A | AC-65806 | N/A | 55to65kBtuh 17 SEER (13 EER) Packaged Heat Pump |
| N/A | N/A | AC-62068 | N/A | 55to65kBtuh 18 SEER (14 EER) Packaged Heat Pump |
| N/A | N/A | AC-73283 | N/A | <55kBtuh 15 SEER (12.5 EER) Split System Heat Pump |
| N/A | N/A | AC-89637 | N/A | <55kBtuh 16 SEER (13 EER) Split System Heat Pump |
| N/A | N/A | AC-53855 | N/A | <55kBtuh 17 SEER (13.5 EER) Split System Heat Pump |
| N/A | N/A | AC-61202 | N/A | <55kBtuh 18 SEER (14 EER) Split System Heat Pump |
| N/A | N/A | AC-62602 | N/A | 55to65kBtuh 15 SEER (12.5 EER) Split System Heat Pump |
| N/A | N/A | AC-71681 | N/A | 55to65kBtuh 16 SEER (13 EER) Split System Heat Pump |
| N/A | N/A | AC-94444 | N/A | 55to65kBtuh 17 SEER (13.5 EER) Split System Heat Pump |
| N/A | N/A | AC-89435 | N/A | 55to65kBtuh 18 SEER (14 EER) Split System Heat Pump |
| N/A | N/A | AC-67740 | N/A | <55kBtuh To Code Savings Portion Packaged Air Conditioner |
| N/A | N/A | AC-69545 | N/A | 55to65kBtuh To Code Savings Portion Packaged Air Conditioner |
| N/A | N/A | AC-50853 | N/A | <45kBtuh To Code Savings Portion Split System Air Conditioner |
| N/A | N/A | AC-56930 | N/A | 45to55kBtuh To Code Savings Portion Split System Air Conditioner |
| N/A | N/A | AC-75420 | N/A | 55to65kBtuh To Code Savings Portion Split System Air Conditioner |
| N/A | N/A | AC-83228 | N/A | <55kBtuh To Code Savings Portion Packaged Heat Pump |
| N/A | N/A | AC-73081 | N/A | 55to65kBtuh To Code Savings Portion Packaged Heat Pump |
| N/A | N/A | AC-53523 | N/A | <55kBtuh To Code Savings Portion Split System Heat Pump |
| N/A | N/A | AC-98919 | N/A | 55to65kBtuh To Code Savings Portion Split System Heat Pump |

Implementation Requirements

For early retirement offerings, identified as “To Code Savings Portion” measures in this work paper:

- These Early Retirement measures will only claim the savings remaining after the HVAC Upstream Program has already claimed the Replace on Burnout (ROB) and New Construction (NEW) savings.

- Initial leads for the program will be generated from participants in the Quality Maintenance (QM) and Quality Renovation (QR) Programs. Maintenance records and analyses performed for the QM and QR program will be collected to help verify unit operation. Additional information on existing EER and operating efficiency may be collected on some applications to help document the existing baseline.

- Pre-inspection and verification will be used to ensure that the proper application type is selected. The program will require pre-inspections on 75% of installations for the first 3 months but will work toward a 100% inspection rate. Pre-inspections will inspect nameplate information such as manufacturing year, visual verification of unit operation, and/or perform verification readings including: amperage, supply air temperature, outdoor air temperature, and mixed air temperature. After 3 months, the program will adjust the inspection percentage based on the pass-fail rates. Two rebates will be paid for Early Retirement installation, but savings will only be claimed once.

Documentation Requirements

Certain evidence must be provided to participate in the early retirement program, including:

- Pre-inspection data to evaluate that the units are still operating

- Customer statement that the existing equipment is still in proper working condition and will continue to operate at least one year

- The evidence below will be asked to be provided by the contractor or customer, but because it may not always be available, will not be a requirement for program participation:

  - Make, model and serial number of existing equipment

  - Records of ongoing equipment maintenance and performance

  - Existing equipment installation dates and invoices

- The above evidence, any other evidence, and the sampling rate of this evidence, will be used to demonstrate the preponderance of evidence of program-induced early retirement through ongoing EM&V coordination. Other evidence may include emails, notes, and customer statements that help demonstrate evidence of how the early retirement program accelerated the early retirement of the existing unit and if any additional drivers other than energy efficiency helped influence the decision for early retirement.

Efficiency Requirements

The minimum tier efficiency requirements are listed in the table shown below. Tier 1 specifications are derived from the Tier 2 CEE Commercial Unitary Air Conditioner Specifications. Tiers 2, 3 and 4 have been added to promote higher efficiency units offered by the HVAC industry.

Minimum Efficiency Requirements

|  | Program Tier | Minimum SEER | Minimum EER |
| --- | --- | --- | --- |
| Packaged Air Conditioner | Code | 14.0 | 11.6 |
|  | Tier 1 | 15.0 | 12.0 |
|  | Tier 2 | 16.0 | 12.4 |
|  | Tier 3 | 17.0 | 13.0 |
|  | Tier 4 | 18.0 | 14.0 |
| Split System Air Conditioner | Code | 14.0 | 12.0 |
|  | Tier 1 | 15.0 | 12.5 |
|  | Tier 2 | 16.0 | 13.0 |
|  | Tier 3 | 17.0 | 13.5 |
|  | Tier 4 | 18.0 | 14.0 |
| Packaged Air Cooled Heat Pump | Code | 14.0 | 11.6 |
|  | Tier 1 | 15.0 | 12.0 |
|  | Tier 2 | 16.0 | 12.4 |
|  | Tier 3 | 17.0 | 13.0 |
|  | Tier 4 | 18.0 | 14.0 |
| Split System Air Cooled Heat Pump | Code | 14.0 | 12.0 |
|  | Tier 1 | 15.0 | 12.5 |
|  | Tier 2 | 16.0 | 13.0 |
|  | Tier 3 | 17.0 | 13.5 |
|  | Tier 4 | 18.0 | 14.0 |

In order to qualify for the program, units must meet either the SEER or EER requirement; units are not required to meet both specifications.

Eligibility Requirements

- All unitary DX equipment is eligible. Central systems and DHW systems are not eligible.

- Replacement must be like for like: HP for HP; AC-only for AC-only.

- Specifically under the Early Retirement program applicability, only contractors actively participating in the HVAC Optimization Program are allowed to participate in this Program.  Part of the application process will include verification procedures for ensuring that equipment is installed and operational.

- Retrofitted HVAC equipment must have cooling capacity (e.g., Btu/h) within +/- 5% of existing equipment OR contractor must provide a load calculation verifying that the new unit is sized correctly for the load.

- All non-residential building types and vintages are eligible for the upstream rebate.

## 1.2 Technical Description

A unitary system is an air conditioning system that cools one or a few spaces, in contrast to a centralized system where a chiller serves most or all of the building. Unitary systems use direct expansion, are usually factory designed, and are available as packaged or split systems for commercial use. A split system consists of an indoor unit (fan, cooling coil, heating elements, filter) connected by refrigerant piping to an outdoor unit (fan, compressor, condenser, expansion valve). A packaged system incorporates all the equipment into a single unit that is typically mounted on the roof. Heat pumps allow the refrigeration cycle to run in reverse and can therefore provide heating or cooling to the conditioned space.

## 1.3 Installation Types and Delivery Mechanisms

The delivery method is:

Upstream Programs – Up-Stream Incentive

The install type is:

Replace on Burnout (ROB)

New Construction (NEW)

Retrofit (RET)

Additionally, an early retirement measure will also be offered through the HVAC optimization program as Retrofit (RET). In this delivery approach, units identified through the HVAC optimization program as still functional, but needing replacement, will be retired prematurely. The program will provide incentives to the contractor for this to occur.

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| New Construction (NEW/NC) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit or Early Replacement (RET/ER) | Above Customer Existing | Above Code or Standard | RUL | EUL-RUL |
| Retrofit First Baseline Only (REF) | Above Customer Existing | N/A | EUL | N/A |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Appliance Turn-in and Recycling | The program motivates customers, through financial incentives, to recycle appliances that are functional but inefficient. This prevents the continued use of those appliances, by both the current owner and potential future owners. |
| Audit - Information - Testing Services | The program performs a free assessment of a customer’s facility and provides the customer with information and guidance on energy efficiency opportunities. |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |
| Partnership | The program implements projects through a partnership between the utility and an institutional, government, or community-based organization. |
| Up-Stream Programs | See Up-Stream Incentive in the Incentive Method Descriptions table. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Exchange - Replacement | The utility program holds events where customers can trade functional equipment for similar but more energy efficient equipment, free of charge. |
| Giveaway | The program provides customers with energy efficiency equipment or services for free. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |
| On-bill Finance – Loan (OBF) | The program offers financing for the cost of an efficient measure as part of the utility bill. This can be an add-on option to an existing program or can serve as an organizing principle for its own program. |
| Up-Stream Incentive Up-Stream Buy Down | The program gives a financial incentive to an upstream market actor (manufacturer or distributor) to encourage the manufacture, provision, or distribution of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | Most measures are from DEER. SEER 18 Packaged HP measures are linearly scaled from SEER 16 and 17. To Code measures are derived using SEER 15 measures. |
| Scaled DEER measure | Yes |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | DEER 2016, READI v2.3.0 |
| Reason for Deviation from DEER | See Section 2 for details |
| DEER Measure IDs Used | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer, See Section 2 for details |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mHVAC-DX-up | All package and split system AC & HP replacements | Com | Com | PreRebUp | 0.75 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-airAC | Air Conditioners (air-cooled, split and unitary) | Com | HVAC | 15 | 5 |
| HVAC-airHP | Heat Pumps (air-cooled, split and unitary) | Com | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

### Code of Federal Regulations (10 CFR 430.32(c)):

Per Federal Register technical amendment to the Code of Federal Regulations [393], the SEER 14 standard will apply to conventional [single phase] central air conditioners and heat pumps manufactured on or after January 1, 2015:

### California Title 20 2015:

Appliance Efficiency Regulations [493] under California Code of Regulations Title 20, Section 1605.1 (c) (1) states “The EER, SEER, COP, HSPF, and SCOP, as applicable, of all central air conditioners, including computer room air conditioners, shall be not less than the applicable values shown in Tables C-2, C-3, C-4, C-5, and C-6.”

### California Title 24 2013:

Title 24 [355] does not address the measures in this work paper; it provides requirements for unitary AC and HP units ≥ 65k Btu/h.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Code of Federal Regulations | 10 CFR 430.32(c)(3), (5) | January 1, 2015 |
| Title 20 (2015) | Section 1605.1(c)(1) Table C-2 | January 1, 2016 |
| Title 24 (2013) | N/A | July 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

N/A

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

The following table indicates which measures are taken directly from or created with the DEER READI tool. Of the 45 measures in this work paper, 34 are directly from DEER.

READI Data Used

| Measure Code | Measure Name | READI Data |
| --- | --- | --- |
| AC-50375 | <55kBtuh 15 SEER (12 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer |
| AC-81566 | <55kBtuh 16 SEER (12.4 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer |
| AC-37735 | <55kBtuh 17 SEER (13 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer |
| AC-31588 | <55kBtuh 18 SEER (14 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer |
| AC-87532 | 55to65kBtuh 15 SEER (12 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer |
| AC-77878 | 55to65kBtuh 16 SEER (12.4 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer |
| AC-22408 | 55to65kBtuh 17 SEER (13 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer |
| AC-75087 | 55to65kBtuh 18 SEER (14 EER) Packaged Air Conditioner | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer |
| AC-46105 | <45kBtuh 15 SEER (12.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer |
| AC-83486 | <45kBtuh 16 SEER (13 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer |
| AC-26490 | <45kBtuh 17 SEER (13.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer |
| AC-50319 | <45kBtuh 18 SEER (14 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer |
| AC-70613 | 45to55kBtuh 15 SEER (12.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer |
| AC-97648 | 45to55kBtuh 16 SEER (13 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer |
| AC-66543 | 45to55kBtuh 17 SEER (13.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer |
| AC-96580 | 45to55kBtuh 18 SEER (14 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer |
| AC-69747 | 55to65kBtuh 15 SEER (12.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer |
| AC-86967 | 55to65kBtuh 16 SEER (13 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer |
| AC-61866 | 55to65kBtuh 17 SEER (13.5 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer |
| AC-87169 | 55to65kBtuh 18 SEER (14 EER) Split System Air Conditioner | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer |
| AC-97980 | <55kBtuh 15 SEER (12 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf |
| AC-92105 | <55kBtuh 16 SEER (12.4 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf |
| AC-59729 | <55kBtuh 17 SEER (13 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf |
| AC-65475 | <55kBtuh 18 SEER (14 EER) Packaged Heat Pump | Scaled by multiplying NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf by the ratio between RE-HV-ResHP-18p0S-9p7H and RE-HV-ResHP-17p0S-9p4H. |
| AC-99784 | 55to65kBtuh 15 SEER (12 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf |
| AC-60134 | 55to65kBtuh 16 SEER (12.4 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf |
| AC-65806 | 55to65kBtuh 17 SEER (13 EER) Packaged Heat Pump | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf |
| AC-62068 | 55to65kBtuh 18 SEER (14 EER) Packaged Heat Pump | Scaled by multiplying NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf by the ratio between RE-HV-ResHP-18p0S-9p7H and RE-HV-ResHP-17p0S-9p4H. |
| AC-73283 | <55kBtuh 15 SEER (12.5 EER) Split System Heat Pump | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf |
| AC-89637 | <55kBtuh 16 SEER (13 EER) Split System Heat Pump | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf |
| AC-53855 | <55kBtuh 17 SEER (13.5 EER) Split System Heat Pump | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf |
| AC-61202 | <55kBtuh 18 SEER (14 EER) Split System Heat Pump | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf |
| AC-62602 | 55to65kBtuh 15 SEER (12.5 EER) Split System Heat Pump | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf |
| AC-71681 | 55to65kBtuh 16 SEER (13 EER) Split System Heat Pump | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf |
| AC-94444 | 55to65kBtuh 17 SEER (13.5 EER) Split System Heat Pump | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf |
| AC-89435 | 55to65kBtuh 18 SEER (14 EER) Split System Heat Pump | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf |
| AC-67740 | <55kBtuh To Code Savings Portion Packaged Air Conditioner | Derived from NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer |
| AC-69545 | 55to65kBtuh To Code Savings Portion Packaged Air Conditioner | Derived from NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer |
| AC-50853 | <45kBtuh To Code Savings Portion Split System Air Conditioner | Derived from NE-HVAC-airAC-Split-lt45kBtuh-15p0seer |
| AC-56930 | 45to55kBtuh To Code Savings Portion Split System Air Conditioner | Derived from NE-HVAC-airAC-Split-45to55kBtuh-15p0seer |
| AC-75420 | 55to65kBtuh To Code Savings Portion Split System Air Conditioner | Derived from NE-HVAC-airAC-Split-55to65kBtuh-15p0seer |
| AC-83228 | <55kBtuh To Code Savings Portion Packaged Heat Pump | Derived from NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf |
| AC-73081 | 55to65kBtuh To Code Savings Portion Packaged Heat Pump | Derived from NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf |
| AC-53523 | <55kBtuh To Code Savings Portion Split System Heat Pump | Derived from NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf |
| AC-98919 | 55to65kBtuh To Code Savings Portion Split System Heat Pump | Derived from NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf |

Since DEER does not have measures for 18 SEER packaged heat pumps, those savings were determined through scaling. As mentioned in the Commission Staff’s December 2011 Phase 2 Workpaper Review [D], the relative improvements between commercial equipment are assumed to be similar to the improvements between the same residential units. Therefore the savings for commercial 18 SEER Packaged HPs were calculated by multiplying the savings for commercial 17 SEER Packaged HPs by the ratio of residential 18 SEER and 17 SEER Packaged HPs.

Example: <55kBtuh 18 SEER (14 EER) Packaged Heat Pump, SCE, Assembly, CZ 06

DEER savings:

| EnergyImpactID | AStdWBkWh | AstdWBkW | AStdWBtherm |
| --- | --- | --- | --- |
| NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | 407 | 0.128 | -0.0148 |
| RE-HV-ResHP-17p0S-9p4H | 42.83 | 0.032 | -0.0012 |
| RE-HV-ResHP-18p0S-9p7H | 59.1 | 0.050 | -0.0012 |

kWh Savings = 407 * (59.1 / 42.83) = 562 kWh

kW Reduction = 0.128 * 0.050 / 0.032 = 0.196 kW

therm Savings = -0.0148 * -0.0012 / -0.0012 = -0.0148 therm (no change)

To Code Savings Portion Measures

The To Code Savings Portion measures in this work paper are the savings from retrofitting customer existing equipment (various SEER values) to 14 SEER code-compliant equipment. The savings were determined by subtracting the “AStdWB” savings from the “APreWB” savings for 15 SEER ACs and HPs. The result was the difference between customer existing equipment and 14 SEER equipment. The To Code measure savings are attributed to the early retirement mechanism (RET), while all other measures savings (ROB, NEW) are attributed to the Upstream HVAC program.

Example: <55kBtuh To Code Savings Portion Packaged Air Conditioner, SCE, Assembly, CZ 06

DEER savings:

| EnergyImpactID | APreWBkWh | APreWBkW | APreWBtherm | AStdWBkWh | AStdWBkW | AStdWBtherm |
| --- | --- | --- | --- | --- | --- | --- |
| NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | 560 | 0.293 | -3.12 | 129 | 0.0454 | -1.2 |

kWh Savings = 560 - 129 = 431 kWh

kW Reduction = 0.293 - 0.0454 = 0.2476 kW

therm Savings = -3.12 - (-1.2) = -1.92 therms

All savings values are listed in the calculation template [A] and the calculations are in Attachment 3[C].

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - Primary School | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - Secondary School | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - Relocatable Classroom | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - Community College | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - University | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Grocery | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Health/Medical - Hospital | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Health/Medical - Nursing Home | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Lodging - Hotel | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Manufacturing - Bio/Tech | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Manufacturing - Light Industrial | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Office - Large | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Office - Small | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Restaurant - Fast-Food | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Restaurant - Sit-Down | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Retail - Multistory Large | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Retail - Single-Story Large | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Retail - Small | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Storage - Conditioned | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Warehouse - Refrigerated | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |

# Section 4. Costs

## 4.1 Base Case Cost

All of the cost values are from the latest ex ante database through the READI v2.3.0. The labor rates and installation hours are from WO17 [475]. See the updated draft DEER2016 HVAC Cost Workbook [B] for details on the cost development.

## 4.2 Measure Case Cost

All of the cost values are from the latest ex ante database through the READI v2.3.0 except for SCE13HC012_05_M001 and SCE13HC012_05_M002. These new SCE cost IDs are created and the draft DEER2016 HVAC Cost Workbook is utilized for developing material costs. The labor rates and installation hours are from WO17 [475]. See the updated draft DEER2016 HVAC Cost Workbook [B] for details on the cost development.

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

The To Code costs will be reported for the early retirement mechanism (RET), while the other costs (ROB, NEW) will be reported for the Upstream HVAC program. For RET measures, the IMC is equal to $0 in order to avoid double counting the costs. See the calculation template [A] for details on the costs.

# Attachments

# References

| [355] |  |
| --- | --- |
| [393] |  |
| [475] |  |
| [493] |  |
| [A] | Attachment 1 |
| [B] | Attachment 2 |
| [C] | Attachment 3 |
| [D] | Attachment 4 |