Work Paper SCE13HC026

Revision 3

Southern California Edison

Window Evaporative Coolers

# At-a-Glance Summary

| Measure Codes | AC-29859 Window Evap Cooler |
| --- | --- |
| Measure Description | This work paper details the installation of window-mounted direct evaporative coolers to displace DX air conditioning (AC) systems in residential buildings. The base case is a residential building with a code compliant (13 SEER) DX central AC. In the measure case, one or more window evaporative coolers are added to the building. They do not replace the central AC. |
| Base Case Description | The base case is a residential building with a code compliant (13 SEER) DX central AC. |
| Units | Per installed evaporative cooler (per unit) |
| Energy Savings | See attached SCE15HC026 Res.xlsx |
| Full Measure Cost ($/unit) | See attached SCE15HC026 Costs.xlsx |
| Incremental Measure Cost ($/unit) | See attached SCE15HC026 Costs.xlsx |
| Effective Useful Life | 15 (HV-Evap) |
| Measure Installation Type | Retrofit – Add-On (REA) |
| Net-to-Gross Ratio | 0.55 (Res-Default>2) 0.85 (Res-Default-HTR-di) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 05/03/12 | Andres Fergadiotti/SCE | Updated to latest template “SP&TS Work Paper Template 2013 v0.1.docx” from WPSCREHC0026, Revision 0 |
| 1 | 01/30/13 | Jason Wang/SCE | Revised work paper in response to 2010-12 ED disposition. - Evap cooler now supplements existing system instead of replacing it - Work paper uses modified DEER savings - Install type changed to REA - Costs updated Added direct install, targeted to the hard to reach multifamily market. |
| 2 | 3/21/2014 | Ray Phillips PECI | Work paper updated for reporting period, effective 7/1/2014 – 12/31/2014. Updated to latest template “SCE EAS Work Paper Template 2013-14 v0.docx” from SCE13HC026, Revision 1 - Updated cost data to include costs associated with increased water use from operation of Window Evaporative Cooler - Updated ESAF and PDAF to reflect more current weather data - Updated energy savings values Updated demand impacts |
| 3 | 01/28/2016 | Andres Fergadiotti/SCE | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -Removed SCE building types -No value modifications |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the installation of window-mounted direct evaporative coolers to displace DX air conditioning (AC) systems in residential buildings. The base case is a residential building with a code compliant (13 SEER) DX central AC. In the measure case, one or more window evaporative coolers are added to the building. They do not replace the central AC.

For this measure, the occupant is expected to enable the window evaporative cooler for cooling the space. During very high ambient temperatures and/or humidity and in the event that the evaporative cooler cannot satisfy the cooling setpoint in the space, the occupant is expected to disable the evaporative cooler and enable the DX central AC.

Under specific ambient air conditions (specified in Section 2), direct evaporative cooling can provide sufficient cooling capacity and comfort while using much less energy than is required for traditional DX cooling. Since the evaporative coolers are meant to displace DX cooling, not replace it, the existing central AC must be turned off before evaporative cooling is used.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Window-mounted direct evaporative coolers |
| Existing Condition | DX air conditioning (AC) systems |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| N/A | N/A | AC-29859 | N/A | Window Evap Cooler |

The measure in this work paper is applicable for all Southern California Edison climate zones and all building types shown in table below.

This measure is part of the Home Energy Efficiency Rebate Program. To qualify for the program, a window evaporative cooler must meet the following requirements:

Installation requirements

- Be permanently installed.

- Have UL-recognized electrical components.

- Provide minimum airflow in accordance with the Air Movement and Control Association (AMCA), Standard 210:

Minimum Air Movement Requirements for Evaporative Coolers

| Minimum Air Movement (CFM/sf)* |  |  |
| --- | --- | --- |
| Climate Zones | Direct | Indirect/Direct |
| 1 – 9 | 1.5 | 1.2 |
| 10 – 13 | 3.2 | 1.6 |
| 14 – 15 | 4.0 | 2.0 |
| 16 | 2.6 | 1.3 |
| *If backup air conditioning is installed, the minimum air movement for all climate zones is 1.0 CFM/sf |  |  |

Capacity requirements

- Be able to provide cooling for up to 1000 square feet (sf).

- Have a rating of at least 3000 CFM. This is based on the following assumptions:

  - From the DEER 2005 Update Final Report [26]: The evaporative cooler cooling supply flow is three times the flow used for the baseline and code baseline buildings. The direct effectiveness is 0.85.

  - Assuming that a residential home requires 400 CFM/ton of cooling from a central AC system, an evaporative cooler will need to provide: 400 * 3 = 1200 CFM/ton. The window unit should be capable of cooling up to 1000 sf, so assuming 1.0 CFM/sf, a 1000 sf area will need: 1000 / 400 = 2.5 tons of cooling. This corresponds to: 2.5 * 1200 = 3000 CFM required for the window evaporative cooler.

Operational requirements

- This measure is eligible for single-family, multi-family, and mobile homes. It is assumed that the thermostat will have a cooling setpoint of 78°F as specified in the DEER single- and multi-family prototypes.

- Expected sequence of operation: When the building (space) temperature is in the order 78 degree F, it is assumed that the occupant will enabled the window evaporative cooler for cooling the space. In the event that the evaporative cooler cannot satisfy the cooling setpoint (e.g., during very high ambient temperatures and/or humidity), the occupant is expected to disabled the evaporative cooler and enabled the DX central AC.

- The evaporative cooler is expected to operate effectively when the dry bulb outside air temperature is 78°F or higher, the dew point is less than 55°F, and the air delivery temperature is less than or equal to 75°F.

- This measure assumes there will be no hard-wired “interlock” to control the operation of the DX and evaporative systems and/or the enabling/disabling of the systems. Therefore the actual system operation is dependent on human behavior and it can be difficult to predict. Four scenarios can occur: (a) only the evaporative cooler is on, (b) only the DX unit is on, (c) both are on, or (d) both are off.  The measure assumes that in most cases the two systems will not operate concurrently.  However, acknowledging the unpredictability of human behavior and the possibility of scenario (c) using more energy than in the base case, a Human Error Adjustment Factor is used to derate savings (see Section 2).

- Since evaporative cooling brings in outdoor air, this air needs a way to escape. When the evaporative cooler is on, the customer is required to open at least one exterior window or door in the dwelling. The customer can direct the flow of cooled air through proper selection of which window or door to open.

Unit quantity requirements

- For single family homes: If the home is larger than 1000 sf, two or more window units, each in a different room, can be installed. If the home is 1000 sf or less, only 1 unit is allowed.

- For multi-family: One window unit can be installed.

- For double-wide mobile homes: One window unit can be installed.

Water considerations

- Water usage: Evaporative coolers require a supply of water to keep the evaporative pads wet, and they can use 3–15 gallons/day depending on weather conditions, unit size, and water drainage [E]. This may be an issue in locations where the water supply is low.

- Supply water brought into the evaporative cooler contains minerals which may create scale or deposits on the pads. This will degrade pad efficiency and reduce their useful life. Periodic pad washing, rotation, and replacement are required to avoid pad degradation, air quality issues (pollen, dirt, dust, odor), and health issues (mold, mildew, bacteria).  Additionally there are several options for water treatment:

  - Install a bleed valve to flush out part of the recirculating water and lower mineral concentration. This uses a significant amount of water and therefore is not allowed for this measure.

  - Install a sump-dump (blow-down) system which periodically removes water and collected dirt from the sump.

  - Install another type of water treatment mechanism: electromagnetic, electrostatic, catalytic or mechanical.

- Wastewater from water treatment can be used for irrigation but may be an environmental concern if the mineral content is too high.

## 1.2 Technical Description

Direct evaporative cooling is achieved by passing outdoor air through a wetted media and distributing it into the indoor space. Evaporating water from this media removes sensible heat from the airstream, lowering its dry bulb temperature. At the same time, moisture is added to the airstream, raising its relative humidity, which can sometimes reach uncomfortable levels. However, for most conditions throughout a typical cooling season, direct evaporative cooling can adequately meet cooling loads and maintain reasonable humidity levels.

## 1.3 Installation Types and Delivery Mechanisms

The delivery mechanisms are Financial Support – Downstream Incentive – Deemed and Financial Support – Direct Install.

The Install Type is Retrofit – Add-on (REA).

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

A direct evaporative cooler (not window-mounted) measure is included in the 2014 DEER READI tool, version 1.0.5; the measure ID is D03-405. It is assumed that a window-mounted unit will have energy usage characteristics similar to that of a central direct evaporative cooling system, so D03-405 was used as a starting point for savings calculations. The DEER measure assumes HVAC unit replacement, but since the work paper measure supplements an existing HVAC unit, the DEER values are adjusted as indicated in Section 2 below.

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | Yes |
| Scaled DEER measure | Yes |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | No |
| DEER Version | 2005 |
| Reason for Deviation from DEER | See Section 2 |
| DEER Measure IDs Used | D03-405 Direct Evaporative Cooler |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | All | 0.55 |
| Res-Default-HTR-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |

This work paper includes measures that are offered via direct install activities into hard-to-reach (HTR) customer homes.  “Final Resolution E-4700”, dated December 18, 2014, defines specific criteria to classify customer homes as HTR. The “Required Corrections to Measure Level Input Parameters Identified by Commission Staff per D.14-10-046 Order Paragraph 16”, dated November 3, 2014, includes additional clarification for the geographic criteria.

SCE’s Multi-Family Energy Efficiency Rebate (MFEER) program addresses the ongoing concern with “split incentives”, where the residents are not the owners of the property, so they lack incentive to improve their energy usage. Similarly, the property owners do not live on-site and pay higher utility expenses due to inefficient appliances, thus lack any incentive to upgrade. The MFEER is designed to drive this customer segment toward participation by offering property owners a variety of energy efficiency measures and services.  The MFEER program will offer and track measure installations in both common and dwelling areas of multifamily complexes and common areas of mobile home parks and condominiums.  Measures offered via direct install activities in both common and dwelling areas of multifamily complexes and common areas of mobile home parks and condominiums will receive the HTR NTG.  Other measures in the MFEER program will receive default NTG (NTGR_ID: Res-Default>2), unless otherwise specified in DEER.

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HV-Evap | Window Evaporative Cooler | Residential | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

Title 24 2013 [355] does not provide energy efficiency standards or energy design standards for this measure.

Title 20 2014 [422] covers test methods for packaged direct and direct/indirect evaporative coolers, but does not mention window evaporative coolers.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | N/A | N/A |
| Title 20 (2014) | N/A | N/A |
| DOE | N/A | N/A |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### .5.1 Study Title #1

N/A

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Calculation Formulas

The savings values are represented by the equations below:

Annual energy savings	= DEER 2014 kWh Savings * ESAF * HEAF

Demand reduction	= DEER 2014 kW reduction * PDAF * HEAF

Annual therm savings	= DEER 2014 therm savings * ESAF * HEAF

where:			DEER 2014 savings are from the READi tool v.1.0.5, measure D03-405

ESAF is the Energy Savings Adjustment Factor

PDAF is the Peak Demand Adjustment Factor

HEAF is the Human Error Adjustment Factor

Energy Savings Adjustment Factor (ESAF) and Peak Demand Adjustment Factor (PDAF)

The DEER measure assumes that the direct evaporative cooler operates year-round because it replaces the existing central AC. Since the window unit in this work paper displaces but does not replace the existing AC, it only operates part-time. The DX unit is used when the evaporative cooler is unable to satisfy the cooling load and/or when the ambient conditions are not ideal for evaporative cooling. Therefore the ESAF and PDAF are used to de-rate the DEER savings to account for the window unit’s part-time operation.

Derivation of ESAF and PDAF

The ESAF represents the percentage of the year during which evaporative cooling can be used most effectively. It varies by climate zone and is derived using a full year of Typical Meteorological Year 3 (TMY3) weather data [B]. The three simultaneous conditions under which evaporative cooling can be effective are:

- Dry bulb temperature (DBT) is greater or equal to 78°F.

It is assumed that evaporative cooling will be used to maintain comfort when the ambient DBT reaches or exceeds the DEER set point of 78°F.

- Dew point temperature (DPT) is less than 55°F.

To avoid condensation problems and high humidity levels, it is recommended that a direct evaporative cooler not be running if the dew point is 55°F or higher.

- The air delivery temperature (ADT) is less than or equal to 75 °F.

The chart in Figure 1 is a summary tabulation of air temperatures that a direct evaporative cooler can deliver, derived from the psychometric chart using an 85% approach to the wet bulb depression [E]. As indicated in the highlighted boxes, 75°F is estimated to be the highest deliverable temperature in the optimum conditions range.

Direct Evaporative Cooler Operating Range [E]

The following are the steps used to derive ESAF and PDAF from the TMY3 data:

- Determine the number of hours per year during which cooling is required (tcooling). This is done by counting the number of hours when the DBT is above 78°F.

- Calculate the achievable air delivery temperature (ADT):

  - The wet bulb temperature (WBT) is calculated from the DBT and relative humidity (RH), using the following equation [C]:

WBT=DBT*atan0.151977*RH+8.313659+atanDBT+RH-atanRH-1.676331+0.00391838*RH1.5*atan0.023101*RH-4.686035

  - The wet bulb depression (WBD) is calculated using the following equation:

WBD=DBT-WBT

  - The ADT can then be calculated using the DBT and WBD. Assuming an evaporative cooling system efficiency of 85%, the deliverable air temperature is the outside air dry bulb temperature minus 85% of the wet bulb depression [D].

ADT=DBT-(WBD*0.85)

- Calculate the number of hours per year during which the 3 direct evaporative cooling conditions are met (tdirectevap). This is done by filtering the TMY3 data for when DBT ≥ 78°F, DPT <55°F, and ADT ≤ 75°F.

- The ESAF is calculated as the ratio of the total cooling hours that may be satisfied by a direct evaporative cooler to the total number of hours in the year that may require cooling:

ESAF=tdirectevaptcooling

- Similarly, the PDAF is calculated as the ratio of the total cooling hours that may be satisfied by a direct evaporative cooler during the 9-hour three-day DEER peak period (tdirectevap,peak) to the whole 9 hours. For example, climate zone 6 would require that September 1st-3rd be checked between the hours of 2:00 p.m. and 5:00 p.m.

PDAF=tdirectevap,peak9 hours

The calculated ESAF and PDAF for each CZ are shown in table below. For reference, the 1% dry-bulb and 1% mean coincident wet-bulb temperatures are also included, from the ASHRAE Fundamentals Handbook 2009 [F]. A 1% temperature means that those temperatures are not exceeded for more than 1% of the year. Evaporative cooling is most effective in hot, dry desert areas such as climate zones 14 and 15.

ESAF and PDAF Summary Table

| CZ | ESAF | PDAF | 1% Dry-bulb temperature | 1% Mean coincident wet-bulb temperature | Weather station |
| --- | --- | --- | --- | --- | --- |
| 6 | 44% | 56% | 80.4 | 64.7 | LA Intl AP |
| 8 | 31% | 33% | 89.9 | 69.2 | Tustin MCAF |
| 9 | 27% | 0% | 94.6 | 68.3 | Burbank AP |
| 10 | 49% | 0% | 97.4 | 69.1 | Riverside Muni |
| 13 | 65% | 0% | 101.1 | 70.0 | Fresno Yosemite Intl AP |
| 14 | 88% | 100% | 99.8 | 65.0 | Lancaster Fox Field |
| 15 | 60% | 11% | 109.0 | 72.2 | Palm Springs Intl |
| 16 | 95% | 100% | 88.0 | 61.0 | Mount Shasta |

The spreadsheet used for deriving ESAF and PDAF (“Weather Data - ESAF and PDAF - REV 2 WDEC.xlsx”) is too large to attach to this work paper and is therefore available from SCE upon request.

ESAF and PDAF Calculation (CZ 13)

| Climate Zone | 13 |
| --- | --- |
| Energy Savings Adjustment Factor (ESAF) | 65% |
| Peak Demand Adjustment Factor (PDAF) | 0% |
| Number of hours DBT is >= 78F [# of cooling hours per year] | 1990 |
| Number of hours DBT is >= 78F, DPT is < 55F, and ATD is <= 75F [# of cooling hours by Evap Cooler per year] | 1293 |
| Peak Period Month | 7 |
| Peak Period Start day | 8 |
| # of Peak Demand Hrs | 0 |

Human Error Adjustment Factor (HEAF)

This measure requires that only one mechanical system at a time can operate, and this will be made clear to the customer. However, the customer may forget to do so and end up operating both DX and evaporative systems simultaneously. Therefore, a human error adjustment factor is required to de-rate savings. As there have been no studies performed to measure this particular factor, the HEAF will be arbitrarily set at 75% until a study yields a more conclusive value. This implies that up to 25% of the savings will be lost due to non-ideal operation of the evaporative cooler and DX system.

Example Calculation

The DEER 2014 savings for the Direct Evaporative Cooler measure in SFM, CZ06 are:

DEER kWh savings: 182 kWh

DEER kW reduction: 0.773 kW

DEER therm savings: -28.3 therms

Using the calculations formulas shown at the beginning of Section 2:

kWh savings: 182 kWh * 0.444 ESAF * 0.75 HEAF = 60.67 kWh

kW reduction: 0.773 kW * 0.5556 PDAF * 0.75 HEAF = 0.3221 kW

therm savings: -28.3 therms * 0.444 ESAF * 0.75 HEAF = -9.43 therms

The magnitude of negative therm savings within DEER seems excessive for a measure that provides cooling during the summer only, but were applied to the calculations.

The following table indicates which measures are taken directly from or created with the DEER READI tool.

READI Data Used

| Measure Code | Measure Name | READI Data |
| --- | --- | --- |
| AC-29859 | Window Evap Cooler |  |

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Residential Single Family | DEER:HVAC_Eff_AC | RES |
| Residential Multi-Family | DEER:HVAC_Eff_AC | RES |
| Residential Mobile Home - Double-Wide | DEER:HVAC_Eff_AC | RES |

# Section 4. Costs

## 4.1 Base Case Cost

For REA measures, base case cost is not used.

## 4.2 Measure Case Cost

Measure equipment cost was determined by averaging the cost of several window evaporative coolers from 3000 to 3500 CFM, from multiple online retailers: $578.69. A cost totaling $134.46 was added to the Measure Cost to account for additional water usage typically associated with evaporative cooling measures. The water costs represent an average over the life of the measure, including inflation, from a sampling of water rate sheets from climate zones 6, 9 and 15. See Attachment “SCE15HC026 Costs.xlsx” for details. The labor cost was taken from RS Means: $177.00 [A]. See Attachment “SCE15HC026 Costs.xlsx” for details. There will be maintenance costs associated with the measure primarily due to build-up of sediment and minerals. Evaporative coolers need a major cleaning every season and may need routine maintenance several times during the cooling season

Water Cost Calculations

| Climate Zone | Annual Cooling Load (Btu) | ESAF | BTU/lb water evaporated | lb water/ft3 | Water Rates/100 ft3 | Total |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | 8317221 | 44% | 1000 | 62.4 | 4.35 | $2.55 |
| 9 | 17584000 | 27% | 1000 | 62.4 | 2.96 | $2.25 |
| 15 | 77573000 | 60% | 1000 | 62.4 | 2.24 | $16.71 |
| Average |  |  |  |  |  | $7.17 |
| Added water costs over life of measure (15 yr Measure Life; 1.5% annual rate of inflation) |  |  |  |  |  | $134.46 |

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| AC-29859 | REA | $890.15 | $890.15 | N/A |

# Attachments

1.

2.

3.

4.

5.

6.

7.

8.

# References

[26]

[355]

[422]

[A] RS Means Mechanical Cost Data 2010, 33rd Annual Edition, Reed Construction Data, Inc.

[B] National Solar Radiation Data Base. http://rredc.nrel.gov/solar/old_data/nsrdb/1991-2005/tmy3/

[C] Stull, Roland – University of British Columbia, Vancouver, British Columbia, Canada. (2011). Wet-Bulb Temperature from Relative Humidity and Air Temperature.

[D] Bucklin, R. A., Leary, J. D., McConnell, D. B., & Wilkerson, E. G. (1993, December 01). Publication #CIR1135. Fan and pad greenhouse evaporative cooling systems. Retrieved from http://edis.ifas.ufl.edu/ae069

[E] California Energy Commission, Consumer Energy Center. (2013, April 26). Evaporative cooling. Retrieved from http://www.consumerenergycenter.org/home/heating_cooling/evaporative.html

[F] American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc. (2009). 2009 ASHRAE Handbook, Fundamentals. Appendix: Design Conditions for Selected Locations. Atlanta, GA: ASHRAE