Work Paper SCE13HC029

Revision 4

Southern California Edison

Residential HVAC Quality Maintenance

# At-a-Glance Summary

| Measure Codes | AC-44078, AC-56069, AC-95345, AC-94699, AC-60036, AC-21964, AC-16390 |
| --- | --- |
| Measure Description | HVAC Quality Maintenance treatments: Refrigerant charge adjustment, condenser coil cleaning, evaporator coil cleaning, air flow adjustment, duct seal medium to low, duct seal high to low, and design capacity sizing |
| Base Case Description | Central air-cooled direct expansion cooling and gas heating without adequate Quality Maintenance |
| Units | Ton |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 5 years (HV-ResRCx) |
| Measure Installation Type | Retrofit Add-On (REA), Replace-on-Burnout (ROB) |
| Net-to-Gross Ratio | Res-Default>2 (0.55) Res-sAll-mDuctSeal (0.78) Res-sAll-mHVAC-RCA (0.78) Res-Default-HTG-di (0.85) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 05/29/2012 | Janice Peterson, PECI | Original work paper |
| 1 | 12/04/2013 | Ryan Cho/SCE | In accordance with the Energy Division’s disposition [34], the following revisions are incorporated into this workpaper. - Revised all Unit Energy Savings (UES) values. - Updated the EUL value to 5 years. Updated the solution codes. |
| 2 | 12/31/2013 | Yun Han/SCE | - Updated to latest WP template - Add Residential Mobile Home – Double-Wide building type - Add Direct Install Delivery & Incentive Method Update NTG for Direct Install and Downstream |
| 3 | 5/09/2014 | Andres Fergadiotti/SCE | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - Updated DMH savings Removed Brushless Direct Current Blower Motor measure, which is addressed in SCE13HC028 (Solution Code: AC-68273 ) |
| 3 | 7/30/2014 | Andres Fergadiotti/SCE | - The single Res HVAC QM measure was broken out into multiple measures, in alignment with PG&E. - Measure savings are from the 5/2/13 ED Res QM Disposition. - Some disposition savings were replaced with newer DEER2014 values: Res-RefrigCharge-wtd, Res-DuctSeal-HighToLow-wtd, and Res-DuctSeal-MedToLow-wtd - Added new measure “Design Capacity Sizing.” - Updated all costs |
| 4 | 2/3/2016 | Andres Fergadiotti/SCE | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -No value modifications -Added HTR program language -Remove irrelevant documentation/narrative supporting previous calculation methods |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the Residential HVAC Quality Maintenance (QM) measures for packaged and split system HVAC units. These treatments are related to ductwork and HVAC unit optimization.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Residential HVAC Quality Maintenance (QM) |
| Existing Condition | Residential HVAC – Standard Non-QM System |
| Code/Standard |  |
| Industry Standard Practice | (ACCA) Standard 4 for “Maintenance of Residential HVAC Systems” |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| N/A | N/A | AC-44078 | N/A | Refrigerant Charge Adjustment |
| N/A | N/A | AC-56069 | N/A | Condenser Coil Cleaning |
| N/A | N/A | AC-95345 | N/A | Evaporator Coil Cleaning |
| N/A | N/A | AC-94699 | N/A | Air Flow Adjustment |
| N/A | N/A | AC-60036 | N/A | Duct Seal Med to Low |
| N/A | N/A | AC-21964 | N/A | Duct Seal High to Low |
| N/A | N/A | AC-16390 | N/A | Design Capacity Sizing |

Residential Single Family, Multi-family, and Double-wide Mobile Homes in SCE’s climate zones that use central air-cooled direct expansion cooling and gas heating are eligible. The participant must have electricity distributed by Southern California Edison (SCE) to the installation service address. Additionally, the following prerequisites must be met before the Quality Maintenance measures can be implemented:

- Unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to airflow are completed and before refrigerant charge is tested and/or adjusted.

- Unit must be drawing power.

- Unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.

- Customer must agree to QM Service Agreement.

The 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing some or all of the QM treatments related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver 350 cfm/ton after the airflow treatments have been performed, refrigerant charge cannot be properly diagnosed, rendering the QM process incomplete and the savings in this work paper invalid.

If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per 2013 Title 24 Section 150.2(b), or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2013 Title 24 Section 150.2(b)1D [355].

The level of maintenance by technicians on a typical air conditioner unit is minimal with service being performed at an unacceptable level. This may eventually lead to unit failure and/or poor performance, forcing premature equipment replacement. In response to this problem, Air Conditioner Contractors of America (ACCA) developed Standard 4 for “Maintenance of Residential HVAC Systems” [1]. For the measures contained in this work paper, an assessment and report is required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop treatment recommendations.

## 1.2 Technical Description

Proper maintenance of the unit enables an air conditioner to operate at or near its optimal efficiency. The Quality Maintenance measures are treatments designed to increase the unit’s ability to deliver heating and cooling efficiently and to provide increased thermal comfort.  An example of a performance/parameter improvement is: Refrigerant Charge Adjustment improves EER and Cooling Capacity.  Treatments are further detailed in the report.

The Design Capacity Sizing measure, not included in the ED Disposition or DEER2014 database, is intended to address oversizing of the Design (Cooling) Capacity of the base case mechanical (HVAC) system, generally in the order of 20% over a properly sized mechanical system as documented and suggested in the SCE’s Residential Quality Installation workpaper (SCE13HC023). This is an ROB measure because the customer’s existing equipment has passed its useful life, and the customer has the opportunity to choose a properly sized system as the replacement.

## 1.3 Installation Types and Delivery Mechanisms

The delivery methods are:

- Financial Support – Downstream Incentive – Deemed

- Financial Support – Direct Install.

The install types are:

- Replace-on-Burnout (ROB) for Design Capacity Sizing

- Retrofit Add-on (REA) for the remaining measures

| Measure Code | Measure Name | Install Type |
| --- | --- | --- |
| AC-44078 | Refrigerant Charge Adjustment | REA |
| AC-56069 | Condenser Coil Cleaning | REA |
| AC-95345 | Evaporator Coil Cleaning | REA |
| AC-94699 | Air Flow Adjustment | REA |
| AC-60036 | Duct Seal Med to Low | REA |
| AC-21964 | Duct Seal High to Low | REA |
| AC-16390 | Design Capacity Sizing | ROB |

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER 2014 contains some of the QM treatments as standalone measures, with the assumption that all other features of the prototype are held constant at an energy efficient baseline; the standalone measures are: refrigerant charge and adjustment, duct sealing, refrigerant charge with duct sealing, and commercial condenser coil cleaning. To determine savings, DEER values were modified as shown in the 5/2/13 ED Residential HVAC QM Disposition.

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | Yes |
| Scaled DEER measure | No |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | Yes |
| DEER Version | DEER 2014 and 2011 per disposition |
| Reason for Deviation from DEER | DEER measures were modified as shown in the 5/2/13 ED Residential HVAC QM Disposition. |
| DEER Measure IDs Used | Res-RefrigCharge-wtd (sample) |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | All | 0.55 |
| Res-sAll-mDuctSeal | Duct Sealing | Res | Any | PreReb | 0.78 |
| Res-sAll-mHVAC-RCA | HVAC Maintenance: Refrigerant Charge Adjustment (RCA) | Res | Any | PreReb | 0.78 |
| Res-Default-HTG-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |

Multi-Family Energy Efficiency Rebate (MFEER) Direct Install Program

This work paper includes measures that are offered via direct install activities into hard-to-reach (HTR) customer homes.  “Final Resolution E-4700”, dated December 18, 2014, defines specific criteria to classify customer homes as HTR. The “Required Corrections to Measure Level Input Parameters Identified by Commission Staff per D.14-10-046 Order Paragraph 16”, dated November 3, 2014, includes additional clarification for the geographic criteria.

SCE’s Multi-Family Energy Efficiency Rebate (MFEER) program addresses the ongoing concern with “split incentives”, where the residents are not the owners of the property, so they lack incentive to improve their energy usage. Similarly, the property owners do not live on-site and pay higher utility expenses due to inefficient appliances, thus lack any incentive to upgrade. The MFEER is designed to drive this customer segment toward participation by offering property owners a variety of energy efficiency measures and services.  The MFEER program will offer and track measure installations in both common and dwelling areas of multifamily complexes and common areas of mobile home parks and condominiums.  Measures offered via direct install activities in both common and dwelling areas of multifamily complexes and common areas of mobile home parks and condominiums will receive the HTR NTG.  Other measures in the MFEER program will receive default NTG (NTGR_ID: Res-Default>2), unless otherwise specified in DEER.

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HV-ResRCx | Residential HVAC assessment report & maintenance contract | Res | HVAC | 5 | 1.7 |

### 1.4.2 Codes and Standards Analysis

The measure contained in this work paper is generally not governed by either state or federal codes and standards.

However, in the event that ducts are found to be so badly damaged that some or all of the ductwork must be replaced, the total length of the replaced ducts shall be less than 40 linear feet in total per 2013 Title 24 Section 150.2(b) 1D, or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2013 Title 24 Section 150.2(b) 1D [355].

Title 24 does not deal with quality maintenance issues. The program requires the HVAC contractor to be license by the California State Licensing Board (CSLB) and the HVAC technicians to be EPA certified. Under state mechanical code, changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency are exempt from the requirement to obtain a mechanical permit.

In the 2013 California Building Code [462], regarding Section 1.8.4 Permits, Fees, Applications, and Inspections, a written construction permit shall be obtained from the enforcing agency prior to the erection, construction, reconstruction, installation, relocation, or alteration of any mechanical system.

Exceptions:

- Work exempt from permits as specified in Chapter 1, Administration, Division II, Sections 112.2 through 112.2.3 of this code.

- Changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 Part 6 (2013) | Section 150.2(b) 1D | July 1, 2014 |
| Title 24 Part 2 (2013) | Section 1.8.4 | January 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

This work paper uses modified DEER savings, so no non-DEER studies were used in determination of the savings.

### 1.5.1 Study Title #1

N/A

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Energy savings and demand reduction are based on the May 2, 2013 Energy Division Workpaper Disposition for Residential Quality Maintenance:

“2013_2014_ResHVACQMWorkpaperDisposition_2May2013.xlsx” (Attachment 2) [367]. For the following measures, newer DEER savings became available after the disposition was issued, so those more recent values were used instead: Res-RefrigCharge-wtd; Res-DuctSeal-HighToLow-wtd; and Res-DuctSeal-MedToLow-wtd.  Attachment 3 contains the revised calculations with DEER 2014 data.

The Design Capacity Sizing measure was not included in the Disposition or DEER 2014, so savings were estimated as a fraction of the total (lumped) energy and demand savings documented in the Disposition.  Expected Incidence Rate and Installation Rate values for this measure were conservatively estimated as 0.35 and 0.45 respectively with a calculated adjuster of: 0.35 * 0.45 = 0.1575. See Attachment 3 for all calculations.

Example for Single Family Home in climate zone 6:

If the sum of the RCA, Coil Cleaning, Air Flow, and Duct Sealing measures is 9.96 kWh, then the Design Capacity Sizing savings is: 0.1575 * 9.96 = 1.57 kWh.

All measures are anticipated to be updated in the near future using best available data and/or WO32 HVAC Impact Evaluation findings.

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Residential Single Family | DEER:HVAC_Eff_AC | RES |
| Residential Multi-Family | DEER:HVAC_Eff_AC | RES |
| Residential Mobile Home - Double-Wide | DEER:HVAC_Eff_AC | RES |

# Section 4. Costs

## 4.1 Base Case Cost

The base case is the customer’s existing equipment; therefore the base case cost is $0.

## 4.2 Measure Case Cost

### Measure costs are first calculated per household and then divided by a climate-specific tonnage to determine per-ton costs.

### 4.2a Refrigerant Charge Adjustment

DEER 2008 [215] provides per-ton costs for the following:

- Increase Refrigerant Charge - Typical (< 20% rated charge)

- Increase Refrigerant Charge - High (>= 20% rated charge)

- Decrease Refrigerant Charge - Typical (< 20% rated charge)

- Decrease Refrigerant Charge - High (>= 20% rated charge)

These costs are weighted based on PG&E’s 2010 RCA participant data [13] and multiplied by 3.27 tons/household to come up with single per-ton costs of $34.86 for material and $120.46 for labor; it is assumed that this distribution is typical for California.

2010 PG&E RCA Program distribution on percentage charge

| 2010 PG&E RCA program distribution |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| RCA Percent Charge | Distribution Count | Category | Percentage of Total | DEER 2008 Cost Case | Material Cost | Labor Cost |
| 150.00% | 16 | >=20% Over | 2.05% | Decrease Refrigerant Charge - High (>= 20% rated charge) | $10.04 | $36.82 |
| 140.00% | 177 |  |  |  |  |  |
| 120.00% | 8 |  |  |  |  |  |
| 119.99% | 628 | <20% Over | 29.47% | Decrease Refrigerant Charge - Typical (< 20% rated charge) | $5.58 | $36.82 |
| 110.00% | 2257 |  |  |  |  |  |
| 100.10% | 0 | N/A | N/A | N/A |  |  |
| 100.00% | 221 | <20% Under | 57.76% | Increase Refrigerant Charge - Typical (< 20% rated charge) | $11.55 | $36.82 |
| 99.90% | 3218 |  |  |  |  |  |
| 90.00% | 2127 |  |  |  |  |  |
| 80.99% | 88 |  |  |  |  |  |
| 80.00% | 880 | >=20% Under | 10.72% | Increase Refrigerant Charge - High (>= 20% rated charge) | $19.93 | $36.82 |
| 60.00% | 84 |  |  |  |  |  |
| 50.00% | 34 |  |  |  |  |  |
| 40.00% | 51 |  |  |  |  |  |

### 4.2b Duct Sealing

DEER 2008 provides identical per-household costs for the following:

- Duct Sealing (Total Leakage Reduced from 24% of AHU flow to 12%)

- Duct Sealing (Total Leakage Reduced from 40% of AHU flow to 12%)

Since the QM program will not perform diagnostic testing on the customer’s duct system, only duct sealing will be completed by participating contractors/technicians. Mike Yim [14] of Summit Blue Consulting estimated one hour of labor for the duct diagnostic testing. The DEER cost is based on 6 man hours, so 1 hour is subtracted out to yield $46.46 for material and $368.23 for labor.

### 4.2c Condenser and Evaporator Coil Cleaning

The DEER 2008 per-household cost for cleaning condenser coils is $0.00 for material and $114.15 for labor. It is assumed that the cost is the same for cleaning condenser and evaporator coils.

### 4.2d Air Flow Adjustment

It is assumed that the per-household cost for an air flow adjustment is the labor cost of an air balance on a package rooftop AC unit, which is $415.00 from RS Means 2010 Building Construction Data [463].

### 4.2e Design Capacity Sizing

It is assumed that the per-household cost for design capacity sizing is the labor cost involved with performing a residential load calculation (e.g. Manual J). Using the DEER default labor rate of $67.88 and an estimated 4 hours for the calculations, the cost is $271.52.

### 4.2f Cost Permutation by Climate Zone

The per-household costs are divided by climate-specific average tonnages from DEER to determine individual costs per climate zone. The following is an example for refrigerant charge adjustment:

Table 15 Refrigerant Charge Adjusment Costs

| CZ | Tons | Material Cost Per Household | Labor Cost Per Household | Material Cost Per Ton | Labor Cost Per Ton | Full Cost, GMC Per Ton |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | 3.35 | $22.66 | $78.30 | $6.76 | $23.37 | $30.14 |
| 8 | 3.12 | $22.66 | $78.30 | $7.26 | $25.10 | $32.36 |
| 9 | 3.48 | $22.66 | $78.30 | $6.51 | $22.50 | $29.01 |
| 10 | 3.59 | $22.66 | $78.30 | $6.31 | $21.81 | $28.12 |
| 13 | 3.33 | $22.66 | $78.30 | $6.80 | $23.51 | $30.32 |
| 14 | 4.24 | $22.66 | $78.30 | $5.34 | $18.47 | $23.81 |
| 15 | 4.62 | $22.66 | $78.30 | $4.90 | $16.95 | $21.85 |
| 16 | 3.3 | $22.66 | $78.30 | $6.87 | $23.73 | $30.59 |

All cost calculations are in Attachment 4.

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| DesignCapacitySizing | ROB | $88.79 | $88.79 | N/A |
| DuctSealHightoLow | REA | $133.27 | $133.27 | N/A |
| AdjustedRefrigerantCharge | REA | $49.04 | $49.04 | N/A |
| CondenserCoilCleaning | REA | $37.33 | $37.33 | N/A |
| DuctSealMedtoLow | REA | $133.27 | $133.27 | N/A |
| AirFlowAdjustment | REA | $135.71 | $135.71 | N/A |
| EvaporatorCoilCleaning | REA | $37.33 | $37.33 | N/A |

# Attachments

# References

[215]

[355]

[367]

[462]

[463]

1. ACCA, “Maintenance of Residential HVAC Systems” - ANSI/ACCA Standard 4, 2008. https://www.acca.org/industry/ansi-standards

2. Itron, Inc. “2008 Database for Energy Efficiency Resources”, Version 2008.2.05, December 2008. http://www.deeresources.com/

3. Database for Energy Efficiency Resources (DEER) Single Family Prototype Input File. http://www.doe2.com/download/DEER/MAStool/

4. DPL – Decision Programming Language, Release 7.00.20, Copyright 2003-2010 by Syncopation software, Inc http://www.syncopation.com/?gclid=CJXd6Nfp1qoCFVMZQgodwHBO7w

5. Robert Mowris & Associates, Anne Blankenship, and Ean Jones. “Field Measurements of Air Conditioners With and Without TXVs”, paper for 2004 ACEE Summer Study Proceedings, 2004.

6. 2008 Building Energy Efficiency Standards for Residential and Nonresidential Buildings, SCE ref. 208.

7. Itron, Inc. “DEER NTG Values – 16 February 2009 Supplemental 2009-2011 Application Filings – Updated DEER NTGR Values – 053008.spreadsheet”, October 2008. http://deeresources.com/index.php?option=com_content&view=article&id=65&Itemid=57

8. Itron, Inc. “DEER EUL/RUL (Effective/Remaining Useful Life) Values, Updated 10 October 2008. http://www.deeresources.com/

9. eQUEST – Building Energy Use and Cost Analysis Software, developed by James J. Hirsch & Associates (JJH), version 3.64 was the latest release. http://www.doe2.com/

10. Energy Savings and EUL results for Quality Maintenance Measures, June 2011.

See SCE_QM_Savings at top of page.

11. DEER Single Family Prototypes with adjusted inputs.  Adapted from 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study, Final Report, prepared for Southern California Edison by Itron, Inc. with support from J. J. Hirsch and Associates, December 2005.

12. Measure Costs Analysis spreadsheet, January, 2012.

13. Mike Yim, Summit Blue Consulting, e-mail message on duct seal cost, July 25, 2011.

14. California Statewide Residential Appliance Saturation Study, http://websafe.kemainc.com/RASS2009/Default.aspx

15. Mowris personal communication via e-mail, May 11, 2011 at 1:37PM.

16. Mowris’ dataset of field measurements for 56 residential units 2004 and derivation of RIF,

17. MDSS_PGE_duct leak_Distribution_Analysis, June 2011

18. Tstat probability_v4, June 2011

19.  California Title 24 thermostat schedule for Residential, “2005 Residential ACM Manual.”

20. DEER SFRes Properties- Capacity-SEER, November2011

21. Vintage Distribution of Home Type, November 2011

22. Peng Xu, Joe Huang, Norman Miller, Nicole Schegel. “Effects Of Global Climate Changes On Building Energy Consumption and Its Implications on Building Energy Codes and Policy in California”, PIER Project Report.  September 2009.

23. Design Expert version 8.0.5 Stat Ease, Inc. 2021 East Hennepin Ave., Suite 480, Minneapolis, MN 55413. http://www.statease.com/dx8descr.html

24. Regressions, June 2011

25. Regression Check Results, June 2011

26. Architectural Energy Consultants (AEC). “2005 Residential ACM Manual.” CEC-400-2005-005-CMF. 2005http://www.energy.ca.gov/title24/2005standards/residential_acm/2005_RES_ACM_CHAPT4.PDF

27. California Energy Commission (CEC). “Nonresidential Alternative Calculation Method (ACM) Approval Manual.” CEC-400-2008-003-CMF. Section 2.5.2.10, Page 2-74. December 2008. http://www.energy.ca.gov/title24/2008standards/

28. Pigg, Scott, Central Air Conditioning in Wisconsin: A Compilation of Recent Field Research, ECW Report Number 241-1, May 2008.

29. Results are summarized in “Table 14 – Mean System Airflow…” of the PIER report Efficiency Characteristics and Opportunities for New California Homes by Proctor, Chitwood and Wilcox for the CEC.

30. KEMA, The Cadmus Group, and Summit Blue Consulting. “Evaluation Measurement and Verification of the California Public Utilities Commission HVAC High Impact Measures and Specialized Commercial Contract Group Programs.” CPUC. February 10, 2010.   http://www.cpuc.ca.gov/PUC/energy/Energy+Efficiency/EM+and+V/

31. Savings and weightings for EUL, December 2011.

32. Itron Inc.  2004-2005 Database for Energy Efficiency Resources (DEER) Update Study - Final Report -- Dec. 2005.  SCE Ref 26.

33. SCE Emails regarding SEER AFUE

34. Workpaper disposition for residential HVAC Quality Maintenance California Public Utilities Commission, Energy Division, May 2, 2013

Bracketed letters refer to the Glossary and bracketed numbers refer to the References and Endnotes