Work Paper SCE13HC031

Revision 2

Southern California Edison

Air Handler Variable Speed Motor

# At-a-Glance Summary

| Measure Codes | AC-65986 |
| --- | --- |
| Measure Description | Variable speed motors of 10HP or less |
| Base Case Description | Nonresidential air handler unit with a permanent split capacitor motor |
| Units | Per air handler unit |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 15 years (EUL ID: Motors-Fan) |
| Measure Installation Type | Replace on Burnout (ROB) |
| Net-to-Gross Ratio | 0.60 (DEER NTGR ID: Com-Default>2yrs) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 6/7/12 | Ricson Chude/SCE | Modifications from WPSCNRHC0031.0: - Savings based on PGECOHV125 R3 - Updated references and added applicable building types. |
| 1 | 7/3/14 | Bach Tsan/SCE, Jason Wang/SCE | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14 - Savings Based on PGECOHVC125 R4 |
| 2 | 1/22/16 | Ryan Cho/SCE | - New template update for 2016 program year - WP effective from 1/1/2016 thru 12/31/2016 - Removed SCE building types -No value modifications |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the installation of variable speed motors (VSM) of 10 hp or less in conjunction with a new air conditioner or heat pump, split or packaged unit air handler system. The base case for this measure is a nonresidential-type air handler with constant-speed fan motor.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Variable speed motors of 10HP or less |
| Existing Condition | Nonresidential air handler unit with a permanent split capacitor motor |
| Code/Standard | N/A |
| Industry Standard Practice | Nonresidential air handler unit with a permanent split capacitor motor |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | AC-65986 | H182 | Variable Speed Drive on Air Handler Motor Controls |

Measure Requirements

- Supply air blower with a new super-efficient direct replacement brushless permanent magnet blower motor with built-in controller must replace the existing permanent split capacitor motor.

- Motor must be 10 horsepower or less to be eligible for this rebate.

- Motor must be capable of plugging into existing control board.

- A variable frequency drive (VFD) is not eligible for this rebate.

## 1.2 Technical Description

Most existing small-scale commercial heating, ventilation and air conditioning (HVAC) blowers use low cost, low efficiency, single speed motors. These motors usually range in power between 0.3 hp and 2 hp. They turn on and off as required by thermostat control. This results in temperature variations and high energy consumption of the air handler motor.

Most major HVAC manufacturers are now offering variable-speed motor air handlers. These motors have integrated electronic controls that modulate the motor and fan speed based on the cooling or heating load of the system; they run at lower speed most of the time. These motors provide much more efficient operation, and improve the quality of the air distribution; however, they come at a price premium. Please note that variable speed motors are different from variable frequency drives (VFD); a VFD is an electronic drive added to a motor, while a multiple speed brushless motor is a motor with built-in speed-modulating capability.

This measure is designed to encourage the installation of such variable-speed motor air handlers in small commercial buildings. Because of the theoretical cubic relationship between fan power and fan speed, a small reduction in fan speed can result in large energy savings.

## 1.3 Installation Types and Delivery Mechanisms

The install type is:

Replace on Burnout (ROB)

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| New Construction (NEW/NC) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit or Early Replacement (RET/ER) | Above Customer Existing | Above Code or Standard | RUL | EUL-RUL |
| Retrofit First Baseline Only (REF) | Above Customer Existing | N/A | EUL | N/A |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

The delivery method is:

Financial Support / Downstream Incentive - Deemed

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER 2014 does not contain an exact match for this measure. The closest similar measure in DEER is for variable-frequency drives (VFDs), but the DEER measure for VFDs does not accurately represent the energy impacts for multi-speed motors applications. Therefore, custom temperature bin calculations have been used to estimate energy savings for multi-speed motors as explained in Section 2 of this workpaper.

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | No |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | N/A |
| Reason for Deviation from DEER | DEER does not contain this measure. |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | Any | 0.6 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| Motors-Fan | HVAC Fan Motors | Com | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

Title 20: These measures do not fall under Title 20 of the California Energy Regulations.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Federal Standards: The Energy Independence and Security Act (EISA) 2007 [226], effective December 19, 2010, mandates that motors manufactured or imported into the United States must meet at a minimum NEMA Premium™ Efficiency Levels. These levels are defined by the NEMA Standards Publication MG 1-2009, Revision 1-2010, Part 12, Page 35, Table 12-12 for motors 1 to 200 hp, design A&B. The standard applies to NEMA design A and B, integral horsepower, general purpose, ODP and TEFC motors (1200, 1800, and 3600 RPMs) from 1-200 hp.

The applicable codes and standards for these measures do not dictate associated hours of operation, measure or baseline costs, EUL, NTG, or in-service rate for the equipment involved.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Federal Standards | Section 313 | December 19, 2010 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

The following assumptions from other sources were used to estimate savings:

2009 ASHRAE Fundamentals Handbook [444]: Maximum cooling and heating loads were calculated based on climate-zone-specific design heating and cooling temperatures, obtained from climatic design information in the 2009 ASHRAE Fundamentals Handbook pages 14.18 and 14.19.

Energy Consumption Characteristics of Commercial Building HVAC Systems – Volume III: Energy Savings Potential [445]: Proposed case fan speed is equal to the load on the heating or cooling coil as a percentage of total capacity on the heating or cooling coils. Multiple speed brushless fan motors are 10% more efficient than the base case based on this DOE document on variable speed motors, page 4-24.

Hours of Operation: The assumed hours of operation are based on a building operating schedule of 8AM to 6PM Monday through Friday.

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Customized weather temperature bin simulations were used to estimate energy savings. The following assumptions were made:

- The electric savings were estimated using customized weather bin simulations [A]

- Air handler fan was assumed to be operating to meet cooling and heating loads.

- Cooling and heating loads were based on climate data and were assumed to vary linearly with outside air temperature.

- Base case fan runtime is equal to the load as a percentage of total capacity on the heating or cooling coils.

- Multiple speed fan motors behave similarly to fan motors equipped with variable frequency drives.

- Assumed 0.5-hp air handler motor and a supply air flowrate of 500 cfm [B].

BIN Simulation Inputs and Assumptions

## Energy Savings Estimation Methodologies

The following relationships between speed and energy consumption were used to determine baseline and measure case energy consumption. The energy savings is calculated as follows:

ES=ECB-ECM

Where:

ES 	= energy savings, kWh

ECB	= baseline energy consumption of the fan per temperature bin, kWh

ECM	= baseline energy consumption of the fan per temperature bin, kWh

Baseline energy consumption for each temperature bin is estimated as follows:

ECB=A+B*SpeedB+CSpeedB2*HP*C*PFeffB*AH

Where:

A	= 0.21976, constant, determined from the CEC Guidebook [E], no units

B	= -0.8748, constant, determined from the CEC Guidebook, no units

C	= 1.65259, constant, determined from the CEC Guidebook, no units

SpeedB	= baseline fan speed, % of nominal speed

HP	= 0.5, fan horsepower, hp

C	= 0.746, hp to kW conversion, kW/hp

PF	= 0.80, assumed power factor, no units

effB	= 0.77, baseline efficiency based on the NEMA efficiency tables [C], no units

AH	= annual operating hours for temperature bin, hours

The measure case energy consumption for each temperature bin is estimated as follows:

ECM=A+B*SpeedM+CSpeedM2*HP*C*PFeffM*AH

Where:

SpeedM= measure fan speed, % of nominal speed

effM	= 0.85, measure case efficiency assuming a 10% efficiency increase [445], no units

Example for CZ 13:

The baseline and measure energy consumption for one temperature bin is:

ECB=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.77*9

=3.6 kWH

ECM=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.85*9

=3.3 kWH

After summing energy consumption across all temperature bins, the energy savings is estimated as:

ES=391.6 kWh-235.8 kWh=155.7kWh

## Demand Reduction Estimation Methodologies

The following relationships between speed and energy consumption were used to determine baseline and measure case energy consumption. The energy savings is calculated as follows:

DR=MDB-MDM

Where:

DR	= demand reduction, kW

MDB	= baseline maximum demand, kW

MDM	= measure maximum demand, kW

The baseline demand for the highest temperature bin is estimated as follows:

MDB=A+B*SpeedB+CSpeedB2*HP*C*PFeffB

The measure case demand for the highest temperature bin is estimated as follows:

MDM=A+B*SpeedM+CSpeedM2*HP*C*PFeffM

Example for CZ 13:

MDB=0.21976+-0.8748*1.0+1.65259 1.02*.065259 .00.800.77

=0.387 kW

MDM=0.21976+-0.8748*1.0+1.65259 1.02*0.5*0.746*0.800.85

=0.351 kW

DR    =0.387-0.351=0.036 kW

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:HVAC_Split-Package_AC | NON RES |
| Education - Primary School | DEER:HVAC_Split-Package_AC | NON RES |
| Education - Secondary School | DEER:HVAC_Split-Package_AC | NON RES |
| Education - Community College | DEER:HVAC_Split-Package_AC | NON RES |
| Education - University | DEER:HVAC_Split-Package_AC | NON RES |
| Lodging - Hotel | DEER:HVAC_Split-Package_AC | NON RES |
| Lodging - Motel | DEER:HVAC_Split-Package_AC | NON RES |
| Manufacturing - Bio/Tech | DEER:HVAC_Split-Package_AC | NON RES |
| Manufacturing - Light Industrial | DEER:HVAC_Split-Package_AC | NON RES |
| Office - Large | DEER:HVAC_Split-Package_AC | NON RES |
| Office - Small | DEER:HVAC_Split-Package_AC | NON RES |
| Retail - Multistory Large | DEER:HVAC_Split-Package_AC | NON RES |
| Retail - Single-Story Large | DEER:HVAC_Split-Package_AC | NON RES |
| Retail - Small | DEER:HVAC_Split-Package_AC | NON RES |
| Storage - Conditioned | DEER:HVAC_Split-Package_AC | NON RES |
| Warehouse - Refrigerated | DEER:HVAC_Split-Package_AC | NON RES |

# Section 4. Costs

## 4.1 Base Case Cost

The base case cost is the average of cost estimates for three different air handler models, from two different HVAC installers. The installer estimates included both material and labor. This cost survey was performed in April 2008 and adjusted to account for inflation between 2008 and 2014 (8.6%). [D]

Base Case Cost=Average of Installer Estimates*(1+Inflation)

Base Case Cost=$1,460*1.086=$1,590

## 4.2 Measure Case Cost

The measure case cost is the average of cost estimates for two different air handler models, from two different HVAC installers. The installer estimates included both material and labor. This cost survey was performed in April 2008 and adjusted to account for inflation between 2008 and 2014 (8.6%). [D]

Measure Case Cost=$1,800*1.086=$1,950

Since the material and labor costs were not separated in the estimates from the HVAC installers, it is not assumed that the labor costs are the same in base and measure cases. Therefore, to determine climate zone-specific costs, the costs shown in Section 4.1 and 4.2 were multiplied by an average of the material and labor climate multipliers.

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs [D]

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| AC-65986 | ROB | $360 | $360 | N/A |

# Attachments

# References

[226]

[444]

[445]

[A] Attachment 2

[B] Attachment 3

[C] Attachment 4

[D] Attachment 5

[E] Attachment 6