Work Paper SCE13HC037

Revision 3

Southern California Edison Company

Comprehensive Commercial HVAC Rooftop Unit Quality Maintenance

# At-a-Glance Summary

| Solution and Measure Codes: | See Table 1 |
| --- | --- |
| Measure Description: | The QM+ and the QM+HP measures are applied to roof top units (RTU) that do not have an outside air economizer. The QM+Econo and QM+EconoHP measures are applied to RTUs that have an outside air economizer. Each measure consists of multiple treatments that could be applied to a roof top mounted packaged HVAC (RTU) system. |
| Base Case Description: | The base case is an RTU that has typical maintenance without the QM+ treatments. The typical level of maintenance of RTUs is assumed to be low, with only the minimum service being performed and units being run until they fail. |
| Units: | Per ton |
| Energy Savings: | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit): | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life: | 5 years [2013_2014-ComHVACQMWorkpaperDisposition_2May2013], but use DEER EUL ID: HVAC-QMPkg |
| Measure Application Type: | Retrofit Add-on (REA) |
| Net-to-Gross Ratio: | 0.6 (DEER NTGR ID: Com-Default>2yrs) |
| Important Comments: | This workpaper does not contain a data set in conformance with the 4/1/2014 Ex Ante Database Specification provided by the California Public Utilities Commission (CPUC) Commission Staff (CS); SCE will provide that data set separately. Workpaper update is intended to support program claims for the 1/1/2013 through 12/31/2014 reporting period. This update is necessary to address inconsistencies between the Program and workpaper in terms of (a) delivery method and (b) measure implementation approach with “aggregated” treatments. All energy and demand impacts in workpaper update reflect latest CPUC’s disposition values - 2013_2014-ComHVACQMWorkpaperDisposition_2May2013 Workpaper update includes scaling of energy and demand impacts to address 2013 Title-24 (CZ2010) weather, effective July 1, 2014 Workpaper update includes cost per CPUC’s 2010-2012 WO-017 Ex Ante Measure Cost Study Energy and demand impacts due to “DEER update for 2015 Codes” effective January 1, 2015, and CPUC’s HVAC Impact Evaluation Study – WO32 affecting 2015 reporting are excluded from this update. 2015 updates will be discussed in Q1/2015 with CS and appropriate updates will be made at that time. There will be at least one more future revision. |

# Document Revision History

| Revision # | Revision Date | Author (Affiliation) | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 05/08/012 | Sean Gouw/SCE | Original workpaper from WPSCNRHC0037.2, updated to new template |
| 1 | 12/11/013 | Andres Fergadiotti/SCE | Updated energy and demand savings in work paper per CPUC’s work paper disposition for Non-Residential HVAC Rooftop Quality Maintenance, dated May 2, 2013 |
| 2 | 4/17/2014 | Andres Fergadiotti/SCE | -Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. |
| 2 | 8/05/2014 | Andres Fergadiotti/SCE, Jason Wang/SCE | - The single Commercial HVAC QM measure was broken out into multiple measures. - Thermostat measures use “per-unit” as unit. - Measure savings are from the 5/2/13 ED Commercial QM Disposition. - Some disposition savings were replaced with newer DEER2014 values: Com-RefrigCharge-wtd - Changed delivery to Downstream Deemed only - Changed NTG to Com-Default>2yrs - Added costs |
| 3 | 12/26/2014 | Andres Fergadiotti/SCE | - Revised delivery method to “Midstream” to match that implemented by Program - Revised measure reporting to “Aggregated” treatments to match offering (and forecasting) used by Program - Revised reporting period to 1/1/2013 through 12/31/2014 - Revised cost per CPUC’s 2010-2012 WO-017 Ex Ante Measure Cost Study (By Ben Lipscomb/Clearesult) - Scaling of energy and demand impacts to include 2013 Title 24 (CZ2010) weather, effective July 1, 2014 - 2015 workpaper template update |

# Section 1: General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details four measures: Quality Maintenance Plus (QM+), Quality Maintenance Plus with Economizer (QM+Econo), Quality Maintenance Plus Heat Pump (QM+HP), and Quality Maintenance Plus with Economizer Plus Heat Pump (QM+EconoHP).  Each measure includes multiple treatments that could be applied to a roof top mounted, packaged HVAC (RTU) system. Heating is provided by either a gas furnace or an air source heat pump.

The QM+ measure and the QM+HP measure are applied to roof top units (RTU) that do not have an outside air economizer.  The base case is an RTU that has typical maintenance without the QM+ treatments.   The QM+Econo and QM+EconoHP measures are applied to RTUs that have an outside air economizer.   The base case is an RTU with an economizer that has typical maintenance without the QM+ treatments.  RTUs are primarily installed on low rise commercial building spaces.

The typical level of maintenance of RTUs is low, with only the minimum service being performed and units being run until they fail.  In response to this national problem, ANSI, ASHRAE, and ACCA developed Standard 180-2008, “Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems,” to “Establish minimum HVAC inspection and maintenance requirements that preserve a system’s ability to achieve acceptable thermal comfort, energy efficiency, and indoor air quality in commercial buildings.” [464] The implementation of the measures covered in this work paper will achieve Quality Maintenance (QM) as defined for RTUs in Standard 180.

The QM+ measures taken from Standard 180 include the following possible treatment groups and treatments:

- Airflow and Coil Cleaning

  - Evaporator and condenser coil cleaning

  - Airflow adjustment

- Refrigerant Adjustment

  - Refrigeration System Test

  - Refrigeration Charge Adjustment – Single and Multiple Compressors

- Schedule Management

  - Schedule Adjustment

  - Thermostat Replacement and Adjustment

- Economizer Service (QM+Econo and QM+EconoHP only)

  - Economizer Survey

  - Economizer Temperature High Limit Control

  - Economizer Controls Commissioning

  - Integrate Economizer: wiring

  - Integrate Economizer: wiring + thermostat

  - Economizer linkage Renovation

  - Economizer Renovation: Damper Motor

  - Economizer Renovation: Damper Motor and Controller/Sensor

By packaging treatments into the QM+, QM+HP, QM+Econo and QM+EconoHP measures, a program can be created to promote and deliver comprehensive HVAC RTU maintenance rather than single measures chosen at the contractor’s discretion.

Table 1: Measures and Codes

| Solution Code | Measure Code | Measure Name |
| --- | --- | --- |
| AC-28435 | N/A | Quality Maintenance plus (QM+) |
| AC-10999 | N/A | Quality Maintenance plus with Economizer (QM+Econo) |
| AC-78555 | N/A | Quality Maintenance plus Heat Pump (QM+HP) |
| AC-89101 | N/A | Quality Maintenance plus with Economizer Heat Pump (QM+EconoHP) |

Future workpaper updates will include finding from CPUC’s 2010-12 WO32 HVAC Impact Evaluation based on field observations of participating technicians in the HVAC commercial quality maintenance (CQM) programs.  WO32 includes findings for key quality maintenance treatments (and parameters) including but not limited to air-economizer performance pre/post measure as well as Refrigerant Charge Adjustment (RCA).

## 1.2 Technical Description

Standard 180 [464] is the basis for the QM measure and associated treatments.  Standard 180 was developed by ASHRAE, ACCA, and ANSI to improve the current inconsistent practices for inspecting and maintaining Heating Ventilating and Air-conditioning (HVAC) systems by providing a standard practice.  The general purpose of this Standard is to establish minimum HVAC inspection and maintenance requirements that preserve a system’s ability to achieve acceptable thermal comfort, energy efficiency, and indoor air quality in commercial buildings (i.e., not industrial or residential buildings of three or fewer stories above grade).

## 1.3 Application Types and Delivery Mechanisms

The delivery method is Midstream Programs/ Midstream - Incentive.  The install type is Retrofit add-on (REA).

The Program provides rebates to HVAC service contractors for performing the measures (with associated treatments) included in this workpaper. Contractors use the rebates to offset the costs of all measures (and treatments) necessary to bring a unit to an operational state in alignment with Program requirements.

Not included (and/or accounted) in this workpaper update - the program also provides Downstream incentives to customers to offset the cost of implementing a Standard 180 compliant maintenance plan through a 3 year service agreement with Program contractors. The downstream costs and incentives support Market Transformation efforts are outside the scope of this workpaper, which describes the Program’s approach for achieving energy savings and demand reductions.

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

Energy and demand impacts on this workpaper are based on the 5/2/2013 ED Disposition for Non-Residential HVAC Rooftop Quality Maintenance – Attachment 2, which are based on DEER savings and other best available data.

Table 2: DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Referenced versions of DEER and READI | N/A |
| Summary of deviation from DEER | DEER does not contain this type of measure. Energy and demand impacts per “5/2/2013 Non-Residential HVAC QM Disposition.” |
| DEER measures scaled? | No |
| DEER eQUEST prototypes used? | No |
| DEER operating hours used? | No |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

Table 3: Net-to-Gross Ratio

| NTGR ID | Description | Sector | BldgType | ProgDelivID | NTG |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | Any | 0.6 |

Note: Direct install measures that are not hard-to-reach will use the default NTG value.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.  Individual measure installation rates are factored into the savings values.

Table 4: Installation Rate

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Technology Fields

The Technology Fields were obtained from the Ex Ante Database Specification. The relevant Use Category, Use Sub-category, Technology Group, and Technology Type values for the measures in this work paper are in the table below.

Table 5: Technology Fields

| Classification | Value |
| --- | --- |
| Measure Case UseCategory | HVAC |
| Measure Case UseSubCats | Space Cooling |
| Measure Case TechGroups | HVAC Technology |
| Measure Case TechTypes | EER Rated Package Rooftop AC / EER Rated Package Rooftop HP |
| Base Case TechGroups | HVAC Technology |
| Base Case TechTypes | EER Rated Package Rooftop AC / EER Rated Package Rooftop HP |

Effective and Remaining Useful Life

The EUL value was obtained from the “2013_2014-ComHVACQMWorkpaperDisposition_2May2013”. The relevant EUL value for the measures in this work paper is in the table below.

Table 6: EUL and RUL

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-QMPkg | Air Conditioners (air-cooled, split and unitary) | Com | HVAC | 5 | N/A |

### 1.4.2 Codes and Standards Analysis

Title 24 (2013) [355] does not address maintenance issues.  Only licensed California contractors will participate in the program.  As required by the California State Licensing Board, contractors will be responsible for meeting all applicable codes and regulations including but not limited to the California Energy Standards – Title 24, CBC, CEC, CMC, and NEC.  In general, maintenance and repairs do not require permits.

In the 2013 California Building Code [462], regarding Section 1.8.4 Permits, Fees, Applications, and Inspections, a written construction permit shall be obtained from the enforcing agency prior to the erection, construction, reconstruction, installation, relocation, or alteration of any mechanical system.

Exceptions:

- Work exempt from permits as specified in Chapter 1, Administration, Division II, Sections 112.2 through 112.2.3 of this code.

- Changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency.

Table 7: Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 Part 2 (2013) | Section 1.8.4 | January 1, 2014 |

### 1.4.3 Non-DEER Study Review

This work paper uses modified DEER savings, so no non-DEER studies were used in determination of measure savings.

# Section 2: Calculation Methodology

The Base energy savings and demand reductions on measure (and treatments) are based on the May 2, 2013 Energy Division Workpaper Disposition for Non-Residential HVAC Rooftop Quality Maintenance – Attachment 2.   All measure impacts are documented and further detailed in Attachment 1.

This version of the workpaper scales energy (kWh) and demand (kW) impacts to accommodate new weather data requirements, e.g., 2013 Title-24 (CZ2010) weather.

The 2013 Title-24 building standards, effective July 1, 2014, specifies the use of new weather data (CZ2010).  The CZ2010 weather data was developed using meteorological data from 1998-2009 for 86 locations in California, combined with satellite-derived solar radiation.  DEER2014 uses the new weather data, along with new peak period definitions based on the new weather data, in the determination of all-weather sensitive energy savings.  According to DEER, the use of the 2013 Title-24 weather files causes all weather sensitive UES values to change by amounts from small (less then +/-1%) to moderate (greater than +/-5%).

Weather Update Methodology

The interim methodology for updating energy (kWh) impacts in measure are based on (scaling) factors and data documented by the CPUC’s as part of their weather update analysis – “Weather Data Comparison Workbook”, dated July 3, 2013 – Attachment 3.  This document compares 2008 and 2013 weather parameters for all 16 California climate zones including (a) cooling and heating degree-days and (b) average temperature during 9-hour peak period utilized for estimating DEER demand.

Energy (kWh) impacts are scaled based on the ratio between cooling and heating degree days from the two weather sets (e.g., 2008 and 2013 weather data) as documented in DEER.

Demand (kW) impacts are scaled based on adjustment factors determined using the Building Energy Simulation - eQuest/DOE2.2 with 2008 and 2013 (CZ2010) weather sets for each Climate Zone under SCE’s territory.  Once Demand (kW) from each weather set is determined, the ratio between these (e.g., kW_2013Weather vs. kW_2008Weather) constitutes the scaling factor for the “weather-updated” DEER Demand (kW).

2014 program documentation indicates that “Misc – Commercial” (4,030 tons); “Office – Large” (3,990 tons); and “Education – Primary School” (3,918 tons) are the sectors with highest program activity.  Since the “Office – Large” DEER prototype is defaulted with Air Handles with CHW coils opposed to DX/GF packaged equipment, the “Education – Primary School” DEER prototype was selected for estimating demand scaling based on 1975 vintage and “Code Case” (CB8) baseline (e.g., EPr-wXX-v75-cCB8-mNE-HVAC-airAC-Pkg-lt55kBtuh).  The selected vintage is consistent with highest population of buildings as documented in DEER’s Commercial Building Weights - per vintage weights by climate zone and building type.  Scaling for Demand (kW) is detailed in Attachment – 1 (under “Impact Matrix”).

All measures are anticipated to be updated with a statewide workpaper likely in 2015/Q2 using best available data and WO32 HVAC Impact Evaluation findings.

# Section 3: Load Shapes

A load shape indicates the distribution of a measure’s energy savings over one year. A load shape is a set of fractions summing to unity, with one fraction per hour (or other time period). DEER load shapes are hourly (8,760 hours/year), so multiplying a savings value by the load shape value for any particular hour yields the energy savings for that particular hour. SCE also has time-of-use (TOU) load shapes which split the year into five time periods that are defined by rate tariffs.

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Table 8: Building Types and Load Shapes

| Building Type | Load Shape | E3 Alt. Building Type |
| --- | --- | --- |
| Assembly | DEER:HVAC_Split-Package_AC, DEER:HVAC_Split-Package_HP | NON_RES |
| Education - Primary School |  |  |
| Education - Secondary School |  |  |
| Education - Relocatable Classroom |  |  |
| Education - Community College |  |  |
| Education - University |  |  |
| Grocery |  |  |
| Food Store |  |  |
| Health/Medical - Nursing Home |  |  |
| Health/Medical - Clinic |  |  |
| Misc - Commercial |  |  |
| Office - Large |  |  |
| Office - Small |  |  |
| Restaurant - Fast-Food |  |  |
| Restaurant - Sit-Down |  |  |
| Retail - Multistory Large |  |  |
| Retail - Single-Story Large |  |  |
| Retail - Small |  |  |

# Section 4: Base Case & Measure Costs

## 4.1 Base Case Cost

The base case is the customer’s existing equipment; therefore the base case cost is $0.00.

## 4.2 Measure Case Cost

The QM+ measure costs are aggregated based on the costs of individual treatments applicable to the measure and the anticipated incidence or probability at which the treatments will be performed.

The references for the individual treatment costs are provided in sections 4.2.1-4.2.7. The probability of individual treatment uptake and the aggregated QM+ measure costs are provided in section 4.2.8.

### 4.2.1 Refrigerant Charge Adjustment

The 2010-2012 WO17 Ex Ante Measure Cost Study [475] provides refrigerant charge adjustment per-ton costs by leveraging direct install primary price data from utilities over the past two program cycles (2010-2012 and 2013-2014): $9.92 for material and $26.78 for labor.

### 4.2.2 Condenser and Evaporator Coil Cleaning

The 2010-2012 WO17 Ex Ante Measure Cost Study [475] provides costs per-ton for cleaning condenser coils and evaporator coils. The per-ton costs for cleaning condenser coils are $6.73 for material and $25.65 for labor. The per-ton costs for cleaning evaporator coils are $7.98 for material and $33.69 for labor.

### 4.2.3 Air Flow Adjustment

Since the 2010-2012 WO17 Ex Ante Measure Cost Study [475] does not include cost on this measure, Utility program tracking data was used to estimate per-ton costs for air flow adjustment of $5.43 for labor and $0.00 for material.

### 4.2.4 Economizer Repair with and without ADEC

For economizer repair without ADEC (e.g., DDC economizer controller), the 2010-2012 WO17 Ex Ante Measure Cost Study provides per-ton costs: $19.64 for material and $19.78 for labor.

The economizer repair treatment includes the option to upgrade the existing economizer controller to an Advanced Digital Economizer Controller (ADEC). The ADEC upgrade enhances the functionality of the existing economizer, and provides a platform for subsequent or concurrent upgrades to HVAC controls. The cost for an economizer repair including the ADEC upgrade can be much higher than the normal economizer repair treatment, accounting for the additional cost of the controller as well as potentially replacing the existing damper assembly and/or damper motor in order to properly function with ADEC. Utility program tracking data was used to estimate a weighted average per-ton cost of $219.95, which can be split into $200.17 for material and $19.78 for labor using the same labor cost for economizer repair without ADEC.

### 4.2.5 Economizer Reprogramming

Since the 2010-2012 WO17 Ex Ante Measure Cost Study [475] does not include cost on this measure, Utility program tracking data was used to estimate weighted average per-ton costs for economizer reprogramming of $0.00 for material and $4.79 for labor.

### 4.2.6 Thermostat Replacement

For thermostat replacement, an average per-unit cost is $139.48 for material (from retailers) and $56.48 for labor (from DEER 2008). Utility program tracking data was used to normalize costs per ton across units on which the measure was installed. The per-ton costs are estimated at $22.97 for material and $9.30 for labor.

### 4.2.7 Thermostat Reprogramming

For thermostat reprogramming, it is assumed that a HVAC controls contractor will charge 1 hour at the DEER default labor rate of $67.88 (as documented in DEER Measure Cost Summary under NR-MISC – Revision 06/30/2008). Utility program tracking data was used to normalize the measure costs per ton. The per-ton costs are estimated at $0.00 for material and $12.50 for labor.

### 4.2.8 Measure Cost Summary

The estimated incidence of performing each treatment for any given unit are based on the 5/2/2013 ED Disposition for Non-Residential HVAC Rooftop Quality Maintenance – Attachment 2. The Economizer Repair with ADEC treatment is not captured by the ED Disposition (and/or DEER) and is the only treatment estimated through actual utility program tracking data. The individual treatment costs and incidence values are summarized in Table 9.

Table 9: Individual Treatment Costs per Ton and Incidence

| Individual Treatment (both DXGF and PKHP) | Material Cost | Labor Cost | GMC/IMC | ED Incidence |
| --- | --- | --- | --- | --- |
| Refrigerant Charge Adjustment | $9.92 | $26.78 | $36.70 | 0.4 |
| Condenser Coil Cleaning | $6.73 | $25.65 | $32.38 | 0.4 |
| Evaporator Coil Cleaning | $7.98 | $33.69 | $41.67 | 0.2 |
| Air Flow Adjustment | $0.00 | $5.43 | $5.43 | 0.2 |
| Economizer Repair without ADEC | $19.64 | $19.78 | $39.42 | 0.1 |
| Economizer Repair with ADEC | $200.17 | $19.78 | $219.95 | 0.4 |
| Economizer Reprogramming | $0.00 | $4.79 | $4.79 | 0.1 |
| Thermostat Replacement | $22.97 | $9.30 | $32.27 | 0.2 |
| Thermostat Reprogramming | $0.00 | $12.50 | $12.50 | 0.1 |

Applying the applicable individual treatment costs with the associated incidence provides aggregated costs for the QM+ measures, as shown in Table 10. Economizer Repair without ADEC, Economizer Repair with ADEC, and Economizer Reprogramming treatments are only applied to the measures including an economizer.

Table 10: Measure Costs per Ton

| Measure | Material Cost | Labor Cost | GMC/IMC |
| --- | --- | --- | --- |
| Quality Maintenance plus (QM+) | $12.85 | $31.91 | $44.76 |
| Quality Maintenance plus with Economizer (QM+Econo) | $94.88 | $42.27 | $137.16 |
| Quality Maintenance plus Heat Pump (QM+HP) | $12.85 | $31.91 | $44.76 |
| Quality Maintenance plus with Economizer Heat Pump (QM+EconoHP) | $94.88 | $42.27 | $137.16 |

The QM+ measure costs are estimates and will be impacted by the actual individual treatment uptake seen by the utility program.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost (GMC)

For REA measures, the Gross Measure Cost (GMC) is the full measure cost from Section 4.2.

### 4.3.2 Incremental Measure Cost (IMC)

For REA measures, the Incremental Measure Cost (IMC) is the same as the GMC.

# Attachments

# References

[464]

[355]

[462]

[475]

# Appendix A: Application Types

This table compares the application types in SCE’s systems with those in DEER.

| SCE Application (Program) Type | DEER Application Type | Savings |  | Cost |  | Life |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL | 1st BL | 2nd BL |
| New Construction (NEW) | New Construction (Nc) | Above Code or Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob), Normal Replacement (NR) | Above Code or Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Customer Existing | Above Code or Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Customer Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Customer Existing | N/A | Full Cost | N/A | EUL | 0 |

# Appendix B: Delivery Mechanisms

A delivery mechanism is a delivery method paired with an incentive method. SCE’s delivery methods include:

- Appliance Turn-in and Recycling

- Audit/Information

- Commissioning

- Financial Support

- Innovative Design

- Midstream Programs

- Partnership

- Upstream Programs

The following table describes the incentive methods.

| Incentive Method | Description |
| --- | --- |
| Direct Install | The utility program performs an assessment of the customer’s facility, provides recommendations, and implements energy efficiency measures for free. |
| Down-Stream Incentive - Deemed | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. |
| Exchange - Replacement | The utility program holds events where customers can trade functional equipment for similar but more energy efficient equipment, free of charge. |
| Giveaway | The utility program provides customers with energy efficient equipment for free. |
| Mid-Stream Incentive | The utility program offers buydowns and incentives to third parties (typically retailers, distributors, and contractors), who then stock, promote, lower prices on, and/or sell energy efficient equipment. Contractors install energy efficiency equipment, sometimes using specified quality procedures, at the customer’s property. |
| On-bill Finance - loan | Customers can finance energy efficiency projects at 0% interest and repay the loan through their monthly utility bill. |
| Testing Services / Other | The utility program performs free testing services or assessments of the customer’s facility and provides information and recommendations for potential energy efficiency measures. |
| Up-Stream Buy Down, Up-Stream Incentive | The utility program offers buydowns and incentives to vendors (typically manufacturers and distributors), who then manufacture, stock, promote, lower prices on, and/or sell energy efficient equipment. There is some overlap between the mid-stream and up-stream approaches. |