Work Paper SCE13HC039

Revision 4

Southern California Edison

VFD Retrofit to Central Plant Systems

# At-a-Glance Summary

| Measure Codes | AC-14365, AC-91987, AC-55411 |
| --- | --- |
| Measure Description | Variable Speed Drive on Cooling Tower (CT) Fan Control Variable Speed Drive on Chilled Water (CHW) Pump Control Variable Speed Drive on Condenser Water (CW) Pump Control |
| Base Case Description | Source: Existing Custom Equipment/Title 24 CT Fan Control – Single speed/two-speed depending on vintage CHW Pump Control – Single speed CW Pump Control – Single speed |
| Units | Per Horsepower (HP) |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 15 years (DEER EUL ID: HVAC-VSDSupFan, HVAC-VSD-pump) |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.6 (DEER NTGR ID: Com-Default>2yrs) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 4/25/12 | Ricardo Sfeir/BASE Energy | This is the original work paper for the bridge cycle 2013-2014. Work paper No. WPSCNRHC0039.0, from the previous cycle, was used to create this work paper. Except for format changes from the new work paper template, there are no other changes from the previous cycle. |
| 1 | 1/29/14 | Phil Jordan / PECI | Work paper was revised to include a new VSD on a condenser water pump measure and update peak demand reduction values for all measures to conform to DEER 2013 demand periods. |
| 2 | 6/6/14 | Michael Crayne/PECI | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - Modeled with new 2013 Title 24 weather files - 2007, 2011, and 2014 vintages included for CT and CW - Modified model inputs for CW - Modified MBT, ESe, and OfS models to have one chiller, for consistency with DEER models - Building vintages weighted using DEER weighting factors - Added new solution code, AC-55411 |
| 3 | 1/26/16 | Ryan Cho/SCE | - New template update for 2016 program year - Removed SCE building types |
| 4 | 5/5/16 | Jay Bhakta/SCE | - Replaced Misc. Commercial building type with Office - Small |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the energy savings achieved from installing variable frequency drives (VFD) in central plant applications with constant volume chillers.

This measure applies to equipment with constant speed cooling tower fans, condenser water pumps, and chilled water pumps not already equipped with VFD/VSDs. VFDs reduce fan or pump motor energy by adjusting motor speeds to meet actual load conditions. Estimated demand and energy savings for this work paper are based on DOE-2/eQUEST modeling results.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Variable Speed Drive on Cooling Tower (CT) Fan Control Variable Speed Drive on Chilled Water (CHW) Pump Control Variable Speed Drive on Condenser Water (CW) Pump Control |
| Existing Condition | N/A |
| Code/Standard | Source: Existing Custom Equipment/Title 24 CT Fan Control – Single speed/two-speed depending on vintage CHW Pump Control – Single speed CW Pump Control – Single speed |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | AC-14365 |  | Variable Speed Drive on Cooling Tower Fan Control |
|  |  | AC-91987 |  | Variable Speed Drive on Chilled Water Pump Control |
|  |  | AC-55411 |  | Variable Speed Drive on Condenser Water Pump Control |

Throughout this paper, the terms variable frequency drive (or VFD) and variable speed drive (or VSD) are used synonymously.

This measure applies to non-residential buildings in all SCE climate zones that use a central chiller plant system with constant speed cooling tower fans, condenser water pump, and chilled water pumps not already equipped with VFDs. This measure should be accompanied by the installation of 2-way chilled water valves for the VFD addition to the chilled water pump measure. Savings are therefore greatest at low-flow conditions.

Successful implementation of this measure will depend greatly on the characteristics of the installed system. For the VFD addition to the condenser water pump special attention should be given to the condenser water flow turndown capabilities of the existing cooling tower(s) and chiller(s). It is imperative that chiller manufacturer selection data and cooling tower manufacturer retrofit information be carefully reviewed to ensure that the existing cooling tower(s) and chiller(s) are rated to operate at the selected minimum condenser water flow, and that the control strategy includes capability to increase the flow as needed to keep the leaving condenser temperature from exceeding an upper limit dependent on the existing chiller. Refer to the attached Measure Limitations Memo [C] in the Attachments Section for more information.

## 1.2 Technical Description

Central plant systems provide space cooling to a building by cooling water in a chiller and circulating this chilled water either through a chilled water coil in an air handler or throughout the building zones. Chillers may be air-cooled or water-cooled, and in the case of water-cooled chillers, a separate water loop absorbs heat from the chiller which is then rejected by a cooling tower. In these systems, a significant amount of energy is consumed by the fans and pumps used to circulate air and water. Cooling tower (CT) fans circulate air to facilitate heat rejection; chilled water (CHW) pumps circulate water cooled by the chiller; condenser water (CW) pumps circulate the water that transfers heat between the chiller and the cooling tower.

These fans and pumps are designed to meet peak load conditions, when the equipment must run at 100% capacity. However, for the majority of the time the demand for cooling is less than the peak design capacity. Standard practice has been to install single-speed fan and pump controls, which causes them to run at 100% speed, even if actual demand may be much less. This presents a significant energy savings opportunity if fan and pump speed can be varied to meet actual demand conditions.

Variable frequency drives control motor speed by varying the frequency and voltage of the fan/pump motor. VFDs are programmed to reduce fan/pump speed to just meet actual load conditions, thus reducing fan/pump speed when loads drop below design conditions, resulting in significant fan/pump energy savings throughout the year.

## 1.3 Installation Types and Delivery Mechanisms

The installation type is retrofit add-on (REA).

The delivery method is Financial Support - Down Stream Incentive – Deemed, with savings reported on a per horsepower basis.

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| New Construction (NEW/NC) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit or Early Replacement (RET/ER) | Above Customer Existing | Above Code or Standard | RUL | EUL-RUL |
| Retrofit First Baseline Only (REF) | Above Customer Existing | N/A | EUL | N/A |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Appliance Turn-in and Recycling | The program motivates customers, through financial incentives, to recycle appliances that are functional but inefficient. This prevents the continued use of those appliances, by both the current owner and potential future owners. |
| Audit - Information - Testing Services | The program performs a free assessment of a customer’s facility and provides the customer with information and guidance on energy efficiency opportunities. |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |
| Partnership | The program implements projects through a partnership between the utility and an institutional, government, or community-based organization. |
| Up-Stream Programs | See Up-Stream Incentive in the Incentive Method Descriptions table. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Exchange - Replacement | The utility program holds events where customers can trade functional equipment for similar but more energy efficient equipment, free of charge. |
| Giveaway | The program provides customers with energy efficiency equipment or services for free. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |
| On-bill Finance – Loan (OBF) | The program offers financing for the cost of an efficient measure as part of the utility bill. This can be an add-on option to an existing program or can serve as an organizing principle for its own program. |
| Up-Stream Incentive Up-Stream Buy Down | The program gives a financial incentive to an upstream market actor (manufacturer or distributor) to encourage the manufacture, provision, or distribution of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

The 2014 Database for Energy Efficient Resources (DEER) [26, 49] does contain similar central plant/VFD measures (DEER ID D03-063: Two-Speed Cooling Tower Fans; DEER ID D03-064: VSD Cooling Tower Fans; DEER ID D03-051: VSD Supply Fan Motors; DEER ID D03-046: Variable Flow Chilled Water Loop; DEER ID D03-047: VSD Chilled Water Loop Pump). DEER does not contain a measure for installing a VSD on Condenser Water Pumps.

For the VSD measure for Chilled Water Loop pumps, DEER reports only a limited number of building types. Additionally, the DEER measure descriptions do not match the measure in this work paper;  D03-046 has three-way valves and a single-speed pump in the base case, and two-way valves and a single-speed pump in the measure case; D03-047 has two-way valves and a single-speed pump in the base case, and two-way valves and a variable-speed pump in the measure case. The measure in this work paper has three-way valves and a single-speed pump in the base case, and two-way valves and a variable-speed pump in the measure case.

For the VSD measure for Cooling Tower Fans, DEER also only reports a limited number of building types, and the DEER measure descriptions do not match the measure in this work paper; D03-063 has single-speed fans in the base case, and two-speed fans in the measure case; D03-064 has two-speed fans in the base case, and variable-speed fans in the measure case. The measure in this work paper has a weighted average of single-speed and two-speed fans in the base (based on the code requirements for each vintage), and variable-speed fans in the measure case. Additionally, the savings in DEER for VSD Cooling Tower Fans are reported as savings per cooling ton, instead of the required kWh savings per horsepower (hp).

Due to the differences between the DEER measures and the measures contained in this work paper, modeling was performed to determine savings for all measures and building types – all results reported in this work paper were modeled.

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | Yes |
| DEER Version | N/A |
| Reason for Deviation from DEER | - DEER 14 does include similar measures, but for a limited number of buildings. Additionally, the DEER measure descriptions do not exactly match the measures in this work paper - This work paper expands the applicable building types, assumes different baseline cases, and uses different per unit savings (kWh/hp vs. kWh/ton) |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | Any | 0.6 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-VSDSupFan | VSD Supply Fan Motors (used for the VFD on Cooling Tower Fan)) | Com | HVAC | 15 | 5 |
| HVAC-VSD-pump | Variable Flow Water Loop, VSD Pump (used for the VFD on Chilled Water Pump and VFD on Condenser Water Pump) | Com | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

Current requirements for heat rejection fan speed controls in non-residential applications are contained in Title 24 2013 [355], Section 140.4(h), page 175. For cooling tower fans 7.5 hp or greater, two-speed controls are required that reduce the fan speed to at least 2/3 of full speed.

Current requirements for variable flow hydronic loops in non-residential applications are contained in Title 24 2013, Section 140.4(k), pages 176-177. For chilled water pumps 5 hp or greater, Title 24 requires variable speed drives on hydronic loops with variable flow capability. Condenser water systems serving only water-cooled chillers are exempt from the requirements in this section.

The requirements for both the cooling tower fan speed control and the hydronic loop flow controls are only for new systems and do not apply to this work paper which deals with retrofit add-on measures.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings, Section 140.4(h), pg. 175 Section 140.4(k), pg. 176-177 | July 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

N/A

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Estimated demand and energy savings for this work paper are based on simulated variable frequency drives (VFD) in central plant cooling tower fans, chilled water pumps, and condenser water pumps.  Simulations were conducted using the DOE-2/eQUEST v.3.64 modeling tool (for the Refrigerated Warehouse building type, the refrigeration version of eQuest was used). Model development and savings analyses are discussed in detail in this section.

## 2.1 DEER Prototypes

Non-residential buildings that can use a central chiller plant system were included in the simulation analysis. A list of the 12 selected building types is reported in table below. The selection of the building types was based on potential program targets. Building models were generated using the eQUEST DEER batch processing tool. The DEER batch processing tool creates eQUEST building models based on existing DEER prototypes for both residential and non-residential market sectors. These building prototypes contain the building characteristics (such as HVAC equipment, construction materials, and occupancy schedules) that are used to calculate DEER measure savings. In addition, the DEER batch tool allows prototypes to be generated by desired vintages, and climate zones.

The DEER non-residential prototypes are generated in the batch processor with the HVAC configuration typical for each building type.  For example, Education - University prototypes are automatically generated with a central chiller plant system, as this is the expected system in the majority of university settings. Some building types considered for program participation do not typically have a central chiller plant configuration in DEER. In these cases, the building prototype was generated in the DEER batch processor with its typical packaged roof-top unit (RTU) configuration. This configuration was then modified in the eQUEST detailed data edit mode to allow a central plant configuration. The table shown below reports which building prototypes include a central chiller plant configuration, and which required modification to allow this type of configuration.

Non-Residential DEER Prototype Models

| DEER Building Type | DEER Prototype HVAC Configuration |
| --- | --- |
| Assembly | Package RTU |
| Education - Secondary School | Package RTU |
| Education – University | Chiller Plant |
| Health/Medical – Hospital | Chiller Plant |
| Health/Medical - Nursing Home | Chiller Plant |
| Lodging – Hotel | Chiller Plant |
| Manufacturing - Bio/Tech | Package RTU |
| Office – Large | Chiller Plant |
| Office – Small | Chiller Plant |
| Retail - Multistory Large | Chiller Plant |
| Manufacturing-Light Industrial | Package RTU |
| Warehouse-Refrigerated | Package RTU |

Once each building type was modified to allow a central plant configuration, each baseline model was then modified per the keyword changes listed in the table shown below (eQUEST Keyword Modifications) to simulate each measure.

## 2.2 Energy Savings

### 2.2.1 eQUEST Energy Simulations

Over 2000 energy simulations were performed to account for the baseline, three measures, 13 building types, eight climate zones (CZ) in SCE service territory, and seven DEER building vintages.  The DEER vintages (with their single-reference year in parentheses) are included in the table shown below.

- Before 1978 (1975 – shown in the table below as 75)

- 1978 – 1992 (1985 – shown in the table below as 85)

- 1993 – 2001 (1996 – shown in the table below as 96)

- 2001 – 2005 (2003 – shown in the table below as 03)

- 2005 – 2009 (2007 – shown in the table below as 07)

- 2009 – 2013 (2011 – shown in the table below as 11)

- 2013 – 2014 (2014 – shown in the table below as 14)

The simulated prototype building with chiller plant for each vintage and CZ was considered the baseline model. The energy and demand consumption from these simulated models represents the base case consumption. Each measure was then modeled using individual model runs. VFDs on chilled water loop pumps were not modeled for 2007 or later vintage buildings. Since they are required by code, the prototype models for these vintages have VFDs already installed in the base case. The table shown below reports the eQUEST keywords used for the model runs, including the input values for both the base case and the measure conditions. The resulting energy and demand consumption from the measure simulations represent the measure case consumption.

For the VFD on condenser water pump measure, it is important to define a minimum condenser water flow rate and a maximum allowable leaving condenser temperature. For the minimum flow rate, the determinants are the minimum flow required by the chiller and the minimum flow required by the tower. Based on research a conservative estimate of 70% [D – G] achievable flow turndown was chosen for the measure case. For the maximum leaving condenser temperature the limit was set to be the condenser temperature at the rated conditions for the baseline model (keyword CHILLER:RATED-COND-T).

eQUEST Keyword Modifications

| Measure |  |  |  |
| --- | --- | --- | --- |
| Vintage(s) | Keyword | Baseline Design Value | Measure Design Value |
| CHW* Loop Pump EEM** |  |  |  |
| 75,85,96,03 | PUMP:CAP-CTRL | N/A | VAR-SPEED-PUMP |
| 75,86,96,03 | SYSTEM:CHW-VALVE-TYPE | N/A | TWO-WAY |
| Chiller Plant Tower Fan EEM |  |  |  |
| 75,85,96 | HEAT-REJECTION:CAPACITY-CTRL | ONE-SPEED-FAN | VARIABLE-SPEED-FAN |
| 03,07,11,14 | HEAT-REJECTION:CAPACITY-CTRL | TWO-SPEED-FAN | VARIABLE-SPEED-FAN |
| CW*** Loop Pump EEM |  |  |  |
| 75,85,96,03,07,11,14 | PUMP:CAP-CTRL | N/A | VAR-SPEED-PUMP |
| 75,85,96,03,07,11,14 | CHILLER:CW-FLOW-CTRL | CONSTANT-FLOW | VARIABLE-FLOW |
| 75,85,96,03,07,11,14 | CHILLER:CW-MIN-FLOW | N/A | 0.70 (ratio) |
| 75,85,96,03,07,11,14 | CHILLER:MAX-COND-T | N/A | 85.0 (degF) |

*Chilled Water (CHW)

** Energy Efficiency Measure (EEM)

***Condenser Water (CW)

While the Health/Medical - Nursing Home prototype included a chiller plant, it utilized an air-cooled condenser instead of a cooling tower. Thus, the VFD on Cooling Tower Fan and VFD on Condenser Water Pump measures were not modeled for this building type. The Warehouse-Refrigerated model does not include a chiller plant, as space cooling is provided by a refrigeration system. Thus, the VFD on Chilled Water Pump and VFD on Condenser Water Pump measures were not modeled for this building type.

The difference in energy consumption between the baseline simulation run and the measure runs represents the energy savings.

### 2.2.2 Multiple Chillers and VFD Towers

The prototypes in the DEER model included only single chiller plants and cooling towers. Since many buildings have multiple chillers and cooling towers, some of the buildings were modeled to include multiple chiller plants and cooling towers. Additional models in three separate climate zones were created for the following building types listed in the table shown below. The three climate zones were selected as a comparison to ensure that energy savings amounts found were consistent with savings from models with single chiller plants taking into account a wide range of climates.

Buildings Modeled with Multiple Chillers and Cooling Towers

| DEER Building Type | Cooling Tons | Vintage | CZ | Number of Modeled Chillers/Towers |
| --- | --- | --- | --- | --- |
| Education - University | 2500 | 85 | 6, 8, 13 | 3 |
| Health/Medical - Hospital | 625 | 85 | 6, 8, 13 | 2 |
| Lodging - Hotel | 500 | 85 | 6, 8, 13 | 2 |
| Retail – Multistory Large | 300 | 85 | 6, 8, 13 | 2 |

To add the multiple systems, a second tower identical to the existing DEER one was added to the condenser water loop. Variable speed control was added to both towers. As required by the equipment configuration one or two chillers and the associated pumps were created based on the baseline chiller and pumps. The only variable that was modified was the capacity ratio, such that the chillers were equally sized and with a total capacity equal to the baseline chiller. This resulted in modeling chillers that would not normally be found in practice. For example, the DEER prototype for the hospital building type had 625 cooling tons of capacity and was modeled with 2 chillers of 312.5 tons. For the chilled water pump, the chilled water loop can only have one pump assigned. This pump, however, may consist of a single pump or multiple pumps (set by keyword “NUMBER”).

For the VFD on the chilled water pump measure the savings are on average 11% greater (with a minimum of 7% and a maximum of 15%) for the multiple chiller models and for the VFD on the cooling tower fans measure the savings are on average 25% less (with a minimum of 5% and a maximum of 49%) for the multiple chiller models; these differences are explained further in the eQUEST Simulation Issues section that follows. The savings difference for the VFD on the chilled water pump is within an acceptable range, and so no adjustment was made to the modeled savings for this measure. To account for the relatively high difference in savings for the cooling tower fan measure, the modeled savings for this measure were decreased by 25%.

Costs for installing multiple VFDs in these applications will not increase as the costs are calculated on a per horsepower basis as discussed in Section 4.

### 2.2.3 eQUEST Simulation Issues

After performing simulations on the “normal operation” buildings, discrepancies were observed in the resulting fan sizes for all buildings. The cooling loads and the resulting equipment sizing were determined by eQUEST without any modifications of the original defaulted DEER and BDL inputs. For example, results on the part load ranges generated by eQUEST for the cooling tower fans and chilled water pumps are not consistent with expectations.

In the models used for this analysis, the cooling towers are significantly oversized (see the table below; for University, CZ 6, V85, the tower is sized at 226.4 kW, while the actual peak load is only 148.9 kW). As a result, the towers are operating at between 40 and 50% load for 99% of hours in the baseline case. This over-sizing is greater in the single tower case (baseline peak load is 65.8% of tower size in the single tower model as opposed to 83.6% in the multiple tower scenario). Thus, the savings potential for adding a variable speed drive on the fan is slightly higher in the single tower case. Reducing the tower capacity in the model increases the ratio between peak load and equipment size but results in warnings that the capacity is less than demand.

Equipment Sizing Results for University Building Type

| Model: University, CZ6, v85 |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Equipment Sizing (PV-A)* (kW) | Equipment Peak (PS-C)** (kW) | Equipment Sizing (PV-A) (kW) | Equipment Peak (PS-C) (kW) |
|  | Tower Fan |  | Chilled Water Pump |  |
| Single Chilled Water Pump/Cooling Tower Fan |  |  |  |  |
| Baseline | 226.4 | 148.9 | 187.4 | 187.4 |
| Tower Fan VSD | 226.4 | 47.0 | - | - |
| Chilled Water Pump VSD | - | - | 187.4 | 77.4 |
| Multiple Chilled Water Pumps/Cooling Towers |  |  |  |  |
| Baseline | 79.69 | 66.6, 62.9, 53.9 | 202 | 202 |
| Tower Fan VSD | 79.69 | 40.7, 62.9, 53.9 | - | - |
| Chilled Water Pump VSD | - | - | 202 | 74.7 |

*PV-A is the Plant Design Parameters report available in the eQUEST SIM (simulation) file

**PS-C is the Equipment Loads and Energy Use report available in the eQUEST SIM file

For the chilled water pumps, the baseline pumps have a peak load consistent with the equipment sizing, and they operate at 100% loading for all operating hours. The modeled pumps with variable speed drives are operating for a significant number of hours in the 0 to 10% load range, particularly when the specified turndown ratio is set at 0.40. This is due to the methodology used in eQUEST for sizing. This sizing issue results in significantly higher savings for installing a VFD on the chilled water pump than installing a VFD on the cooling tower fans. In the baseline model, the cooling tower fan operates at less than 60% load for most hours while the chilled water pump operates at 100%. Savings potential is, therefore, greater for the chilled water pump. The lower savings potential of the cooling tower fan is then divided by a larger motor HP due to over sizing, thereby further increasing the difference in savings on a per HP basis. Engineering review of the energy and demand savings values determined that the energy savings reported by the model are reasonable.

The part load operating hours for the variable speed pumping options are the same in both the single and multiple pump options. What does change is the number of hours in the part load bins for the electrical consumption. For the multiple pump option, only one of the three pumps is required for low load operation. For the single pump option, the majority of hours (80%) are in the 20-30% load range, as the single pump cannot turn down as far. Hence the slightly increased savings potential for the multiple pump model.

### 2.2.4 Weighted Average Methodology

To create a single value for each building type and climate zone, the DEER2014 Energy Impact Weights Tables [B] were used to create a weighted average of each vintage represented in the climate zone. The weighted average was applied to the combined base cases to create a single savings amount for each measure and climate zone. The weighted average baseline for the CHW measure was calculated separately from the weighted average baseline for the CT and CW measures, as it did not include the 07 or later vintages (as VFDs on CHW loop pumps are required for these vintages).

### 2.2.5 Energy Savings Results

Energy savings are calculated as the difference between the baseline model energy use and the energy use as modeled with the VFD installed. To convert savings to kWh/HP, the HP is first calculated by taking the demand (kW) as reported in the Plant Design Parameters (PV-A) Report available in the SIM file. This is then converted by dividing by the constant 0.746 kW/HP. Energy values from the model output are then divided by HP, resulting in kWh/HP. The table shown below shows the energy savings for the Hospital building type.

Energy Savings for Hospital

|  | Energy Savings (kWh/HP) |  |  |
| --- | --- | --- | --- |
| Climate Zone | CHW Loop Pump VSD | CT Fan VSD | CW Loop Pump VSD |
| CZ06 | 5,432 | 454 | 2,214 |
| CZ08 | 5,552 | 498 | 2,256 |
| CZ09 | 5,504 | 473 | 2,202 |
| CZ10 | 5,110 | 459 | 2,090 |
| CZ13 | 4,897 | 489 | 2,000 |
| CZ14 | 4,727 | 388 | 1,930 |
| CZ15 | 5,101 | 709 | 2,066 |
| CZ16 | 4,502 | 171 | 1,779 |

As Energy Savings for Hospital table shows, energy savings for the VFD on Chilled Water Pump measure are the most significant as the savings include reductions in space cooling energy (including the constant volume chiller) and heat rejection energy in addition to the reduced pumping energy. For example, for the 2003 vintage Hospital building type in climate zone 6, the VFD on Chilled water pump measure results in a 20% reduction in pump energy, 4% reduction in heat rejection energy, and 3% reduction in space cooling energy. Pumping savings account for 83.2% of total measure savings, space cooling savings account for 16.7%, and heat rejection savings account for 0.3% (there is a slight energy penalty for ventilation fan energy).

The addition of a VFD on the cooling tower only results in reduced fan power. The addition of a VFD on the condenser water pump results in reduced pumping power during part-load conditions, but there is an increase in space cooling energy (due to higher chiller consumption); however, the reduction in pumping energy is great enough to provide energy savings overall.

## 2.3 Demand Savings

The peak demand results from eQUEST do not conform to the DEER methodology for determining demand across a three-day peak heat wave. To ensure the DEER methodology was applied to determine peak demand savings, the hourly reports included in the eQUEST simulation runs

eQUEST simulation runs include hourly consumption reports. These reports were utilized to extract the demand from the 2-5pm peak period for the DEER-defined three-day peak heat waves. DEER reports the beginning date of the expected three-day heat wave for each climate zone, as follows:

Peak Demand Period used for DEER 2014

|  | Start of 3 Day Period |  |  |
| --- | --- | --- | --- |
| Climate Zone | Month | Day | Week Day |
| CZ06 | Sept | 1 | Tue |
| CZ08 | Sept | 1 | Tue |
| CZ09 | Sept | 1 | Tue |
| CZ10 | Sept | 1 | Tue |
| CZ13 | July | 8 | Wed |
| CZ14 | Aug | 26 | Wed |
| CZ15 | Aug | 25 | Tue |
| CZ16 | Jul | 8 | Wed |

Once the data was extracted for the three-days selected, the hourly results from 2-5pm on the three consecutive days (9 data points) were averaged to provide peak demand estimates. The difference between the baseline and measure peak demand estimates results in the peak demand savings. To create a single demand savings value for each building type in each climate zone, the same methodology as was used for energy savings was applied. The table below shows the demand savings for the Hospital building type.

Demand Savings for Hospital

|  | Energy Savings (kW/HP) |  |  |
| --- | --- | --- | --- |
| Climate Zone | CHW Loop Pump VSD | CT Fan VSD | CW Loop Pump VSD |
| CZ06 | 0.52 | 0.23 | 0.20 |
| CZ08 | 0.51 | 0.23 | 0.18 |
| CZ09 | 0.48 | 0.29 | 0.09 |
| CZ10 | 0.45 | 0.28 | 0.09 |
| CZ13 | 0.45 | 0.28 | 0.12 |
| CZ14 | 0.48 | 0.23 | 0.16 |
| CZ15 | 0.46 | 0.26 | 0.11 |
| CZ16 | 0.52 | 0.16 | 0.23 |

As is explained in Section 2.2.5, savings are most significant for the VFD on Chilled Water Pump measure, as it results in savings for pump energy, space cooling energy, and heat rejection energy.

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:HVAC_Chillers | NON_RES |
| Education - Secondary School | DEER:HVAC_Chillers | NON_RES |
| Education - University | DEER:HVAC_Chillers | NON_RES |
| Health/Medical - Hospital | DEER:HVAC_Chillers | NON_RES |
| Health/Medical - Nursing Home | DEER:HVAC_Chillers | NON_RES |
| Lodging – Hotel | DEER:HVAC_Chillers | NON_RES |
| Manufacturing - Bio/Tech | DEER:HVAC_Chillers | NON_RES |
| Office – Large | DEER:HVAC_Chillers | NON_RES |
| Office – Small | DEER:HVAC_Chillers | NON_RES |
| Retail - Multistory Large | DEER:HVAC_Chillers | NON_RES |
| Manufacturing-Light Industrial | DEER:HVAC_Chillers | NON_RES |
| Warehouse-Refrigerated | DEER:HVAC_Chillers | NON_RES |

# Section 4. Costs

## 4.1 Base Case Cost

Retrofit add on

For this measure category, the base case cost is assumed to be zero because these are discretionary modifications (retrofit) to the customers’ existing equipment.  Their alternative is to make no changes to their existing system.

Base Case Cost

The base case cost is $0/unit for all three measures because the base case refers to the existing equipment, which does not require replacement.

## 4.2 Measure Case Cost

VSD on a Chilled Water Loop Pump Full Measure Costs

For the VSD on a Chilled Water Loop Pump, the material cost reported in DEER 11 [215] for Measure ID D08-NE-HVAC-VSD-CHWpump-gt5HP is used. The cost case for this measure is 2-way valves and VFD pump on chilled water loop. Material cost for this measure is reported to be $306.08 per horsepower. DEER labor rate, NR-HVAC-HC, is used for Labor cost. Based on one labor hour per horsepower, the Full Measure Cost for this measure is estimated to be $373.96.

Full Measure Cost (per HP) = Measure Case Cost + Labor Cost

$373.96 = $306.08 + $67.88

VSD on a Condenser Water Pump Full Measure Costs

For the VSD on a Condenser Water Pump, the cost case is installation of a VFD on an existing condenser water pump. Note that existing cooling towers unable to achieve significant flow turndown can be retrofitted with low-flow nozzles; however, this cost was not included due to lack of specific information on existing cooling tower characteristics. The modeled savings assume the existing tower can achieve a minimum CW flow of 70% without modification based on research conducted of general cooling tower turndown capabilities. DEER 11 does not have a cost for adding VSDs to an existing condenser water pump. Thus, the full measure cost for a VSD on a Condenser Water Pump will be calculated the same as the VSD on a Chilled Water Loop Pump because the technology is similar in adding a VSD to an existing water loop pump.

VSD on a Cooling Tower Fan Full Measure Costs

For the VSD on a Cooling Tower Fan, the full measure cost reported in DEER 11 includes a measure for variable speed tower fans (D08-NE-HVAC-VSD-ClTwrFan-ge7p5HP), but not for installing a VFD on an existing fan. As an alternative, the material costs associated with Measure ID D08-NE-HVAC-VSDSupFan-ge10HP, installing VSD on Supply Fan Motors was determined to be a reasonable substitute. Material cost for this measure is reported to be $176.68 per nameplate horsepower; DEER labor rate, NR-HVAC-HC, is used for Labor cost.  Based on one labor hours per horsepower, the Full Measure Cost for this measure is estimated to be $244.56.

Full Measure Cost = Measure Equipment Cost + Labor Cost

$244.56= $176.68 + $67.88

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| AC-14365 | REA | $246.56 | $244.56 | N/A |
| AC-91987 | REA | $373.96 | $373.96 | N/A |
| AC-55411 | REA | $373.96 | $373.96 | N/A |

# Attachments

# References

[26]

[49]

[213]

[215]

[355]

[A] Attachment 1

[B] Attachment 2

[C] Attachment 3

[D] Taylor, Steven T. 2011. “Optimizing Design & Control of Chilled Water Plants Part 5: Optimized Control Sequences” ASHRAE Journal 54(6):56-74

[E] http://spxcooling.com/pdf/TR-014.pdf

[F] http://www.energy.ca.gov/2008publications/CEC-400-2008-017/rev1_chapters/NRCM_Chapter_4_Mechanical_Systems.pdf#page=83

[G] http://www.energy.ca.gov/2013publications/CEC-400-2013-002/chapters/04_mechanical_systems.pdf#page=107