Work Paper SCE13HC045

Revision 2

Southern California Edison

Enhanced Ventilation for Packaged HVAC Units with Gas Heating and Packaged Heat Pumps

# At-a-Glance Summary

| Measure Codes | AC-72014, AC-97565, AC-63277, AC-14815, AC-30287, AC-67253, AC-18726, AC-36894, AC-32399, AC-42889, AC-88048, AC-52735, AC-32686, AC-70123, AC-62985, AC-71385, AC-28655, AC-12899 |
| --- | --- |
| Measure Description | Enhanced Ventilation installed on existing Packaged HVAC Units with Gas Heating (Gas Packs), AC only units, and Packaged Heat Pumps consists of 18 measures that reduce the energy associated with providing outdoor air ventilation to a building and its occupants. |
| Base Case Description | The base case for each measure is either a single zone constant volume packaged HVAC unit with direct expansion cooling with or without a natural gas furnace or a single zone packaged heat pump. The base case also has an outdoor air economizer to provide cooling when conditions permit. |
| Units | Per Ton |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 5 years (DEER EUL ID: HVAC-airHP, HVAC-airAC); Please note that since this measure is a retrofit add on onto an existing system the RUL of the existing system is used as the EUL for the measure |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.7 (DEER NTGR ID: All-Default<=2yrs) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 7/8/12 | Benjamin Lipscomb, PECI | -Original Work Paper |
| 1 | 7/15/2014 | Bach Tsan/SCE | -Work paper updated for new template -Savings Based on PGECOHVC143 |
|  | 7/18/2014 | Alfredo Gutierrez/SCE | -Added solution codes -Updated attachment file -Work paper updated for reporting period, effective 7/1/14-12/31/14 |
| 2 | 1/26/16 | Ryan Cho/SCE | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -No value modifications |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

Enhanced Ventilation installed on existing Packaged HVAC Units with Gas Heating (Gas Packs), AC only units, and Packaged Heat Pumps consists of 18 measures that reduce the energy associated with providing outdoor air ventilation to a building and its occupants. The measures in this work paper constitute adding Variable Frequency Drives, NEMA premium motors, permanent magnet motors (PMM), and an Advanced Digital Economizer Controller (ADEC) in the combinations shown below in table, Measures and Codes, shown below to an existing packaged single zone direct expansion (DX) HVAC unit with an economizer. The VFD operates at two discrete speeds based on ventilation and cooling or heating demand.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Enhanced Ventilation installed on existing Packaged HVAC Units with Gas Heating (Gas Packs), AC only units, and Packaged Heat Pumps consists of 18 measures that reduce the energy associated with providing outdoor air ventilation to a building and its occupants. |
| Existing Condition | The base case for each measure is either a single zone constant volume packaged HVAC unit with direct expansion cooling with or without a natural gas furnace or a single zone packaged heat pump. The base case also has an outdoor air economizer to provide cooling when conditions permit. |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | AC-72014 |  | Add VFD with AC unit with Gas Heat and ADEC |
|  |  | AC-97565 |  | Add VFD and NEMA motor with AC unit with Gas Heat and ADEC |
|  |  | AC-63277 |  | Add VFD and PMM with AC unit with Gas Heat and ADEC |
|  |  | AC-14815 |  | Add VFD with AC unit only and ADEC |
|  |  | AC-30287 |  | Add VFD and NEMA motor with AC unit only and ADEC |
|  |  | AC-67253 |  | Add VFD and PMM with AC unit only and ADEC |
|  |  | AC-18726 |  | Add VFD with Heat Pump and ADEC |
|  |  | AC-36894 |  | Add VFD and NEMA motor with Heat Pump and ADEC |
|  |  | AC-32399 |  | Add VFD and PMM with Heat Pump and ADEC |
|  |  | AC-42889 |  | Add VFD and ADEC to AC unit with Gas Heat |
|  |  | AC-88048 |  | Add VFD, NEMA motor, and ADEC to AC unit with Gas Heat |
|  |  | AC-52735 |  | Add VFD, PMM, and ADEC to AC unit with Gas Heat |
|  |  | AC-32686 |  | Add VFD and ADEC to AC unit only |
|  |  | AC-70123 |  | Add VFD, NEMA motor, and ADEC with AC unit only |
|  |  | AC-62985 |  | Add VFD, PMM, and ADEC with AC unit only |
|  |  | AC-71385 |  | Add VFD and ADEC to Heat Pump |
|  |  | AC-28655 |  | Add VFD, NEMA motor, and ADEC to Heat Pump |
|  |  | AC-12899 |  | Add VFD, PMM, and ADEC to Heat Pump |

Eligibility Requirements

- Existing system must be packaged single zone DX cooling unit with gas heat, cooling only unit, or heat pump.

- Existing system must have a constant volume supply fan.

- Existing system must have an operable airside economizer installed, and economizer high limit must be optimized for the climate per Title 24 2013 Table 140.4-B [355], adapted below in the table shown below for reference.

- Maintenance, and repairs to economizer should be completed prior to or in conjunction with this measure.

- The measures described in this workpaper are only applicable for the building types shown in Section 3 below.

Economizer High Limit Shut Off Control Requirements*

| Device Type | Climate Zones | Economizer High Limit Equation (economizer off when) |
| --- | --- | --- |
| Fixed Dry Bulb | 1, 3, 5, 11-16 | Toa>75°F |
|  | 2, 4, 10 | Toa>73°F |
|  | 6, 8, 9 | Toa>71°F |
|  | 7 | Toa>69°F |
| Differential Dry Bulb | 1, 3, 5, 11-16 | Toa>Tra°F |
|  | 2, 4, 10 | Toa>Tra-2°F |
|  | 6, 8, 9 | Toa>Tra-4°F |
|  | 7 | Toa>Tra-6°F |
| Fixed Enthalpy + Fixed Dry Bulb | All | hoa>28Btu/lb or Toa>75°F |

*Adapted from Title 24 2013 Table 140.4-B1. Refer to source for additional detail.

## 1.2 Technical Description

### Measure Case Requirements

Implementation of Enhanced Ventilation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 [355]. Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit’s operating modes, including heating and cooling for each stage as well as the ventilation only mode. Title 24 [355] requires outdoor air ventilation to be provided at the greater of 15 CFM per person times 50% of the fire egress occupancy level specified in the California Commercial Building Code and Nonresidential Alternative Calculation Manual (ACM) Approval Method-CEC-December 2008 [62] (or actual known occupancy level) or the appropriate area rate in the figure, Combined Motor and VFD Efficiency for 3 HP Standard, Premium, and PMM Motors, multiplied by the floor area.

Enhanced Ventilation savings may be applied to any unit that meets the above qualifications. For units serving building types that are not explicitly included in this work paper, or for units serving a space type that is inconsistent with the building type, the building type whose occupant density and typical schedule most nearly represents it should be selected to estimate savings. For example, a fast food restaurant within a large retail building should claim savings for a fast food restaurant rather than for a large retail building. This methodology ensures the most accurate savings are applied for a given unit. Enhanced Ventilation measures are intended for systems that primarily serve spaces with human occupancies rather than spaces such as mechanical equipment rooms or computer server rooms, which will not experience variations in ventilation requirements.

The savings contained in this work paper are deemed savings and do not necessarily represent the savings realized for each individual unit the measure is applied to. Rather, they represent the average savings per ton of cooling capacity across the population of buildings of a certain type in a given climate zone.

### Base Case Requirements

The base case for each measure is either a single zone constant volume packaged HVAC unit with direct expansion cooling with or without a natural gas furnace or a single zone packaged heat pump. The base case also has an outdoor air economizer to provide cooling when conditions permit.

“Single zone” means that the system is controlled by a single thermostat and does not employ zone dampers, bypass dampers, or any other means of air volume control required for multiple spaces.

Implementation of Enhanced Ventilation requires proper setup of the damper limits and fan speeds in order to provide ventilation in accordance with Title 24 2013 [355]. Total unit airflow must be verified for at least one of the fan speeds. The percentage of outdoor air must be verified for each of the unit’s operating modes, including heating and cooling for each stage as well as the ventilation only mode.

The measures are described below with the abbreviated measure names that will be used throughout the work paper.

Base Measure (standard motor)

Due to motor reliability concerns at lower speeds, the minimum fan speed modeled for this measure is 40% of the rated motor speed when applied to a standard induction motor. Reliability concerns for induction motors controlled by VFDs are related to high voltage spikes, which can result in winding failure, in addition to overheating due to reduced cooling at very low speeds. Voltage spikes can be mitigated by maintaining short cable lengths and applying capacitance and/or inductance filters when necessary. Minimum speed recommendations for non-inverter-duty rated standard efficiency induction motors range from 5% to 50% for variable torque applications. The 50% minimum recommendation was published by one VFD manufacturer, and is suspected to be overly conservative based on the recommendations from motor manufacturers and other VFD manufacturers. All of the recommendations by motor manufacturers range from 5% to 20% minimum speed for new standard duty, standard efficiency induction motors. Variable torque applications, such as centrifugal fans used for RTU supply fans, are less susceptible to motor failures due to overheating at low speeds because of the low torque requirement at low speeds, which reduces the cooling requirement. Because this measure is intended for applications on existing motors, the 40% minimum speed was chosen as a conservative minimum speed for existing motors.

Base Measure with NEMA Premium Supply Fan Motor

This measure includes the base measure in addition to replacement of the existing standard induction motor with a NEMA Premium efficiency motor, which has a higher overall operating efficiency. The minimum motor speed modeled was reduced to 30% for NEMA Premium motors. The 30% minimum was chosen as a conservative minimum speed for new NEMA Premium motors that may or may not be inverter-duty rated. A review of manufacturers’ recommendations indicated that inverter-duty rated motors may be operated at speeds as low as 0.1%. Motor manufacturer minimum speed recommendations for non-inverter-duty rated NEMA Premium motors range from 5% to 20% of the rated speed.

Base Measure with Permanent Magnet Supply Fan Motor

This measure includes the base measure in addition to replacement of the existing standard induction motor with a Permanent Magnet Motor (PMM), which has higher operating efficiency than both standard induction and NEMA Premium motors, especially at reduced speeds.

The minimum motor speed modeled was reduced to 20% for the PMM measure.  The 20% minimum speed was based on engineering estimation of the lowest practical speed for an RTU fan application. According to the only known manufacturer of PMMs compatible with VFDs, there is no practical lower limit to how slowly their motors can be operated [A].

## 1.3 Installation Types and Delivery Mechanisms

Each of the measures detailed in this work paper are intended for retrofit add on (REA) applications.

The delivery and incentive mechanisms for measures contained in this work paper are Financial Support/Downstream Incentive – Deemed and Midstream Programs / Mid-Stream Incentive.

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

The specific measures in this work paper are not included in the Database for Energy Efficient Resources (DEER) 2014 READi Tool v2.0.1. DEER 2005 [26] includes several similar or related measures, but none of them will properly represent the Enhanced Ventilation measures either separately or in combination.

The DEER prototypes for the “110to134kBtuh” cooling capacity range were chosen as the representative prototypes for systems to which the measure would apply. Initially simulations included DEER prototypes for smaller and larger cooling capacities, but savings were not sensitive to small differences in performance for different capacity ranges. Savings variation between the size ranges simulated was minimal, and results from a single size range were determined to be an adequate representation for all applicable system size ranges.

Based on the PGECOHVC168 Demand Controlled Ventilation R0 work paper analysis, the following modifications were necessary to estimate baseline energy use for Enhanced Ventilation and VFD:

- A minimum outside air fraction of 20% was used instead of 0% due to emerging research (not yet published) that indicates closed damper leakage for packaged HVAC systems are higher than previously thought.

- A maximum outside air fraction of 70% was used instead of 100% due to emerging research (not yet published) that indicates return air damper leakage and exhaust air re-entrainment for packaged HVAC systems are higher than previously thought, leading to inability of most systems to provide 100% outside air.

- Economizer dry-bulb changeover temperatures were set in accordance with Title 24 2013 [355] Table 140.4B.

To implement these modifications to the DEER prototypes the specific modifications to eQUEST keywords shown in the table shown below were performed for the baseline.

Baseline modifications to eQuest keywords

| eQuest Keyword | DEER Value | Modified Baseline Value |
| --- | --- | --- |
| SYSTEM:MIN-OUTSIDE-AIR | Varies | 0.2 |
| SYSTEM:MAX-OA-FRACTION | 1.0 | 0.7 |
| SYSTEM:ECONO-LIMIT-T | Varies | Varies by climate zone from 69°F to 75°F depending on Title 24 2013 Table 140.4B requirement |

### Measure Simulations

To develop measure-case energy use and demand estimates the modified baseline files were further modified to simulate application of a VFD to each system for which a VFD retrofit would result in the benefit of reduced air flow.

Measure-case eQUEST keyword modifications

| eQuest Keyword | Baseline Value | Measure Value |
| --- | --- | --- |
| SYSTEM:FAN-EIR-FPLR | One-speed basecase Fan EIR fPLR | - Two-speed standard Fan EIR fPLRTwo - Two-speed NEMA Fan EIR fPLR - Two-speed PMM Fan EIR fPLR |
| SYSTEM:AIR/TEMP-CONTROL | VARIABLE | STAGED-VOLUME |
| SYSTEM:COOL-STAGES[1] | n/a | 0.99 |
| SYSTEM:HEAT-STAGES[1] | n/a | 0.99 |
| SYSTEM:MIN-FLOW-RATIO | 1 | - 0.4 (Standard Motor) - 0.3 (NEMA) - 0.2 (PMM) |
| SYSTEM:MIN-FAN-RATIO | 1 | - 0.4 (Standard Motor) - 0.3 (NEMA) - 0.2 (PMM) |
| SYSTEM:MIN-SUPPLY-T | 50°F | 50°F |
| SYSTEM:MAX-SUPPLY-T | 180°F | 180°F |

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | Yes |
| DEER Version | N/A |
| Reason for Deviation from DEER | DEER does not contain this measure; the DEER building prototypes used in energy models did not deviate from DEER. |
| DEER Measure IDs Used | N/A, however, prototypes from DEER were used: D08-NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer D08-NE-HVAC-airHP-SpltPkg-110to134kBtuh-11p5eer-3p4cop |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | Any | Any | Any | 0.6 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-airAC, HVAC-airHP | Air Conditioners (air-cooled, split and unitary), Heat Pumps (split and unitary) | Com | HVAC | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

This measure is a retrofit to an existing system, and is not governed by either state or federal codes and standards as long as the project does not include other code-triggering activities such as replacement of HVAC systems. However, Title 24 2013 [355] provides economizer control and general ventilation that are considered to be best practice and are provided here for reference.

2013 Title 24 Economizer Control Requirements

| Title 24 Std. Description | Base or Measure Case | Value | Units | Code Source or Reference |
| --- | --- | --- | --- | --- |
| Economizer high limit control | Base Case | High limit shut-off control requirements by device type and climate zone | °F, Btu/lb | Title 24 2013 Table 140.4-B |

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | 2013 Building Energy Efficiency Standards for Residential and Nonresidential buildings, Table 140.4 – B Air Economizer High Limit Shut Off Control Requirements | July 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

1.5.1 Non-DEER Study Review

Data currently being finalized in Work Order 32 EM&V [B] research of HVAC programs informed assumptions for economizer minimum and maximum outside air rate assumptions discussed in 1.4.1.

There are no further data or calculations provided for the support of the measures in this workpaper.

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

## 2.1 Electric Energy Savings Estimation Methodologies

Energy savings and demand reductions were calculated by modeling a base case scenario and a measure case scenario for each of the measures using eQUEST. The savings is the difference in annual electric energy usage, annual gas energy usage, and peak electric power demand between the base case and the measure case.

Enhanced Ventilation and VFD savings may be applied to any unit that meets the program restrictions and guidelines. For units serving building types that are not explicitly included in this work paper, or for units serving a space type that is inconsistent with the building type, the building type whose occupant density and typical schedule most nearly represents it should be selected to estimate savings. For example, a fast food restaurant within a large retail building should claim savings for a fast food restaurant rather than for a large retail building. This ensures that the most accurate savings are applied for a given unit.

The savings calculations represent the average savings per ton of cooling capacity across the population of buildings of a certain type in a given climate zone.

DEER Prototype Models were developed to represent a “customer average” building for each building type, climate zone, and vintage. These models were extracted from the eQUEST DEER model database using the DEER batch processing capability in eQUEST.

Modeling was performed for all climate zones for the six building vintages shown in the table below, DEER Prototype Building Vintages and Abbreviations, and for each of the building types listed in the table shown below, DEER Building Types Modeled. Savings were calculated for each vintage and were weighted by the vintage weights in DEER08 Building Weights.xls [C]. In order to model the large volume of discrete cases considered, eQUEST batch processing was used.

DEER Prototype Building Vintages and Abbreviations

| Vintage | Abbreviated Vintage Name |
| --- | --- |
| Before 1978 | v75 |
| 1978 - 1992 | v85 |
| 1993 - 2001 | v96 |
| 2002 - 2005 | v03 |
| 2006 – 2009 | v07 |
| 2010 – 2011 | v11 |

DEER Building Types Modeled

| Building Type | Abbreviated Building Type |
| --- | --- |
| Assembly | ASM |
| Education: Primary School | EPR |
| Education – Secondary School | ESE |
| Education – Community College | ECC |
| Education – University | EUN |
| Health/Medical – Hospital | HSP |
| Health/Medical – Nursing Home | NRS |
| Lodging – Hotel | HTL |
| Manufacturing – Bio/Tech | MBT |
| Large Office | OFL |
| Small Office | OFS |
| Restaurant – Fast Food | RFF |
| Restaurant – Sit-Down | RSD |
| Retail – 3-Story Large | RT3 |
| Retail – Large | RTL |
| Retail – Small | RTS |
| Storage – Conditioned | SCN |

The modeled building types were chosen because they utilize packaged rooftop units. They also represent the majority of commercial buildings that use packaged rooftop units.

The assumptions and modeling methodologies used for the base case and each of the measures are detailed below. This section refers extensively to eQUEST/DOE-2 keywords, which are defined and detailed in the DOE-2 Dictionary [D].

### Base Case

The base case models are the DEER “customer average” building prototypes. They were modified to update the weather file from Typical Meteorological Year Version 2 (TMY2) to TMY3 weather data in an effort to use the most recent and relevant weather data available.

Besides the weather file modification, all of the Vintage 75 prototypes were modified to include economizer operation with a fixed outdoor air dry bulb temperature limit in accordance with Title 24 as shown in the figure shown below. The default prototypes for Vintage 75 assume a fixed outdoor air damper, while all of the other prototypes use a high dry bulb economizer limit in accordance with Title 24. The economizer adjustment to the Vintage 75 prototypes reflects the assumption that the economizer of the unit in question was repaired and properly configured prior to installation of any of these measures.

Title 24 Economizer High Limit Requirements

### VFD Fan Control with Motor Power Interaction

To simulate the addition of the variable frequency drive, a custom fan power curve was developed using data from a bench test of 3 horsepower (HP) versions of each of the three types of motors considered in this work paper. The bench test used was performed by ADM Associates [E] for the Sacramento Municipal Utility District (SMUD) [F]. At the present time, the NovaTorque Premium Plus is the only PMM designed to operate with a belt driven fan and VFD. This report is particularly applicable since the 3HP motor size is often found on units from 7.5 to 12.5 tons, which is only slightly larger than the smallest units typically serviced in the HVAC Optimization program.

In the bench test report, a typical centrifugal fan curve was used to select the operating points from the bench test data for each of the three motors. The efficiency comparison graph shown in the figure shown below depicts combined motor and VFD efficiency in a fan application.

Combined Motor and VFD Efficiency for 3 HP Standard, Premium, and PMM Motors

These curves were fit with a cubic polynomial and combined motor and VSD efficiency as a function of percent motor speed. Belt efficiency was also considered, and an additional belt efficiency curve was developed based on data in the BC Hydro Guide to Flexible Drives [G].

The required percent motor power as a function of percent speed was then calculated by dividing the ideal motor power by the VFD and motor efficiency and V-Belt efficiency. This resulted in the three fan power curves shown in the figure shown below. Ideal fan power is included as a comparison to the three curves developed for this work paper. Development of the three curves including belt efficiency is documented in the embedded workbook Fan Power Curves.xls [H].

Fan Power Curves for Standard, Premium, and PMM Motors

Note that the PMM curve extends down to 20% speed, the NEMA Premium to 30%, and the Standard to 40% speed. This reflects the recommended minimum turndown for each type of motor. The minimum recommended turndown was chosen as a conservative number to lower the risk of motor burnout. NovaTorque indicated that the PMM can be turned down to 10% speed with no risk of motor failure, so a 20% minimum was chosen to maintain a conservative savings estimate. These curves also reflect the additional power at full load introduced by the addition of the VFD. The yellow dot at the upper right indicates the base case motor power requirement at full speed for comparison to the three measure cases with the efficiency of the VFD included. The addition of a VFD raises the motor power required at 100% speed to levels higher than the baseline for the standard and NEMA Premium motors, but the improved efficiency of the PMM results in slightly reduced power consumption at full speed even with the addition of a VFD.

In order to simulate fan operation of 2-speeds, the STAGED-VOLUME capability of eQUEST was used. This function allows an air handling unit to operate at different flow rates depending on the heating and cooling demand. The modes that the unit will operate in are: floating (ventilation only), economizer cooling, or full heating/cooling. This function allows the capability of staged capacities, but for the purpose of this measure, one stage of either heating or cooling was used. The energy calculations in eQUEST are on an hourly basis. The unit can operate in various modes during this hour. The calculations account for this through summation of each fraction of an hour per mode to meet space loads. For each mode the air flow and associated part load ratio for the fan will be different. The part load ratio is calculated based on the appropriate fan curve. Fan curves were developed from the PGECOHBC143R0 work paper. Instead of having to develop a fan curve that incorporated the 2-speed fan characteristics, the original fan curves could be used. Hourly reports were verified to ensure the model was operating at discrete flow rates. The following calculation is the method in which eQUEST calculates the part load fan ratio per hour.

PLRfan averaged hour=%hourfloat mode×PLRfloat mode+%hourecon mode×PLRecon mode+%hourclg/htg mode×PLRclg/htg mode

%hourfloat mode+%hourecon mode+%hourclg/htg mode=1

Supply Flow versus Part Load Fan Ratio

There is a similar relationship for the system supply flow. To demonstrate, the economizing mode was disabled. Therefor the relationship between supply and part load fan ratio is linear. This is demonstrated by the following relationship. The figure shown above shows the expected linear relationship between supply flow and fan part load ratio developed from simulation hourly reports.

∴Supply Flowaveraged hour=Flowfloat mode+%hourclg/htg modeFlowclg/htg mode-Flowfloat mode

Since the intent was not to simulate fan speed that varies continuously, but rather multiple discrete speed operation varying according to the operating mode of the unit, eQUEST/DOE-2 keywords were selected to limit the fan’s speed and power behavior to closely mimic the intended multiple speed operation. Cooling speed was set at a minimum of 90% speed or the speed that results in no less than 50 °F supply air temperature using the CMIN-FLOW-RATIO and MIN-SUPPLY-T keywords. Heating speed was set at a minimum of 90% speed or the speed that results in no more than 180 °F supply air temperature using the HMIN-FLOW-RATIO and MAX-SUPPLY-T keywords. The ventilation only speed, MIN-FLOW-RATIO, was set to the maximum of 40% for standard induction motors, 30% for NEMA Premium motors, and 20% for PMMs.

The custom fan power curves were used to simulate the three different motor types. Specifically, the cubic polynomial coefficients for the existing models were modified in the batch processor to reflect the coefficients for a cubic polynomial fitted to each fan power curve shown in the figure, Fan Power Curves for Standard, Premium, and PMM Motors.

The following was used for per ton of cooling capacity electric savings calculations. For building types that had multiple system types, the cooling capacity corresponds to the total capacity of the only the systems that were changed.

kWh per ton savings=baseline kWh-measure kWhcooling tons

Where:

kWh per ton savings = annual unit energy savings

baseline kWh = annual building energy consumption of customer average baseline

measure kWh = annual building energy consumption of measure

cooling tons = cooling capacity of units measure was applied to (Btu/h) divided by 12,000 (Btu/h per ton)

## 2.2. Demand Reduction Estimation Methodologies

Demand reduction is calculated similarly to electric energy savings, however there is an additional calculation step required to estimate peak demand reduction in accordance with DEER peak period definitions. The DEER demand reduction estimation protocol requires average hourly peak demand from a defined time period that varies by climate zone to be determined for the baseline and measure. The time period defined by climate zone is shown in the table shown below [I].

DEER 2014 Peak Demand Periods

| CZ | start month | start day | end month | end day | start hour | end hour |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 9 | 16 | 9 | 18 | 15 | 17 |
| 2 | 7 | 8 | 7 | 10 | 15 | 17 |
| 3 | 7 | 8 | 7 | 10 | 15 | 17 |
| 4 | 9 | 1 | 9 | 3 | 15 | 17 |
| 5 | 9 | 8 | 9 | 10 | 15 | 17 |
| 6 | 9 | 1 | 9 | 3 | 15 | 17 |
| 7 | 9 | 1 | 9 | 3 | 15 | 17 |
| 8 | 9 | 1 | 9 | 3 | 15 | 17 |
| 9 | 9 | 1 | 9 | 3 | 15 | 17 |
| 10 | 9 | 1 | 9 | 3 | 15 | 17 |
| 11 | 7 | 8 | 7 | 10 | 15 | 17 |
| 12 | 7 | 8 | 7 | 10 | 15 | 17 |
| 13 | 7 | 8 | 7 | 10 | 15 | 17 |
| 14 | 8 | 26 | 8 | 28 | 15 | 17 |
| 15 | 8 | 25 | 8 | 27 | 15 | 17 |
| 16 | 7 | 8 | 7 | 10 | 15 | 17 |

Hourly peak demand from the nine hours defined for each climate zone is averaged for each climate zone. The following equation is then used to determine demand reduction per ton of cooling capacity.

kW per ton demand reduction=baseline kW-measure kWcooling tons

Where:

kW per ton savings = annual unit demand reduction

baseline kW = average demand for DEER peak period of customer average baseline

measure kW = average demand for DEER peak period of measure

cooling tons = cooling capacity of units measure was applied to (Btu/h) divided by 12,000 (Btu/h per ton)

## 2.3 Gas Energy Savings Estimation Methodologies

Gas energy savings are calculated similarly to electric energy savings. The gas energy savings from the first baseline are represented in the calculations below.

therms per ton savings=baseline therms-measure thermscooling tons

Where:

therms per ton savings = annual unit energy savings

baseline therms = annual building energy consumption of customer average baseline

measure therms = annual building energy consumption of measure

cooling tons = cooling capacity of units measure was applied to (Btu/h) divided by 12,000 (Btu/h per ton)

## 2.4 Vintage Weighted Average

Baseline and measure simulations used prototypes for the following 6 DEER vintages: v75, v85, v96, v03, v07, and v11. The weighted average electric and gas energy savings, and demand reduction for application of the measure to any vintage were then developed using DEER 2014 vintage weighting tables and procedures. The following equation provides the methodology used to apply the DEER 2014 weights.

final weighted value=i=7507Wi ×Vii=7507Wi

Where:

final weighted value=reported UES value (kWh/ton, kW/ton, or therms/ton)

i=vintage 75, 85, 96, 03, 07, or 11

W=Weight for a given vintage i

V=UES Value for a given vintage (kWh/ton, kW/ton, or therms/ton)

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | Reduce_Cooling_Load-Ret | Large_Office |
| Education – Community College | Reduce_Cooling_Load-Ret | College_University |
| Education – Primary School | Reduce_Cooling_Load-Ret | Small_Office |
| Education – Secondary School | Reduce_Cooling_Load-Ret | Small_Office |
| Education – University | Reduce_Cooling_Load-Ret | College_University |
| Health/Medical – Hospital | Reduce_Cooling_Load-Ret | College_University |
| Lodging – Hotel | Reduce_Cooling_Load-Ret | Hotel_Motel |
| Health/Medical – Nursing Home | Reduce_Cooling_Load-Ret | Small_Office |
| Manufacturing Biotech | Reduce_Cooling_Load-Ret | Industrial |
| Office – Large | Reduce_Cooling_Load-Ret | Large_Office |
| Office - Small | Reduce_Cooling_Load-Ret | Small_Office |
| Restaurant – Fast Food | Reduce_Cooling_Load-Ret | Small_Office |
| Restaurant – Sit-Down | Reduce_Cooling_Load-Ret | Small_Office |
| Retail – Multistory Large | Reduce_Cooling_Load-Ret | Large_Retail_Store |
| Retail – Single-Story Large | Reduce_Cooling_Load-Ret | Large_Retail_Store |
| Retail – Small | Reduce_Cooling_Load-Ret | Small_Retail_Store |
| Storage – Conditioned | Reduce_Cooling_Load-Ret | Misc._Commercial |

# Section 4. Costs

## 4.1 Base Case Cost

The following Measure Application Types is are appropriate to these measures. The Base Case Costs are:

Base Case Cost Data

| Measure Codes | Measure Application Type | Baseline | Equipment Cost ($) | Labor / Installation Cost ($) | Maintenance / Other Cost ($) | Total Base Case Cost ($) |
| --- | --- | --- | --- | --- | --- | --- |
|  | REA | Existing | 0 | 0 | 0 | 0 |

All costs are noted as $ per measure unit

Since this is an REA application for a retrofit on existing equipment, the base case cost is zero.

## 4.2 Measure Case Cost

To develop measure cost estimates a combination of retail, manufacturer suggested retail, and distributor prices were gathered for ADEC, VFD controllers, and motors made by multiple manufacturers. Cost data related to ADEC was developed based on cost information from PGECOHVC168 Demand Controlled Ventilation R0. A base labor rate of $86.93 per hour was used, and was adjusted to account for local variation. A weighted average cost for the state was developed based on the methodology used for the Draft DEER Measure Cost Update [J]. The base labor rate and adjustments are in alignment with the methodology presented in the Draft DEER Measure Cost Update. As a controls upgrade, measure costs do not scale strongly with cooling capacity. To reference cost with the same base unit as UES values (per ton) an average capacity of 12.5 tons was assumed to be the average capacity to which the measure would be applied. Detailed cost calculations are documented in ENV_VFD+ADEC cost data.xlsx [K].

Measure Case Cost Data

| Measure Codes | Measure | Measure Material Cost ($) | Labor Cost ($) | Measure Cost ($) | Avg. tonnage | Measure Material Cost ($/ton) | Labor Cost ($/ton) | Measure Cost ($/ton) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AC-72014, AC-14815, AC-18726 | Add VFD to unit with ADEC | $964.40 | $402.67 | $1,367.08 | 12.5 | $77.15 | $32.21 | $109.37 |
| AC-97565, AC-30287, AC-36894 | Add VFD and NEMA motor to unit with ADEC | $1,452.36 | $704.68 | $2,157.04 | 12.5 | $116.19 | $56.37 | $172.56 |
| AC-63277, AC-67253, AC-32399 | Add VFD and PMM to unit with ADEC | $1,571.89 | $704.68 | $2,276.57 | 12.5 | $125.75 | $56.37 | $182.12 |
| AC-42889, AC-32686, AC-71385 | Add VFD and ADEC to unit | $1,778.68 | $805.35 | $2,584.03 | 12.5 | $142.29 | $64.43 | $206.72 |
| AC-88048, AC-70123, AC-28655 | Add VFD, NEMA motor, and ADEC to unit | $2,266.63 | $1,107.36 | $3,373.99 | 12.5 | $181.33 | $88.59 | $269.92 |
| AC-52735, AC-62985, AC-12899 | Add VFD, PMM, and ADEC to unit | $2,386.16 | $1,107.36 | $3,494.52 | 12.5 | $190.89 | $88.59 | $279.48 |

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| AC-72014, AC-14815, AC-18726 | REA | $109.37 | $109.37 | N/A |
| AC-97565, AC-30287, AC-36894 | REA | $172.56 | $172.56 | N/A |
| AC-63277, AC-67253, AC-32399 | REA | $182.13 | $182.13 | N/A |
| AC-42889, AC-32686, AC-71385 | REA | $206.72 | $206.72 | N/A |
| AC-88048, AC-70123, AC-28655 | REA | $269.92 | $269.92 | N/A |
| AC-52735, AC-62985, AC-12899 | REA | $279.48 | $279.48 | N/A |

# Attachments

# References

[26]

[62]

[355]

[A] Personal communication (phone call) with Shams Shaikh of NovaTorque, Inc.

[B] KEMA. Impact Evaluation Research Plan, WO032—Residential and Small Commercial HVAC. Oakland, CA. (April 2012) Retrieved 4/24/2014 from

http://www.energydataweb.com/cpucFiles/93/WO032HVACResearchPlan_2.pdf

[C] DEER08 Building Weights.xls

[D] James J. Hirsch & Associates, DOE-2.2 Building Energy Use and Cost Analysis Program Volume 2: Dictionary. Lawrence Berkeley National Laboratory, December 2009

[E] ADM Associates, NovaTorque Brushless Permanent Magnet Motor Bench Test Final Report. Sacramento Municipal Utility District, 2010

[F] Install/Program Type (Courtesy of SCE Strategic Planning and Technical Services, from rev4 Install/Program Type document 11/8/11)

[G] BC Hydro: Guides To Energy Management M310: Flexible Drives. BC Hydro

[H] Fan Power Curves.xls

[I] James J. Hirsch & Associates. (2014, February 11). DEER2014 — Codes and Standards Update. Retrieved from deeresources.com: http://deeresources.com/files/DEER2013codeUpdate/download/DEER2014UpdateDocumentation_2-12-2014.pdf

[J] Itron. 2010-2012 WO017 Ex Ante Measure Cost Study Draft Report. San Francisco, CA (2014, February 28). Retrived 4/24/2014 from

http://www.energydataweb.com/cpucFiles/pdaDocs/1039/2010-2012%20WO017%20Ex%20Ante%20Measure%20Cost%20Study%20-%20Draft%20Report.pdf

[K] PECI, ENV_VFD+ADEC cost data.xls. 5/29/2014