Work Paper SCE15HC052

Revision 2

Southern California Edison

Efficient Fan Controller for Residential Air Conditioners and Furnaces

For Work Paper Reviewer Use Only

List all major comments that occurred during the review. This table may only be removed during management review.

| Major Comment | Reviewer Name | Date | Outcome/Resolution |
| --- | --- | --- | --- |
| E.g. Please remove measure LT-12345 (LD123) from this work paper because it is no longer eligible for incentives. | Reviewer 1 | 6/1/15 | E.g. Comment incorporated. LT-12345 was removed. |

# At-a-Glance Summary

| Measure Codes | AC-48754 – Air Conditioner – Efficient Fan Control |
| --- | --- |
| Measure Description | Fan controller device using built-in logic to delay the evaporator fan cycle off time. |
| Base Case Description | Split-system air-conditioner with fan cycling off at the same time as the compressor. |
| Units | Per unit (PG&E) Per ton (SCE) |
| Energy Savings | Refer to Excel Calculation Attachment. |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment. |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment. |
| Effective Useful Life | 5 years (HVAC-FlowCtrl-AirFiltCtrls) |
| Measure Installation Type | REA |
| Net-to-Gross Ratio | 0.85; ET-Default |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 08/24/12 | Brian James/SCE | Original work paper |
| 1 | 04/01/14 | Ray Phillips/PECI | Update using the latest DEER eQUEST prototypes (via MASControl). - Update to include all 16 CA climate zones - Update kW and kWh savings |
| 2 | 01/04/2016 | Andres Fergadiotti/SCE | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -No value modifications -Added solution Code for Fan Controller – Smart (Programmable) T-Stat -Workpaper converted over to SCE template |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper outlines the retrofit add-on of an efficient fan controller (EFC) device onto a residential single-family, multi-family or double-wide mobile home split-system air conditioner or gas furnace. The base case is a 14 SEER AC unit without an EFC.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Installation of efficient fan controller or thermostat with an efficient fan controller to control fan after standard cooling or heating cycles |
| Existing Condition | Split-system air conditioning unit with indoor evaporator coil or ducted natural gas furnace without a built-in fan delay. |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | AC-48754 |  | Air Conditioner - Efficient Fan Control |

Eligibility Requirements:

This measure only applies to residential split-system air conditioning units with an indoor evaporator coil. The baseline air conditioning system cannot have built-in delay.

Implementation Requirements:

This work paper only allows the installation of an automated fan controller, unless the manually-set time-delay fan controller is set and commissioned by a trained contractor. This measure can be installed in single family, multi-family, and double-wide mobile homes in all SCE climate zones.

Documentation Requirements

There are no documentation requirements at this time.

## 1.2 Technical Description

EFC devices delay the evaporator fan cycle off time to take advantage of the residual liquid refrigerant remaining in the evaporator after the compressor cycles off. The controller can delay the fan cycle off time either by allowing the user to set the time delay period, or by using built-in logic to delay the fan cycle off time based on the compressor run time. This work paper only allows the installation of a fan controller with built-in logic, heretofore after referred to as “automated fan controller,” unless the manually set time delay is set and commissioned by a trained contractor.

## 1.3 Installation Types and Delivery Mechanisms

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | Yes |
| Scaled DEER measure | No |
| DEER Base Case | Yes |
| DEER Measure Case | No |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | Yes, with modifications; see below |
| DEER Version | DEER, 2014, DEER 2015, READI v2.3.0 |
| Reason for Deviation from DEER | Packaged Variable Volume Variable Temperature HVAC system was changed to Package Single Zone to reflect a typical residential building with a single zone |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| ET-Default | Emerging Technologies approved by ED through work paper review | All | Any | Any | 0.85 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.  Note that this measure assumes an EUL based on the RUL of the HVAC system affected by the REA measure as described below. The EUL of the measure is capped at the remaining useful life of split and package equipment, or a third of 15 years, as it is assumed that the controller would be removed with the equipment once it reaches its remaining useful life.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| HVAC-FlowCtrl-AirFiltCtrls | Air Filter Alarm | Res | HVAC | 5 | 1.67 |

### 1.4.2 Codes and Standards Analysis

There are currently no federal, state, or regional codes that impact efficient fan controllers for residential AC. However, starting in 2015 federal code requires a residential AC unit installed in California to have a SEER (Seasonal Energy Efficiency Ratio) rating of at least 1 [B]. This efficiency rating was used to establish the baseline AC unit for this measure. For application in 2014 programs the savings are slightly conservative as the 2014 code requires SEER 13.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | N/A | N/A |
| Title 20 (2014) | N/A | N/A |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### 1.5.1 Non-DEER Study Review

ET11SCE1130 tested a nominal 3-ton split air-conditioning unit in a laboratory setting where the unit was equipped with an air-cooled condenser and a single speed compressor. This combination of components is representative of one of the most common configurations of air-conditioning units found in residential applications. The measure evaluation portion of the testing included the installation of the two types of commercially available add-on delay controllers. The two fan controllers allowed the fans to run after the compressor was shut off, but one ran for a prescribed period of time while the other had a built-in logic to delay for a period of time based off of the compressor’s run time. The projects findings were used for subsequent analysis using eQuest to perform multiple simulations across California climate zones. The full report can be viewed in the attached file “ET11SCE1130_Evap Fan Delay_Final.pdf” found below.

1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Energy savings was calculated using eQuest v3.64 to establish the baseline energy consumption then applying the part load ratio curve fit equation from the ET report [A]. The eQuest simulations used a minimally above-code SEER 14 split-AC system to be slightly conservative. The cooling capacity varied by building type and climate zone based on the DEER building prototypes for double-wide mobile home, multi-family, and single family residential buildings. The DEER building prototypes are the most recent updates to include the Title 24 2008 [208] and Title 24 2013 [355] code based vintages. These new prototypes were the models that were used in conjunction with revised weather data files to provide the energy savings for the measure. Four hourly variables were captured from the eQuest simulations for a year: total cooling load (Btu/hr), condensing unit energy (kWh), supply (indoor) fan energy (kWh), and AC total cooling capacity (Btu/hr). The total AC energy usage was calculated by equation 1:

Equation 1

Total Baseline AC Energy Usage kWh=Condensing Unit EnergykWh+Supply Fan Energy (kWh)

The part load ratio was determined by equation 2:

Equation 2

Part Load Ratio=Total Cooling Load(Btuhr)AC Total Cooling Capacity (Btuhr)

Once the Part Load Ratio (PLR) is obtained, equation 3 applies the logarithmic curve fit of percentage of energy savings versus part load ratio determined from laboratory testing. See Figure 11 on page 15 of the attached report [A].

Equation 3

AC Energy Savings kWh=Total Baseline Energy Usage kWh×(-0.2lnPLR+0.0006)

The result from equation 3 is AC energy savings for each hour. This number is summed for all hours of the year to obtain the total energy savings. Results were obtained for each zone (each with a separate split-AC system) as specified in the DEER building prototypes. There were 2 systems (N-S, E-W orientations) in double-wide mobile homes 4 systems in single-family homes (single-story, two-story, two orientations), and 24 systems in multi-family homes (two-story buildings with 12 units, two orientations). The results obtained for each of the building prototypes were averaged to obtain one representative savings number per building type.

For a sample calculation, consider a double-wide mobile home in climate zone 6 with a N-S orientation at 5:00 PM on July 9 per the example cooling calculation spreadsheets in Attachments 7 and 8. First solve equation 1:

0.972 Total Baseline AC Energy Usage kWh=0.863 Condensing Unit EnergykWh+0.109 Supply Fan Energy (kWh)

Next, solve for the PLR with equation 2:

0.476 Part Load Ratio=12,078 Total Cooling Load(Btuhr)25,358 AC Total Cooling Capacity (Btuhr)

Lastly, solve for the AC energy savings for that hour with equation 3:

0.145 AC Energy Savings kWh=0.972 Total Baseline Energy Usage kWh×(-0.2ln0.476+0.0006)

This process is repeated for all 8,760 hours in the year and summed to obtain the total annual energy savings for the EFC controller of each DEER building prototype. The annual energy savings were then normalized by cooling capacity using actual tonnage for each unit examined within each prototype for SCE. For PG&E, the savings are normalized to a “per unit” value using tonnages for each building type extracted from the MASControl tool. These tonnages are 3.184, 2.123, and 1.122 for single family, double wide mobile home, and multi-family, respectively. Results for all zones or systems were simple averages for each building type and orientation. As an example of the energy savings, for a double-wide mobile home in CZ 13, the calculated energy savings were 113.63 kWh/ton annually. (The mobile home energy savings is currently being represented by the single family home savings until DEER mobile family prototypes are available with post 2008-2013 Title 24 Code updates.) The savings are converted to a per unit basis as follows for PG&E:

241.24 AC Energy Savings kWh/unit=113.63 AC Energy Savings (kWh/ton)×(2.123 tons/unit)

Demand Reduction Calculations

Since hourly values of AC energy savings were available for one full year, demand reduction was calculated by summing the total energy consumed during the peak demand period for the specific summer weekday periods delineated by climate zone, 2:00 PM to 5:00 PM as set forth in CPUC Decision D06-06-063. The total energy consumption during this period was then divided by nine, the number of peak hours, as shown in equation 4. The AC Energy Savings During Peak Period was normalized by cooling capacity using actual tonnage from the DEER prototypes:

Equation 4

Demand Reduction kW=AC Energy Savings During Peak Period(kWh)Total Hours in Peak Period (hr)

Using the previous example of a double-wide mobile home in CZ 13, whose peak period falls between 2:00 PM and 5:00 PM, July 8-10 we obtain the following results after applying equation 4:

0.0687 Demand Reduction kW=AC Energy Savings During Peak PeriodkWh=0.6189 Total Hours in Peak Period (hr)

This value is averaged with the E-W orientation to obtain a final peak demand reduction of 0.0687 kW.

See attachments 2, 3, and 4 for detailed energy savings and demand reduction calculations [D, E, F].

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Residential – Double-Wide Mobile Home | DEER:HVAC_EFF_AC | RES |
| Residential – Multi-Family | DEER:HVAC_EFF_AC | RES |
| Residential – Single Family | DEER:HVAC_EFF_AC | RES |

# Section 4. Costs

## 4.1 Base Case Cost

For REA measures, there is no base case cost as the measure is being added onto the existing equipment.

## 4.2 Measure Case Cost

The measure equipment material cost was determined by reviewing the purchased price for two fan delay controllers tested in the ET laboratory report [A]. The price paid was $25 per controller, plus $3.50 for shipping and handling. The price was cross-referenced with Southern California Gas Company’s work paper SCG0077.0 California HVAC Upgrade: Efficient Fan Controller (EFC) – Residential, which listed the material equipment cost at $25. The controller cost is also normalized on a per-ton basis using the average rated capacities of the HVAC systems in the DEER eQuest models for DMO, MFM, and SFM. The average rated capacities for DMO, MFM, and SFM are 2.123, 1.122, and 3.184 tons, respectively. The combined average rated capacity used to calculate the average cost per ton is 2.14 tons. This results in an average equipment cost of $13.32 per ton.

The measure labor cost was determined from “Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls.” The base labor rate is $67.88 per hour for the residential sector for downstream prescriptive rebates/incentives. Installation of the fan controller takes 1-2 hours, so the labor cost is estimated at $135.76. Normalized per ton, the measure labor cost is $63.44. Refer to Attachment 5 for the cost calculation [G].

Measure Case Cost= Measure Equipment Cost + Measure Labor Cost

= $28.50+ $135.76

= $164.26/unit

Measure Case Cost= Measure Equipment Cost + Measure Labor Cost

= $13.32+ $63.44

= $76.76/ton

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| AC-48754 | REA | $76.76 | $76.76 | N/A |

# Attachments

- Efficient_Fan_Controller_for_Residential_Air_Conditioners_SFM_Results_v4.xlsb (available upon request due to size)

- Efficient_Fan_Controller_for_Residential_Air_Conditioners_MFM_Results_v4.xlsb (available upon request due to size)

- Efficient_Fan_Controller_for_Residential_Air_Conditioners_DMO_Results_v4.xlsb (available upon request due to size)

# References

[208]

[355]

- Effects of Delaying Evaporator Fan Cycle Off Time for Residential Air-Conditioning Units. Design and Engineering Services, Emerging Technologies Program. March 20, 2012. - Attachment

- Energy Conservation Standards for Residential Central Air Conditioners and Heat Pumps http://www1.eere.energy.gov/buildings/appliance_standards/residential/residential_cac_hp.html

- Attachment 1. Calculation Template 2015 v4.xlsm

- Attachment 2. Efficient_Fan_Controller_for_Residential_Air_Conditioners_SFM_Results_v4.xlsb

- Attachment 3. Efficient_Fan_Controller_for_Residential_Air_Conditioners_MFM_Results_v4.xlsb

- Attachment 4. Efficient_Fan_Controller_for_Residential_Air_Conditioners_DMO_Results_v4.xlsb

- Attachment 5. Cost Calcs.xlsx