Work Paper SCE13HC055

Revision 0

Southern California Edison Company

Circulating Block Heater

# At-a-Glance Summary

| Solution and Measure Codes: | PR-14541, PR-28785, PR-26010, PR-90678, PR-64293, PR-54146, and PR-84587, PR-93262, PR-93796, PR-92194, PR-97000, PR-69302, PR-75840, PR-82783 |
| --- | --- |
| Measure Description: | The energy efficiency measure will include adding a recirculation pump with a downsized electric resistance heater to a backup generator. |
| Base Case Description: | The existing thermo siphon heater relies on the change in density, buoyancy, to circulate the heated coolant within the generator. |
| Units: | Per Unit |
| Energy Savings: | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit): | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life: | 15 years (EUL ID: Motors-pump) |
| Measure Installation Type: | Replace on Burnout (ROB), and New Construction(NEW) |
| Net-to-Gross Ratio: | 0.85 (DEER NTGR ID: ET-Default) |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/2014 Ex Ante Database Specification provided by the California Public Utilities Commission (CPUC) Commission Staff (CS); SCE will provide that data set separately. |

# Document Revision History

| Revision # | Revision Date | Author (Affiliation) | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 9/19/2014 | Alfredo Gutierrez & Richard Song(SCE) | Original Work Paper for 13-14 Program Cycle. |

# Section 1: General Measure & Baseline Data

## 1.1 Measure Description & Background

The measure is a circulating block heater used on backup diesel generators. This measure will replace an existing thermo siphon heater with a recirculation pump and a smaller electric resistance heater. The measure will be tiered based upon the backup generator sizes shown below:

•	37-199 kW

•	200-799 kW

•	800-1099 kW

•	1100-2500 kW

The measures contained within this work paper can be found in the table below.

Table 1: Measures and Codes

| Solution Code | Measure Code | Measure Name |
| --- | --- | --- |
| PR-14541 | N/A | 37-199 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater |
| PR-28785 | N/A | 200-799 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater |
| PR-26010 | N/A | 800-1099 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater |
| PR-90678 | N/A | 1100-2500 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater |
| PR-64293 | N/A | 37-199 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater |
| PR-54146 | N/A | 200-799 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater |
| PR-84587 | N/A | 800-1099 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater |
| PR-93262 | N/A | 37-199 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater (New) |
| PR-93796 | N/A | 200-799 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater (New) |
| PR-92194 | N/A | 800-1099 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater (New) |
| PR-97000 | N/A | 1100-2500 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater (New) |
| PR-69302 | N/A | 37-199 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater (New) |
| PR-75840 | N/A | 200-799 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater (New) |
| PR-82783 | N/A | 800-1099 kW Backup Generator with Circulating Block Heater replacing Properly Sized Thermosiphon Heater (New) |

Eligibility Requirements

- Existing backup generator (ROB) is eligible for incentive if it is not currently fitted with a Circulating Block Heater or device utilizing similar electro-mechanical system to heat generator block pre-warming fluid.

- New generator installation (NEW) where base design prescribes a pre-heating device other than Circulating Block Heater or similar device may also apply for incentive to upgrade from base design to efficient design including a Circulating Block Heater.

Implementation Requirements

- Installation of Circulating Block Heater should be performed by a qualified technician (i.e. generator maintenance technician or mechanical service technician).(ROB)

- Installer should assess and perform (if necessary) fluid hose adjustments that may be associated with the retrofit to enable the Circulating Block Heater to function at optimal energy efficiency. (ROB)

- These measures are approved the building types shown in Table 9 for all SCE climate zones.

## 1.2 Technical Description

This technology has an integrated electric pump that circulates coolant throughout the engine block ensuring that there is a minimal temperature difference between the supply and return temperatures. The pump/heater (CBH) is an integral assembly. The existing thermo siphon heater is removed as a unit and the new CBH is inserted into the exact same location. It is a single unit installation within one housing with the mechanical element (pump) enclosed in the same "shell" as the smaller resistance heating element (relative to the thermo siphon) integral to the circulating block heater. Disconnect and reconnect points to existing hoses would not change unless improperly plumbed in the first place.

Along with the pump, a small resistance heater is used to heat the coolant within the engine block. When actual installations are completed, field inspections will verify if the existing resistance heater was replaced with smaller resistance heaters. By pumping the heated coolant, a more uniform temperature is obtained throughout the engine block. As a result of using a recirculation pump, a smaller electric resistance heater can be used to heat the coolant as there will be a more uniform temperature achieved through the mixing of fluid throughout the engine block.

The base case equipment is a thermo siphon heater. These types of heaters rely on the change in density (impacting buoyancy) in order to circulate the heated coolant. This type of circulation leads to non-uniform temperature distribution, where the coolant is warmer at the top of the block and colder at the bottom, which requires the electric resistance heater to operate for a longer duration. This also means that there is waste heat in sections of the block, as the heater must operate to maintain a certain temperature, so the top of the block will always be hotter than necessary.

## 1.3 Installation Types and Delivery Mechanisms

See Appendices A and B for definitions of installation types and delivery mechanisms.

The delivery method is:

- Financial Support - Down Stream Incentive – Deemed

The application type is Replace on Burnout (ROB), and New Construction (NEW).

## 1.4 Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

Currently, DEER does not address this type of measure. Also, DEER interactive effects will not be used as most backup generators are kept in non-conditioned or exterior spaces.

Table 2: DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Referenced versions of DEER and READI | N/A |
| Summary of deviation from DEER | DEER does not contain this type of measure. |
| DEER measures scaled? | No |
| DEER eQUEST prototypes used? | No |
| DEER operating hours used? | No |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

Table 3: Net-to-Gross Ratio

| NTGR ID | Description | Sector | BldgType | ProgDelivID | NTG |
| --- | --- | --- | --- | --- | --- |
| ET-Default | Emerging Technologies approved by ED through work paper review | All | Any | Any | 0.85 |

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

Table 4: Installation Rate

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Technology Fields

The Technology Fields were obtained from the Ex Ante Database Specification. The relevant Use Category, Use Sub-category, Technology Group, and Technology Type values for the measures in this work paper are in the table below.

Table 5: Technology Fields

| Classification | Value |
| --- | --- |
| Measure Case UseCategory | Process Heat |
| Measure Case UseSubCats | Preheating of liquids/solids |
| Measure Case TechGroups | Liquid Circulation |
| Measure Case TechTypes | Flow Plus Temperature Controls |
| Base Case TechGroups | Liquid Circulation |
| Base Case TechTypes | Temperature Reset Control |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

Table 6: EUL and RUL

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| Motors-pump | Water Loop Pumps | Com | Process | 15 | 5 |

### 1.4.2 Codes and Standards Analysis

Currently, both the 2013 Title 24 [355] and the 2014 Title 20 [422] energy codes do not cover the use or installation of circulating block heaters.

Please note that the Air Quality Management District (AQMD) does set standards regarding what the definition of an emergency backup generator actually is and the allowable air emissions from backup generators. However, the allowable emissions do not impact savings calculations as backup generators are required to be ready at all times for use. Emission standards are not covered in this work paper.

Table 7: Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | N/A | N/A |
| Title 20 (2014) | N/A | N/A |
| AQMD | N/A | N/A |

### 1.4.3 Non-DEER Study Review

The savings for the measures contained within this work paper are based on field monitoring data from the Bonneville Power Administration (BPA). This data was collected from numerous case studies that ran through the BPA’s Emerging Technology program. The data collected included average daily kWh and outside air (OA) temperature for both the preexisting thermo siphon heater and the retrofitted circulating block heater [A]. There are 17 sources of data, which are taken from different sites including waste water plants and data centers. The data was collected for different periods of time for each site, but on average, there are 2 months pre and post for each site used in the regression analysis performed for this work paper.

The Emerging Products study ET08SCE1020 “Air Source Heat Pump for Preheating of Emergency Diesel Backup Generators” [491] investigated the used of using air source heat pumps for this measure, but found that the use of air source heat pumps was not cost effective. This study serves to show that the current measures within this work paper were facilitated through SCE’s ET program, utilizing data from BPA that was analyzed through the ET program.

# Section 2: Calculation Methodology

The savings for the measures in this work paper are found from BPA field monitored case study data referenced above. The BPA case studies provide OA temperature and daily average kWh for both the pre-existing thermo siphon heater and the measure. The data provided was then used to create multiple regression models for the different generator sizes where this measure will be offered. These regression models, along with the circulating block heater tool used for SCE’s customized program can be found in attachment 2. The raw data used to generate the regression models has not been attached to this work paper due to size limitations, however, it is available upon request.

DATA EXPLORATION

Temperature and Daily kWh Variation within Size Categories

While sites are assigned a size category of 1-4, this categorization corresponds only very loosely to the actual (baseline) usage, and is highly dependent on baseline heater size.  There is significant variation and overlap across categories in generator size, heater size, and observed kWh usage.

Table 8: Site-Specific Heater Sizes

| Site | Site Size Category | Generator Size kW | Baseline Heater Size kW | Existing Measured kW | Avg Baseline kWh | New Rated Heater Size kW | New Measured kW | Avg Treatment kWh |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| COCCH | 1 | 15 | 0.5 | 0.46 | 11.0 | 1 | 0.99 | 6.8 |
| Kid Kare | 1 | 40 | 1 | 0.89 | 21.1 | 1 | 0.99 | 13.4 |
| TCWWTP | 1 | 15 | 1 | 0.93 | 10.9 | 1 | 1.03 | 8.2 |
| HCNW | 1 | 600 | 6 | 4.3 | 52.0 | 6 | 5.4 | 46.8 |
| COCFD | 2 | 75 | 1 | 0.88 | 20.9 | 1 | 0.94 | 11.6 |
| COCTV | 2 | 100 | 1 | 0.88 | 20.9 | 1 | 0.92 | 7.2 |
| COMKR | 2 | 50 | 1 | 0.93 | 20.7 | 1 | 1 | 11.7 |
| COMW | 2 | 100 | 1 | 0.95 | 22.7 | 1 | 0.98 | 16.1 |
| KE ECAM | 2 | 65 | 1 | 0.93 | 22.3 | 1 | 0.99 | 12.5 |
| TCWP | 2 | 20 | 1 | 0.97 | 22.3 | 1 | 1.05 | 10.5 |
| BLDG210 | 2 | 250 | 2.5 | 2.22 | 47.1 | 3 | 2.8 | 24.2 |
| PCDC | 2 | 900 | 6 | 4.62 | 48.4 | 6 | 5.5 | 44.1 |
| BayView | 3 | 150 | 1.5 | 1.39 | 33.3 | 1.5 | 1.34 | 14.9 |
| BNS GEN | 3 | 500 | 4.95 | 1.85 | 44.3 | 2.5 | 1.89 | 26.3 |
| KRMC | 3 | 1000 | 6 | 4.5 | 87.7 | 6 | 5.7 | 21.0 |
| COCWWTP | 3 | 664 | 6 | 5.9 | 112.8 | 3 | 2.9 | 40.8 |
| NQ | 4 | 1000 | 10 | 9.54 | 228.4 | 10 | 10.15 | 110.3 |

Observations take place at varying times of year, and there is significant variation in range of temperatures observed from site to site and from baseline to treatment periods.  Some sites show significant temperature dependence in baseline usage, whereas other sites show no temperature dependence (often displaying remarkably consistent usage).  Temperature dependence is observed at sites with larger baseline heater sizes (within a size category), and is consistent with a properly-sized heater.  Temperature independence (flat baseline) is observed at sites with smaller baseline heater sizes, and is consistent with an undersized heater (reflecting the heater is running consistently on full).

The sites per size category that exhibit flat baselines (indicative of undersized heaters) suggest the following designation of undersized v. proper-sized heaters:

Table 9: Baseline Heater Size Ranges (as suggested by data)

| Site Size Category | Undersized Heater Range | Proper-sized Heater Range |
| --- | --- | --- |
| 1 | 1 kW and below | 2 kW and above |
| 2 | 1 kW and below | 2 kW and above |
| 3 | 5 kW and below | 6 kW and above |

Note: there is not enough data to determine the proper sizing range for size category 4 sites.  Only one category 4 site was observed, with baseline heater size of 10 kW, and the data for this site suggests the heater was under-sized.  The heater range applies only to baseline heater sizes; the new heaters all exhibit temperature dependence.

ESTIMATION METHODOLOGY

Undersized and proper-sized sites behave very differently, and thus should be modeled separately.

Baseline Usage for Undersized Sites

Undersized sites frequently showed remarkable consistency; individual sites did not display enough variation to warrant modeling.  Therefore a single expected baseline usage was attributed for each site.  Across sites, these usages exhibited a fairly linear relationship with heater size across site size categories.

Baseline Usage for Properly-Sized Sites

Baseline usage in properly-sized sites were modeled (for each size category) as a function of temperature.  There were not enough sites or variation in the baseline heater size to model usage as a function of heater size as well as site size category.  The model applied (per site size category) is:

daily_kWh= β0+β1*Temperature+ε

Where:

Daily_kWh is the daily usage (kWh) as collected

Temperature is the observed average outside air temperature (°F)

Treatment Usage (All Sites)

Measure undersized heaters were not an issue as in the baseline periods, therefore treatment usage was modeled as a function of temperature and new heater size for all sites.  The model applied (per site size category) is:

daily_kWh= β0+β1*New_Heater_Size+β2*New_Heater_Size*Temperature+ε

Where:

Daily_kWh is the daily usage (kWh) as collected

New_Heater_Size is the recorded new heater size (kW)

Temperature is the observed average outside air temperature (°F)

ESTIMATION RESULTS

Equation 1: Estimated Baseline Usage for Undersized Sites:

daily_kWh = 20.2 * Baseline_Heater_Size	(1)

Table 10: Estimated Baseline Usage for Properly-Sized Sites (regression results)

| Site Size Category | Regression Coefficients |  |
| --- | --- | --- |
|  | Intercept | Temp. |
| 1 | 105.91 | -1.178 |
| 2 | 88.92 | -0.701 |
| 3 | 139.85 | -0.932 |

Table 11: Estimated Treatment Usage (regression results)

| Site Size Category | Regression Coefficients |  |  |
| --- | --- | --- | --- |
|  | Intercept | Heater Size | Heater Size * Temp. |
| 1 | 3.70 | 13.135 | -0.136 |
| 2 | 5.86 | 13.195 | -0.133 |
| 3 | 10.26 | 16.688 | -0.179 |
| 4 | 229.52 | 0 | -2.577 |

Note: As only one site of size category 4 was observed, estimated treatment was not a function of new heater size (regression model was a function of temperature only).

SAVINGS ESTIMATES

Using the estimation results to estimate savings from a CBH installation in SCE territory requires the following items:

- Site size category

- Baseline heater size

- New heater size

- Climate zone (to determine average temperature)

Note that the range of observed temperatures are generally lower than those observed in SCE territory climate zones, particularly for baseline regression.  These savings estimates thus are projecting heater performance for temperatures generally outside the observed range.   Savings estimation is determined by the following steps:

- Determine whether baseline heater is undersized or properly-sized for the site size category.

  - For undersized baseline heaters, average daily kWh is determined using Equation (1).

  - For properly-sized heaters, averaged daily kWh is determined for climate zone average temperature, using regression results in Table 10.

- Estimate treatment usage based on new heater size and climate zone average temperature, using regression results in Table 11.

- The difference in daily kWh can be projected into annual saving using preferred assumed days of operation.

Savings Estimation Sample Calculation:

Sample 1: Climate Zone 6, site size category 1, baseline heater size 1 kW, new heater size 1 kW, annual operation 334 days / year.

- Designation: Undersized

- Annual Average Temperature: 61.5°F

- Baseline Daily kWh: 20.2 * [Baseline Heater Size] = 20.2 kWh / day.

- Treatment Daily kWh: 3.70 + 13.135 * [New Heater Size] – 0.136 * [New Heater Size] * [61.5°F]  = 8.4 kWh / day

- Annual Savings: (20.2 kWh/day – 8.4 kWh/day) * 334 days/year = 3,928 kWh/year.

Sample 2: Climate Zone 8, site size category 3, baseline heater size 6 kW, new heater size 6 kW, annual operation 334 days / year.

- Designation: Proper-sized

- Annual Average Temperature: 63.4°F

- Baseline Daily kWh: 139.85 – 0.932 * [63.4°F] = 80.8 kWh / day.

- Treatment Daily kWh: 10.26 + 16.688 * [New Heater Size] – 0.179 * [New Heater Size] * [63.4°F]  = 42.1 kWh / day

- Annual Savings: (80.8 kWh/day – 42.1 kWh/day) * 334 days/year = 12,908 kWh/year.

| Table 12: Sample Savings - Climate Zone 6 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline Heater Size | New Heater Size | Baseline Heater Designation | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings |
| 1 | 1 | 1 | Undersized | 20.2 | 8.4 | 3,928 |
|  | 3 | 3 | Proper-Sized | 33.4 | 17.9 | 5,181 |
| 2 | 1 | 1 | Undersized | 20.2 | 10.9 | 3,124 |
|  | 6 | 6 | Proper-Sized | 45.8 | 35.8 | 3,349 |
| 3 | 2 | 2 | Undersized | 40.4 | 21.6 | 6,293 |
|  | 6 | 6 | Proper-Sized | 82.5 | 44.2 | 12,817 |
| 4 | 10 | 10 | Undersized | 202.0 | 71.0 | 43,753 |

| Table 13: Sample Savings - Climate Zone 8 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Baseline Heater Size | New Heater Size | Baseline Heater Designation | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings |
| 1 | 1 | 1 | Undersized | 20.2 | 8.2 | 4,014 |
|  | 3 | 3 | Proper-Sized | 31.2 | 17.1 | 4,693 |
| 2 | 1 | 1 | Undersized | 20.2 | 10.6 | 3,208 |
|  | 6 | 6 | Proper-Sized | 44.5 | 34.3 | 3,412 |
| 3 | 2 | 2 | Undersized | 40.4 | 20.9 | 6,521 |
|  | 6 | 6 | Proper-Sized | 80.8 | 42.1 | 12,908 |
| 4 | 10 | 10 | Undersized | 202.0 | 66.1 | 45,389 |

Please note that DEER interactive effects are not used in the calculation of the energy savings as the equipment will either be installed outside or in an unconditioned room. Due to the equipment being installed either outside or in an unconditioned room, the energy savings will not vary by building type.

The Demand reduction for each measure can be found by taking the energy savings and dividing by the total operating hours for each measure. As these measures are typically installed on backup generators which are required to kick on when needed (when the power goes out), the energy savings calculations assume that the circulating block heaters are enabled continuously for 334 days out of the year (accounting for maintenance). A sample calculation has been shown below:

Sample 3: Climate Zone 6, site size category 1, baseline heater size 1 kW, new heater size 1 kW, annual operation 334 days / year.

- Designation: Undersized

- Annual Average Temperature: 61.5°F

- Baseline Daily kWh: 20.2 * [Baseline Heater Size] = 20.2 kWh / day.

- Treatment Daily kWh: 3.70 + 13.135 * [New Heater Size] – 0.136 * [New Heater Size] * [61.5°F]  = 8.4 kWh / day

- Annual Savings: (20.2 kWh/day – 8.4 kWh/day) * 334 days/year = 3,928 kWh/year.

- Annual kW Savings: 3,928 kWh/year / (334 days/year * 24 hours/day) = 0.4900 kW

Sensitivity Analysis

In order to check the validity of using a yearly average temperature vs. a daily average temperature, a sensitivity analysis was performed for climate zones 6 and 15. The sensitivity analysis for both climate zone 6 and climate zone 15 is provided in this work paper for reference (attachment 3).

For climate zone 6, the average daily temperature was found and used with the regression models mentioned above. The savings using daily average temperature were on average, within 0.06% of the savings using the yearly average temperature, as seen below:

Table 14 Savings Comparison for Climate Zone 6

| Measure | Sensitivity Analysis Savings (kWh) | Original Savings (kWh) | % Difference in Savings |
| --- | --- | --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 3,926 | 3,928 | 0.04% |
| 200-799 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 3,122 | 3,124 | 0.05% |
| 800-1099 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 6,289 | 6,293 | 0.07% |
| 1100-2500 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 43,722 | 43,753 | 0.07% |

For climate zone 15, the average daily temperature was found and used with the regression models mentioned above. The savings using daily average temperature were on average, within 0.07% of the savings using the yearly average temperature, as seen below:

Table 15 Savings Comparison for Climate Zone 15

| Measure | Sensitivity Analysis Savings (kWh) | Original Savings (kWh) | % Difference in Savings |
| --- | --- | --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 4,553 | 4,552 | -0.01% |
| 200-799 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 3,735 | 3,734 | -0.02% |
| 800-1099 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 7,937 | 7,936 | -0.02% |
| 1100-2500 kW Backup Generator with Circulating Block Heater replacing Undersized Thermosiphon Heater | 55,556 | 55,545 | -0.02% |

Based on the results of the sensitivity analysis, the savings using the yearly average temperature seems to be an appropriate assumption for this work paper.

# Section 3: Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Table 16: Building Types and Load Shapes

| Building Type | Load Shape | E3 Alt. Building Type |
| --- | --- | --- |
| Agricultural | Industrial | Industrial |
| Assembly | Industrial | Industrial |
| Health/Medical - Clinic | Industrial | Industrial |
| Education - Community College | Industrial | Industrial |
| Education - Primary School | Industrial | Industrial |
| Education - Relocatable Classroom | Industrial | Industrial |
| Education - Secondary School | Industrial | Industrial |
| Education - University | Industrial | Industrial |
| Food Store | Industrial | Industrial |
| Grocery | Industrial | Industrial |
| Lodging - Guest Rooms | Industrial | Industrial |
| Health/Medical - Hospital | Industrial | Industrial |
| Lodging - Hotel | Industrial | Industrial |
| Industrial | Industrial | Industrial |
| Manufacturing - Bio/Tech | Industrial | Industrial |
| Misc - Commercial | Industrial | Industrial |
| Manufacturing - Light Industrial | Industrial | Industrial |
| Lodging - Motel | Industrial | Industrial |
| Health/Medical - Nursing Home | Industrial | Industrial |
| Office - Large | Industrial | Industrial |
| Office - Small | Industrial | Industrial |
| Restaurant - Fast-Food | Industrial | Industrial |
| Restaurant - Sit-Down | Industrial | Industrial |
| Retail - Multistory Large | Industrial | Industrial |
| Retail - Single-Story Large | Industrial | Industrial |
| Retail - Small | Industrial | Industrial |
| Storage - Conditioned | Industrial | Industrial |
| Storage - Unconditioned | Industrial | Industrial |
| Transportation - Communication - Utilities | Industrial | Industrial |
| Warehouse - Refrigerated | Industrial | Industrial |

# Section 4: Base Case & Measure Costs

Please note that due to the lack of information between undersized and properly sized heaters, the cost is treated as exactly the same for both types of measures. This will be addressed on the next update of the work paper when additional SCE territory specific data is available.

## 4.1 Base Case Cost

The base case equipment costs for these measures are found from equipment manufacturers. The table below shows the cost of thermo siphon heaters.

Table 17 Base Case Cost

| Measure | Base Case Cost | Labor Cost | Total Cost |
| --- | --- | --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater | $150 | $600 | $750 |
| 200-799 kW Backup Generator with Circulating Block Heater | $600 | $600 | $1200 |
| 800-1099 kW Backup Generator with Circulating Block Heater | $600 | $600 | $1200 |
| 1100-2500 kW Backup Generator with Circulating Block Heater | $900 | $600 | $1500 |

## 4.2 Measure Case Cost

The measure case costs for these measures are also found from equipment manufacture quotes. The labor costs come from SCE’s customized program for actual installation of this technology. The measures costs for this work paper are shown in the table below.

Table 18 Measure Case Cost

| Measure | Measure Case Cost | Labor Cost | Total Cost |
| --- | --- | --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater | $400 | $600 | $1000 |
| 200-799 kW Backup Generator with Circulating Block Heater | $1200 | $600 | $1800 |
| 800-1099 kW Backup Generator with Circulating Block Heater | $1200 | $600 | $1800 |
| 1100-2500 kW Backup Generator with Circulating Block Heater | $1500 | $600 | $2100 |

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost (GMC)

For RET measures, the Gross Measure Cost (GMC) is:

GMC = Measure Equipment Cost + Measure Labor Cost

For ROB/NEW measures, the GMC is:

GMC = (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

The GMC for both RET and ROB/NEW measures can be found in the table below.

Table 19 Gross Measure Cost

| Measure | GMC for RET Measures | GMC for ROB/NEW Measures |
| --- | --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater | $1000 | $250 |
| 200-799 kW Backup Generator with Circulating Block Heater | $1800 | $600 |
| 800-1099 kW Backup Generator with Circulating Block Heater | $1800 | $600 |
| 1100-2500 kW Backup Generator with Circulating Block Heater | $2100 | $600 |

### 4.3.2 Incremental Measure Cost (IMC)

For RET and ROB measures, the incremental measure cost (IMC) is:

IMC = (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

The IMC for both RET and ROB measures can be found in the table below.

Table 20 Incremental Measure Cost

| Measure | IMC for RET/ROB Measures |
| --- | --- |
| 37-199 kW Backup Generator with Circulating Block Heater | $250 |
| 200-799 kW Backup Generator with Circulating Block Heater | $600 |
| 800-1099 kW Backup Generator with Circulating Block Heater | $600 |
| 1100-2500 kW Backup Generator with Circulating Block Heater | $600 |

# Attachments

# References

[31]

[351]

[355]

[422]

[436]

[491]

[A] Bonneville Power Administration (BPA). (2014). Emerging Technology field Test Results and Future Opportunities.

# Appendix A: Installation Types

This table compares the installation types in SCE’s systems with those in DEER.

| SCE Installation Type | CPUC Installation Type | Savings |  | Cost |  | Life |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL | 1st BL | 2nd BL |
| New Construction (NEW) | New Construction (Nc) | Above Code or Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob), Normal Replacement (NR) | Above Code or Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Customer Existing | Above Code or Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Customer Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Customer Existing | N/A | Full Cost | N/A | EUL | 0 |

# Appendix B: Delivery Mechanisms

A delivery mechanism is a delivery method paired with an incentive method. SCE’s delivery methods include:

- Appliance Turn-in and Recycling

- Audit/Information

- Commissioning

- Financial Support

- Innovative Design

- Midstream Programs

- Partnership

- Upstream Programs

The following table describes the incentive methods.

| Incentive Method | Description |
| --- | --- |
| Direct Install | The utility program performs an assessment of the customer’s facility, provides recommendations, and implements energy efficiency measures for free. |
| Down-Stream Incentive - Deemed | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. |
| Exchange - Replacement | The utility program holds events where customers can trade functional equipment for similar but more energy efficient equipment, free of charge. |
| Giveaway | The utility program provides customers with energy efficient equipment for free. |
| Mid-Stream Incentive | The utility program offers buydowns and incentives to third parties (typically retailers, distributors, and contractors), who then stock, promote, lower prices on, and/or sell energy efficient equipment. Contractors install energy efficiency equipment, sometimes using specified quality procedures, at the customer’s property. |
| On-bill Finance - loan | Customers can finance energy efficiency projects at 0% interest and repay the loan through their monthly utility bill. |
| Testing Services / Other | The utility program performs free testing services or assessments of the customer’s facility and provides information and recommendations for potential energy efficiency measures. |
| Up-Stream Buy Down, Up-Stream Incentive | The utility program offers buydowns and incentives to vendors (typically manufacturers and distributors), who then manufacture, stock, promote, lower prices on, and/or sell energy efficient equipment. There is some overlap between the mid-stream and up-stream approaches. |

PCDC was reported to have a baseline heater size of 12 kW; this value is anomalously large and not consistent with other observable data.  Based on measured kW and usage levels, a heater size of 6 is more plausible and more consistent.

Runtime logging for KRMC strongly suggest that the replacement heaters were significantly oversized for their needs.  Therefore, the usage data are not representative of a site with an appropriately-sized heater.  As a result, KRMC data are excluded from the analysis.

At sites where an overwhelming mode value was observed, the mode was used as the expected baseline usage.  Otherwise, the mean baseline usage was used.

Until more data are collected for additional category 4 sites, savings for category 4 sites can only be estimated using the undersized heater methodology.

Note: decimal rounding may yield slightly different results in these examples.