Work Paper SCE13LG098

Revision 2

Southern California Edison Company

Fluorescent to LED Retrofits in Reach-in Display Cases

# At-a-Glance Summary

| Applicable Measure Codes: | LT-17642, LT-20643, LT-30954, LT-49651, LT-58674, LT-65612, LT-69439, LT-75912, LT-78303, LT-79548, LT-80693, LT-84544, LT-89513, LT-93848, LT-97154 |
| --- | --- |
| Measure Description: | This work paper details the retrofit of a 4-ft/5-ft T8 fluorescent fixture with electronic ballast and a 4-ft/5-ft/6-ft T12 HO fluorescent fixture with magnetic ballast with a vertical light emitting diode (LED) lighting system in refrigerated display cases. |
| Base Case Description: | 4-ft/5-ft T8 fluorescent fixture with electronic ballast and a 4-ft/5-ft/6-ft T12 HO fluorescent fixture with magnetic ballast |
| Energy Impact Common Units: | Per Door, Per Fixture |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | Refer to Table 5 |
| Measure Application Type: | Early Retirement (ER), Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | 0.6 or 0.85 |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13LG098.0 | No | 05/29/2012 | Branden Morhous/Lincus, Inc. | - Updated workpaper format to latest template “SP&TS Work Paper Template 2013 v0.1.docx”(based on previous version WPSCNRLG0098) - Clarified base/measure cases and unit description - Updated annual operating hours of building types according to DEER 2011 - Updated NTG values |
| SCE13LG098.1 | No | 07/12/2013 | Yun Han/SCE | - Added EUL ID in the EUL section - Added 4x T12 measures from 10-12 WP - Updated code language to T24 2013 - Added code language relevant to T12 - Updated T8 measure names from 10-12 WP - Updated 5’ LED Wattage & cost from 6 door to 5 door - Added 3’ & 4’ horizontal display case LED measures per fixture |
| SCE13LG098.2 | No | 08/01/2014 | Sabarish Vinod/Lincus, Inc. | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - Updated interactive effects with new weather files. - Updated NTG values - Updated load shapes - Updated solution codes - Updated delivery mechanisms and measure application type |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the retrofit of a 4-ft/5-ft T8 fluorescent fixture with electronic ballast and a 4-ft/5-ft/6-ft T12 HO fluorescent fixture with magnetic ballast with a vertical light emitting diode (LED) lighting system in refrigerated display cases.

This work paper also details the retrofit of a 3-ft/4-ft T8 fluorescent fixture with electronic ballast and a 3-ft/4-ft T12/T12HO fluorescent fixture with magnetic ballast with a horizontal LED lighting system in refrigerated display cases for shelf and canopy.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| LT-17642 | (1) 48in Medium Temp Reach-in Display Cases Canopy LED replacing (2) 48in T8 Linear Fluorescent |
| LT-20643 | (1) 48in Medium Temp Reach-in Display Cases Shelf LED replacing (1) 48in T12 Linear Fluorescent |
| LT-30954 | (1) 48in Medium Temp Reach-in Display Cases Shelf LED replacing (1) 48in T8 Linear Fluorescent |
| LT-49651 | (1) 36in Medium Temp Reach-in Display Cases Canopy LED replacing (2) 36in T12 Linear Fluorescent |
| LT-58674 | (1) 36in Medium Temp Reach-in Display Cases Canopy LED replacing (2) 36in T8 Linear Fluorescent |
| LT-65612 | (1) 36in Medium Temp Reach-in Display Cases Shelf LED replacing (1) 36in T12 Linear Fluorescent |
| LT-69439 | (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent |
| LT-75912 | (1) 36in Medium Temp Reach-in Display Cases Shelf LED replacing (1) 36in T8 Linear Fluorescent |
| LT-78303 | (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent |
| LT-79548 | (1) 72in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent |
| LT-80693 | (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent |
| LT-84544 | (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent |
| LT-89513 | (1) 48in Medium Temp Reach-in Display Cases Canopy LED replacing (2) 48in T12 Linear Fluorescent |
| LT-93848 | (1) 72in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent |
| LT-97154 | (1) 48in Medium Temp Reach-in Display Cases Canopy LED replacing (1) 48in T12 Linear Fluorescent |
| LT-17642 | (1) 48in Medium Temp Reach-in Display Cases Canopy LED replacing (2) 48in T8 Linear Fluorescent |

To qualify for a rebate, the product must be listed on Design Lights Consortium’s Qualified Products List.

- Minimum Luminaire Efficacy (Lm/w) - 50 Lm/W

- Minimum Lifetime - must be ≥ 50,000 hours

- Manufacturer Warranty - 5 years

- Power Factor - ≥ 0.9

- Total Harmonic Distortion - ≤ 20%

- Minimum Light Output – End-mounted

- Zonal Lumen Density - ≥95%: 10°-90°

- Allowable CCT - ≤ 5,000K

- Minimum CRI - 80 CRI

- Off-State Power - 0W

- Zonal Lumen Density

  - Vertical Refrigerated Case Luminaires - ≥95%: 10°-90°

  - Horizontal Refrigerated Case Luminaires - ≥95%: 0°-90°

Documentation of the above criteria is required for qualification of the proposed/installed lighting system.  Documentation is also required to verify the basecase lighting system.

## 1.2 Technical Description

T8 Fluorescent (Baseline Technology)

The baseline for vertical LED is a 5-foot T8 fluorescent lighting fixture for medium temperature (MT) display cases and a 5-foot T8 High Output (HO) fluorescent lighting fixture for low temperature (LT) display cases. The reason different fixtures are used is because colder temperatures make the fixtures operate less efficiently and output less light, so high output fixtures are used in the low temperature applications.

The fixture code used as the medium temperature basecase for this work paper is F51LL from Appendix B: Table of Standard Fixture Wattages of the 2012 Statewide Customized Offering Procedures Manual for Business [A] (see attachment 2). This fixture consumes 36 Watts. The system used as the low temperature basecase for this work paper is an F40T8/HO. This fixture consumes 56.3 Watts, based on field test data [B].

The baseline for horizontal LED is a 3-foot and 4-foot T8 fluorescent lighting fixture for MT display cases. The fixture code used as the MT basecase for this work paper is F32ILL and F42ILL from Appendix B [A](see attachment 2). The 3-foot fixture consumes 46 Watts for 2 lamps. The 4-foot fixture consumes 59 Watts for 2 lamps.

T12 Fluorescent (Baseline Technology)

The baseline for vertical LED is a 5-foot and 6-foot T12 HO fluorescent lighting fixture for both MT and LT display cases. The 5-foot T12 HO uses fixture code F52SHE, consuming 176 Watts for a 2-lamp system, 88 Watts/lamp. The 6-foot T12 HO uses fixture code F62SHE, consuming 194 Watts for a 2-lamp system, 97 Watts/lamp.

The baseline for horizontal LED is a 3-foot and 4-foot T12 fluorescent lighting fixture for MT display cases. The fixture code used as the MT basecase for this work paper is F32SE, F42EIS, and F42SHS. The 3-foot fixture consumes 74 Watts for 2 lamps. The 4-foot fixture consumes 82 Watts for 2-lamps (F42EIS) and 72.5 Watts for 1 HO lamp (F42SHS). LED is replacing either (1) HO T12 lamp or (2) T12 lamps. The 4-foot T12 fluorescent will use 4-foot T8 as the code baseline.

LED (Proposed Technology)

The measure case involves LED lights installed in refrigerated display cases. The LED lighting system also provides the additional benefit of reduced heat dissipation into the cold space, thereby reducing the cooling load. As a result, the new lighting systems reduce compressor run time and energy consumption. This work paper applies to lighting for reach-in glass door display cases of low temperature (“freezer” – below 32F) and medium temperature (“cooler – above 32F) cabinets for single-compressor systems in food stores, misc-commercial, fast food restaurants, and small retail and multiplex compressors in grocery stores, sit down restaurants, multistory large retail, single story large retail, and refrigerated warehouses.

## 1.3 Measure Application Type

There are three delivery methods for this work paper:

- Financial Support – Down-Stream Incentive –Deemed

- Midstream Programs / Mid-Stream Incentive

- Financial Support – Direct Install

The install types for this work paper are Retrofit (RET) for Financial Support – Direct Install and Replace On Burnout (ROB) for Midstream Programs / Mid-Stream Incentive.

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

These specific measures are not included in the Database for Energy Efficient Resources (DEER) Version 2014 v4.01. DEER contains multiple linear fluorescent measures; however, none of the DEER measures exactly match the measures in this work paper.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER does not contain this type of measure. |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID* | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Com | Any | 0.6 |
| Com-Default-HTR-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. ** | Com | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis.  This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the defaulted NTG value, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID* | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | Lighting |
| Measure Case UseSubCats | RefDisplay |
| Measure Case TechGroups | Ref_Storage |
| Measure Case TechTypes | RefrigLtg |
| Base Case TechGroups | Ref_Storage |
| Base Case TechTypes | RefrigLtg |

### 1.4.2 Codes and Standards Analysis

Title 24 2008 [208] and Title 20 2012 [C] do not apply. Title 24, 2013 [D] contains code related to refrigerated display cases that affect new (NEW) display case installations.

Refrigerated Display Cases. Lighting in refrigerated display cases, and lights on glass doors installed on walk-in coolers and freezers shall be controlled by one of the following:

A. Automatic time switch controls to turn off lights during non-business hours. Timed overrides for any line-up or walk-in case may only be used to turn the lights on for up to one hour. Manual overrides shall time-out automatically to turn the lights off after one hour.

B. Motion sensor controls on each case that reduce

EXCEPTION to Section 120.6(b)3: Stores which are normally open for business 140 hours or more per week.

Code of Federal Regulations contain lamp efficacy standards for applicable linear fluorescent lamps manufactured after July 14, 2012[E].

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Section 120.6(b)3 | January 1, 2014 |
| Code of Federal Regulations | 10 CFR 430.32(n) | July 14, 2012 |

### 1.4.3 Non-DEER Study Review

Several Non-DEER studies were reviewed:

- Demonstration Assessment of Lighting-Emitting Diode (LED) Freezer Case Lighting [227]: This is a DOE-sponsored study of a LED lighting and occupancy sensor retrofit of refrigerated display cases in an Albertsons store.

- LED Freezer Case Lighting Systems [456]: The Sacramento Municipal Utility District led an effort to develop an LED freezer case lighting system with motion sensors and dimming controls.

- LED Lighting for Low Temperature Refrigerated Display Cases [457]: Southern California Edison evaluated the savings potential of LEDs and aisle traffic sensors on low-temperature reach-in refrigerated display cases.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 5 below identifies the value/methodology used for the measures in this work paper.

Table 7 EUL Value/Methodology

| READi EUL ID | Description | Sector | Enduse | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| GrocDisp-FixtLtg-LED | Display Case Lighting LED Lighting | Com | Lighting | 16 | 5.3 |

# Section 2. Energy Savings & Demand Reduction Calculations

Assuming that the lighting power requirements of each technology are known, determining the direct power and energy savings is relatively straightforward. Secondary effects on the refrigeration system are a little more difficult to quantify as they depend on many other factors. The two most important factors are: percentage of heat generated by the lighting system ending up as load on the case and efficiency of the refrigeration system.

The power required by each lighting system for the baseline 3/4/5/6-foot T8 and T12 system is based on standard wattages [A]. For the 5-foot and 6-foot vertical LED system, the power is based on the average wattage of current LED display case fixtures [F] (see attachment 3).  The 5-foot and 6-foot vertical LED system used as the basis for this work paper is an average between refrigerated display LED vertical lighting systems of three major lighting companies (Manufacturer 1, Manufacturer 2, and Manufacturer 3) with a color temperature of about 4000K. The average center fixture consumes 20 watts and the average side fixture consumes 12 watts found in the attachment [G]. The 3-foot and 4-foot horizontal LED fixture Wattage is an average of various manufacturers’ fixtures [H]. The wattages can be found in the attachments [I,J].

The lighting power values for each system are shown in the following table.

Table 7 Lighting Power Values

| Lighting System | Power | Comments |
| --- | --- | --- |
| 3’ T8 Fluorescent | 23 W | Per Lamp |
| 3’ T12 Fluorescent | 37 W | Per lamp |
| 4’ T12 Fluorescent | 41 W | Per Lamp |
| 4’ T12 HO Fluorescent | 72.5 W | Per lamp |
| 3’ Canopy LED | 15.5 W | Per lamp |
| 3’ Shelf LED | 6.8 W | Per lamp |
| 4’ Canopy LED | 18.7 W | Per lamp |
| 4’ Shelf LED | 9.6 W | Per lamp |
| 5’ T8 Fluorescent | 36 W | Per lamp |
| 5’ T8/HO Fluorescent | 56.3 W | Per lamp |
| 5’ T12 HO Fluorescent | 88 W | Per lamp |
| 6’ T12 HO Fluorescent | 97 W | Per lamp |
| 5’ LED Side | 14 W | Per Lamp |
| 5’ LED Center | 20 W | Per Lamp |
| 6’ LED Side | 17.2 W | Per Lamp |
| 6’ LED Center | 29.9 W | Per Lamp |

The calculations shown below are an example of T8/HO to vertical LED systems. The calculations for the T8 and T12 baseline were determined using the same methodology.

The calculations are based on two different types of refrigeration systems. The single-compressor system is used for the following building types:

- Food Store

- Misc. Commercial

- Restaurant – Fast-Food

- Retail – Small

While the multiplex compressor system is used for the following building types:

- Grocery

- Restaurant – Sit-Down

- Retail – Multistory Large

- Retail – Single-Story Large

- Warehouse – Refrigerated

Lighting Power and Energy Calculations

- The different configurations of each lighting system make direct comparison of these numbers fairly complicated.  A 5-door display case will typically be equipped with 6 fluorescent bulbs.  When equipped with LEDs, it will have 4 center strips and 2 end strips.  To provide a comparison that would take these differences into account, the lighting power values for fluorescent lamps were converted into per door values according to the following equations:

where,

kWT8/HO = direct power draw of T8/HO system, kW/door

For 5’ LED system;

kW5'LED=0.014 kWLEDx 2 lamps+0.020 kWLEDx 4 lamps15 Doors

kW5'lED=0.0216 kW Per door.

- Lighting power savings for the retrofit technologies is the difference between their direct power draw and that of the T8/HO.

where

kWlighting = lighting power savings, kW/door

- Lighting energy savings is the product of power savings and run time.  Many supermarkets and other stores turn their case lighting systems off at night when the stores are closed or when shopper traffic is light.  This will impact both the lighting and refrigeration energy use.  It is assumed that lights are turned on for 13.5 hours each day (or 4,910 hours per year) [K]. This value comes from DEER.

where

kWhlighting = annual lighting energy savings, kWh/door/year

Cooling Load Calculation

- Heat generated by the lighting system results in additional cooling load on the refrigeration system.  Because of the different equipment present in the lighting systems, each has its own equation for determining the cooling load.

  - For T8/HO fluorescent, some heat is dissipated by the ballast, which is located outside the refrigerated space. The ballast efficiency factor (BEF) accounts for the ratio of output to input power of the ballast. A typical value for BEF is 0.89. Fluorescent lamps become less efficient at lower temperatures. However, this factor varies for different types of lamps and between manufacturers. There is uncertainty regarding the operating temperature inside the lens/jacket surrounding the lamp, but it is believed to be close to the 70F temperature used to test lamps.  Therefore, ktemp is assumed to be 1. It is assumed that 79% of the power fed into the lamp is converted to heat [L].

QT8/HO=kWT8/HO x BEF x ktemp x klamp heat x 3,413Btu/hrkW

where

QT8/HO		= cooling load due to lighting system, Btu/hr/door

BEF		= ballast efficiency factor, 0.89 (typical)

ktemp		= temperature correction factor, 1.0 (assumed)

klamp heat		= lamp heat factor, 0.79 (typical)

  - For LED, some heat is dissipated by the power supply, which is located outside the refrigerated space.  It is assumed that 80% of the total lighting power is converted to heat inside the case [M].

where

QLED		= cooling load due to lighting system, Btu/hr/door

klamp heat		= lamp heat factor, 0.80 (typical)

- The change in lighting cooling load from T8 to each retrofit technology is quantified as the difference in measured cooling load between the two scenarios.

∆Q = QT8/HO – QLED

where

Q = change in lighting cooling load, Btu/hr/door

- Table 8 contains a summary of all power, energy and cooling load values calculated thus far in the analysis. Summary for other measures can be found in the attachments [G, I, J].

Table 8 Summary of direct power, energy and cooling load calculations for 5-foot T8 base case

| Key Parameters | 5-foot T8 Fluorescent | 5-foot T8/HO Fluorescent | 5-foot LED |
| --- | --- | --- | --- |
| Direct power (kW/lamp) | 0.036 | 0.0563 | - |
| Direct power (kW/door) | 0.0432 | 0.0676 | 0.0216 |
| Direct annual energy (kWh/door/year)* | 212 | 332 | 106 |
| Cooling load due to lighting system (Btu/hr/door) | 48 | 75 | 33 |

Compressor Efficiency

Once the lighting cooling load was determined, the following steps were followed to determine the compressor power requirements and energy savings.  Because this work paper addresses lighting for several different types of equipment with various refrigeration system configurations, compressor analysis is limited to the differential cooling load imposed by the lighting system, not the total cooling load of a particular display case or walk-in box.  Compressor analyses for two different types of refrigeration systems are included.  The first analysis focuses on smaller single-compressor systems typically seen in small convenience and grocery stores.  The second analysis deals with larger supermarket systems comprised of several multiplex compressors serving multiple refrigeration cases in the store. The differential compressor power requirements are based on calculated cooling load and energy-efficiency ratios (EER) obtained from manufacturers’ data, for the compressor sizes expected in each type of system.

- Determine the saturated condensing temperature (SCT)

For medium temperature (MT):

For low temperature (LT):

where

DBadj	= dry-bulb temperature (F) of ambient or adjacent space where the compressor/condensing units reside.  Defaults are based on climate zone design values in the table below.

Table 9 Climate Zone Design Dry Bulb Temperature and Representative City

| Climate Zone | Description | Representative City | Summer Design Dry-Bulb (ASHRAE Climatic Region X Data, 0.5% Column via proxy Title 24) [°F] |
| --- | --- | --- | --- |
| 6 | South Coast | Torrance | 86 |
| 8 | South Coast | Fullerton | 94 |
| 9 | South Inland | Burbank-Glendale | 96 |
| 10 | South Inland | Riverside | 100 |
| 13 | Central Valley | Fresno | 101 |
| 14 | Desert | Palmdale | 103 |
| 15 | Desert | Palm Springs-Intl | 113 |
| 16 | Mountain | Blue Canyon | 85 |

Source:	ASHRAE 1982. Climatic Data for Region X. [N]

For small single compressor systems:

- Determine the EER for both MT and LT applications

  - Compressor performance curves were obtained from a review of manufacturer data for small reciprocating compressors as a function of SCT, cooling load, and cooling capacity of compressor.

  - Part-load ratio (PLR):

It is the ratio of total cooling load to compressor capacity.  It indicates the percentage of compressor capacity needed to remove the total cooling load.  It is calculated by following equation:

where,

PLR		= Part Load Ratio

Qcoolinge		= cooling load

Qcapacity		= total compressor capacity

NOTE: Compressor capacity is determined by multiplying cooling load by compressor over-sizing factor of 15%:

Qcapacity = Qcooling * 1.15

Therefore, PLR = 1/1.15 = 0.87

  - For medium temperature compressors, the following equation is used to determine the EERMT (Btu/hr/watts) [O]

EERMT = a + (b * SCT) + (c * PLR) + (d * SCT2) + (e * PLR2) + (f * SCT * PLR) + (g * SCT3) + (h * PLR3) + (i * SCT * PLR2) + 
(j * SCT2 * PLR)

where,

a	= 3.75346018700468

b	= -0.049642253137389

c	= 29.4589834935596

d	= 0.000342066982768282

e	= -11.7705583766926

f	= -0.212941092717051

g	= -1.46606221890819E-06

h	= 6.80170133906075

i	= -0.020187240339536

j	= 0.000657941213335828

PLR	= 0.87

  - For low temperature compressors, the following equation is used to determine the EERLT (Btu/hr/watts) [N]

  - EERLT = a + (b * SCT) + (c * PLR) + (d * SCT2) + (e * PLR2) + (f * SCT * PLR) + (g * SCT3) + (h * PLR3) + (i * SCT * PLR2) + 
(j * SCT2 * PLR)

where,

a	= 9.86650982829017

b	= -0.230356886617629

c	= 22.905553824974

d	= 0.00218892905109218

e	= -2.48866737934442

f	= -0.248051519588758

g	= -7.57495453950879E-06

h	= 2.03606248623924

i	= -0.0214774331896676

j	= 0.000938305518020252

PLR	= 0.87

  - Typically, reduction in cooling load results in a decreased EER for a retrofit measure due to a change in the PLR.  However, this analysis deals with the change in cooling load for many different sizes of equipment in multiple applications with varying baseline cooling loads. Therefore, it would be difficult to assume a new PLR that would be applicable to all types of equipment addressed here.  To simplify the analysis, EER is assumed to remain constant for both the baseline and retrofit situations.

Power & Energy Use

- Power savings

  - Differential power used by the compressor to remove the cooling load imposed by the lighting system is determined based on calculated cooling load and EER, as outlined below.

where

kWcomp	= change in compressor power, kW/door

Qdoor	= change in cooling load per door for MT or LT, Btu/hr/door

EER	= EER for LT or MT, Btu/hr/watts

  - Total power savings (ΔkW) is the sum of lighting and compressor savings.

- Equivalent full load hours (EFLH) of operation

EFLH is determined by multiplying annual available operation hours (8,760) by overall duty cycle factor.  Duty cycle is a function of compressor capacity, defrost and weather, as shown below.

The following equation shows the relationship between capacity, defrost and weather factor.  Capacity factor is a function of compressor capacity and cooling load, determined by subtracting the PLR from 1. Using a compressor capacity factor of 15% results in a PLR of 87%.  The defrost factor depends on the number and duration of defrost cycles and is determined by dividing the defrost duration (in hours) by 24 hours.  Weather factor is a function of CTZ.  Using DOE-2 simulation results for a typical supermarket, weather factors were determined for each CTZ [O]

Duty cycle = Capacity factor x Defrost factor x Weather factor

where,

Capacity factor 	= function of PLR, (1-PLR)

Defrost factor 	= 10% (2.4 hrs / 24 hrs) for LT, (1 – 0.10)

= 5% (1.2 hrs / 24 hrs) for MT, (1 – 0.05)

Weather factor 	= function of CTZ (see discussion below)

To estimate weather factor for each CTZ, the annual energy usage of a refrigeration system for a typical supermarket in each CTZ, based on a DOE-2 computer simulation, was used. [O] Using CTZ 15 as a benchmark with 85% weather factor, weather factors for the other 15 CTZs were estimated.  The following equation shows this methodology.

The following table illustrates the annual energy usage of refrigeration for each CTZ and corresponding weather factors.

where,

WFCTZ	= weather factor for each CTZ

Annual kWh CTZ	= annual energy usage of refrigeration system for each CTZ, kWh/yr

Annual kWh CTZ15	= annual energy usage of refrigeration system for CTZ 15, kWh/yr

WFCTZ-15	= weather factor for CTZ 15, 85%

Table 10 Weather Factor Values for SCE Climate Zones

| CTZ | Refrigeration Annual Energy Usage (kWh/yr)* | Weather Factor (%) |
| --- | --- | --- |
| 6 | 502,982 | 78.9% |
| 8 | 506,024 | 79.4% |
| 9 | 500,936 | 78.6% |
| 10 | 495,565 | 77.7% |
| 13 | 496,488 | 77.9% |
| 14 | 491,056 | 77.0% |
| 15 | 541,873 | 85.0% |
| 16 | 452,877 | 71.0% |

*From DOE-2 simulations for a typical supermarket [P]

Accordingly, EFLH = 8,760 x Duty cycle    (hrs/yr)

- Energy savings (∆kWh):

  - Annual energy savings of the compressor (ΔkWhcomp) is determined based on calculated differential compressor power and EFLH, as outlined below.

  - Total energy savings (ΔkWh) is the sum of compressor and lighting energy.

For large multiplex compressor systems:

- Determine the EER for both MT and LT applications

  - Compressor performance curves were obtained from a review of manufacturer data for large reciprocating compressors as a function of SCT and SET. In multiplex systems, suction pressure controls ensure SET remains constant, so no PLR analysis is necessary.

  - For medium temperature compressors, the following equation is used to determine the EERMT (Btu/hr/watts) at SET of 28F. [O]

  - EERMT = a  * SCT3 + b * SCT2 + c * SCT + d

where,

a	= 0.00002515

b	= 0.0100767

c	= -1.45844836

d	= 82.96962576

  - For low temperature compressors, the following equation is used to determine the EERLT (Btu/hr/watts) [O]

  - EERLT = a * SCT3 + b * SCT2 + c * SCT + d

where,

a	= 0.00000491

b	= -0.00107023

c	= -0.03013591

d	= 15.74788397

  - This analysis assumes no change in EER due to a reduction in cooling load for a retrofit measure.

- These demand and energy savings values are reported per door.  No further normalization is required.

Table 11 summarizes the demand and energy savings of 5’ T8 fixtures for MT and LT applications for all SCE climate zones in the grocery market sector. The calculations and the savings for the rest of the applicable market sectors and measures can be found in the attachments [G, I, J].

Table 11 Demand and Energy Savings for 5-foot T8 to LED Retrofit

| Climate Zone | Representative City and Temperature (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Grocery |  | Grocery |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MT, T8 to 5' LED retrofit |  | LT, T8/HO to 5' LED retrofit |  |
|  |  |  | Demand Savings (ΔkW/unit) | Energy Savings (ΔkWh/unit) | Demand Savings (ΔkW/unit) | Energy Savings (ΔkWh/unit) |
| 6 | Torrance - 86⁰F | /Door | 0.023649 | 116 | 0.053194 | 256 |
| 8 | Fullerton - 94⁰F | /Door | 0.023912 | 119 | 0.054192 | 262 |
| 9 | Burbank-Glendale - 96⁰F | /Door | 0.023985 | 119 | 0.054463 | 263 |
| 10 | Riverside - 100⁰F | /Door | 0.024142 | 120 | 0.055034 | 265 |
| 13 | Fresno - 101⁰F | /Door | 0.024184 | 119 | 0.055184 | 264 |
| 14 | Palmdale - 103⁰F | /Door | 0.024270 | 120 | 0.055492 | 267 |
| 15 | Palm Springs-Intl - 113⁰F | /Door | 0.024777 | 121 | 0.057269 | 273 |
| 16 | Blue Canyon - 85⁰F | /Door | 0.023619 | 119 | 0.053078 | 260 |

Therm Savings Calculations

The therm savings will be realized in the room where the refrigeration equipment is housed. The refrigeration equipment will eject less heat because the heat input from the lighting system will be decreased. Therefore, the HVAC system of that room will need to provide additional heating to the building (hence negative therms). On single compressor systems, the heat is rejected into the conditioned space below the refrigerated case [Q](Attachment 4). On multiplex systems, the heat is rejected in an air cooled or water cooled condenser which is typically outside. Therefore, there will be no therm savings on multiplex systems since their heat rejection equipment is not located in a conditioned space.

DEER provides interactive effects values for kW, kWh, and therms based on the building type and climate zone. Interactive effects values are simply dimensionless units which quantify the HVAC savings when lighting loads are decreased in conditioned spaces. The interactive effects values were obtained from DEER 2011[K]. The equation to find the therm savings is as follows:

Therm Savings = ΔkWh * Therm IE FactorCTZ,Building Type

Where:

Therm IE FactorCTZ,Building Type = therms interactive effect factor based on the climate zone and building type. The calculation for interactive effects is included in the excel calculation file [R](Attachment 1). Savings for other measures can be found in the attachments [G, I, J].

Table 12. Therms Savings for 5-foot T8 to LED Retrofit

| Climate Zone | Representative City and Temperature (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Small Stores (Food Stores) | Large Stores (Grocery Stores and Large Retail Stores) |
| --- | --- | --- | --- | --- |
|  |  |  | MT, T8 to 5' LED retrofit | LT, T8/HO to 5' LED retrofit |
|  |  |  | Therm Savings (ΔTherm/unit) | Therm Savings (ΔTherm/unit) |
| 6 | Torrance - 86⁰F | /Door | -0.707 | 0.00000 |
| 8 | Fullerton - 94⁰F | /Door | -0.639 | 0.00000 |
| 9 | Burbank-Glendale - 96⁰F | /Door | -0.653 | 0.00000 |
| 10 | Riverside - 100⁰F | /Door | -0.652 | 0.00000 |
| 13 | Fresno - 101⁰F | /Door | -0.845 | 0.00000 |
| 14 | Palmdale - 103⁰F | /Door | -0.835 | 0.00000 |
| 15 | Palm Springs-Intl - 113⁰F | /Door | -0.342 | 0.00000 |
| 16 | Blue Canyon - 85⁰F | /Door | -1.321 | 0.00000 |

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the DEER:Indoor_Non-CFL_Ltg load shape.  See Table 13 for a list of all Building Types and Load Shapes. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 13 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Grocery | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Food Store | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Misc - Commercial | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Restaurant - Sit-Down | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Restaurant - Fast-Food | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Retail - Multistory Large | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Retail - Single-Story Large | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Retail - Small | NON_RES | DEER:Indoor_Non-CFL_Ltg |
| Warehouse - Refrigerated | NON_RES | DEER:Indoor_Non-CFL_Ltg |

# Section 4. Base Case & Measure Costs

Direct Install measures use program tracking systems for measure costs.

Costs calculations can be found in the attachment.

## 4.1 Base Case Cost

Base Material Costs (5’T8)

The following information was obtained from the Revised Measure Cost Summary from DEER 2008[S].

Note that the material cost of a 1 lamp 48in T8 NLO = $16.28 from DEER and a 1 lamp 48in T8 VHLO = $16.97 from DEER.

The following equations were then used to obtain the costs of a 5’ fixture by relating it to a 4’ and 8’ fixture from DEER.

5'T8=4'T8+5'-4'8'-4'x($8'T8-$4'T8)

5'T8=$16.28+5'-4'8'-4'x(29.27-16.28)

5'T8=$19.53 per fixture

5'T8/HO=$20.04  per fixture

Cost per door can be calculated as follows:

5'T8/Door=T8x6 lamps5 doors

5'T8/Door=$19.53x6 lamps5 doors

5'T8/Door=$23.44 per fixture

5'T8/HO/Door=$24.05 per fixture

Base Labor Costs (5’ T8)

Note that the labor cost of a 1 lamp 48in T8 = $26.51 from DEER, a 1 lamp 48in T8/HO = $27.99 from DEER, and a 1 lamp 96in T8 = $26.51 from DEER. Therefore, the labor cost for a 5’T8 is the same as a 4’T8.

Cost per door can be calculated as follows:

5'T8/Door=T8x6 lamps5 doors

5’T8= $26.51 x (6/5)

5’T8= $31.81 per door, 5’T8/HO= $33.14 per door

Cost for T12 systems are calculated the same way as T8 systems and can be found in Attachment 1 [R].

Table 14 Base Cost

| Measure | Cost | Labor | Total |
| --- | --- | --- | --- |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $24.05 | $33.14 | $57.19 |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $21.94 | $35.13 | $57.07 |
| (1) 72in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $26.07 | $38.44 | $64.51 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $23.44 | $31.81 | $55.25 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $21.94 | $35.13 | $57.07 |
| (1) 72in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $26.07 | $38.44 | $64.51 |

## 4.2 Measure Case Cost

Based on inquiries from LED manufacturers [U], the 5-foot LED fixtures are available for $160/center fixture and $140/end fixture. Assuming a 5 door display case with 6 lamps, the following equation is used to determine the cost per door:

$/Door=$end x 2 end lamps+ $center x 4 center lamps5 doors

$/Door=$140 x 2 end lamps+$160 x 4 center lamps5 doors

$/Door=$184 per door

Based on inquiries from LED manufacturers [U], the 6-foot LED fixtures are available for $180/center fixture and $160/end fixture. Assuming a 5 door display case with 6 lamps, the following equation is used to determine the cost per door:

$/Door=$end x 2 end lamps+ $center x 4 center lamps5 doors

$/Door=$160 x 2 end lamps+$180x 4 center lamps5 doors

$/Door=$208.00 per door

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

Per the E3, the gross measure cost (GMC) is the cost to install an energy efficient measure. In the case of ROB, the GMC is the same as the incremental measure cost (see section 4.3). In the case of RET, GMC means the full cost of the measure to purchase and install.

GMC = Measure Equipment Cost + Measure Labor Cost

Labor costs are assumed to be the same as the linear fluorescent systems, since the existing fixture has to be removed and the new fixture put in just the same.

Gross measure cost of all measures is shown in Table 15.

Table 15 Gross Measure Cost

| Measure | Cost | Labor | Total |
| --- | --- | --- | --- |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $184.00 | $33.14 | $217.14 |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $184.00 | $35.13 | $219.13 |
| (1) 72in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $208.00 | $38.44 | $246.44 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $184.00 | $31.81 | $215.81 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $184.00 | $35.13 | $219.13 |
| (1) 72in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $208.00 | $38.44 | $246.44 |

### 4.3.2 Incremental Measure Cost

For this measure category, the incremental measure cost (IMC) is used strictly for providing insight to program managers to assist in determining rebates for deemed measures. For retrofit measures the incremental measure cost is NOT used for reporting in the cost effectiveness calculations.

Finally, incremental cost can be calculated for a 5’ LED measure replacing a 5’T8 Fixture. Labor cost is assumed to be the same.

Incremental Cost = Measure Material $ – Base Material $

Incremental CostT8 = $237.60 – $24.05

Incremental CostT8 = $213.55

Incremental measure cost of all measures is shown in Table 16.

Table 16 Incremental Measure Cost

| Measure | Measure Cost | Base Cost | Incremental |
| --- | --- | --- | --- |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $184.00 | $24.05 | $159.95 |
| (1) 60in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $184.00 | $21.94 | $162.06 |
| (1) 72in Retrofits in Low Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $208.00 | $26.07 | $181.93 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T8 Linear Fluorescent | $184.00 | $23.44 | $160.56 |
| (1) 60in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 60in T12 Linear Fluorescent | $184.00 | $21.94 | $162.06 |
| (1) 72in Retrofits in Medium Temp Reach-in Display Cases LED replacing (1) 72in T12 Linear Fluorescent | $208.00 | $26.07 | $181.93 |

# Attachments

# References

[31]

[132]

[208]

[A] Attachment 2 – App B Standard Fixture Watts.pdf

[B] Fiber Optic Lighting in Low Temperature Reach-in Refrigerated Display Cases [ET 05.04]. Southern California Edison RTTC. December 2006

[C] http://www.energy.ca.gov/2012publications/CEC-400-2012-019/CEC-400-2012-019-CMF.pdf

[D]  http://www.energy.ca.gov/2012publications/CEC-400-2012-004/CEC-400-2012-004-CMF.pdf

[E]  http://www.gpo.gov/fdsys/pkg/CFR-2012-title10-vol3/pdf/CFR-2012-title10-vol3-sec430-32.pdf

[F] Attachment 3 – LEDDisplay Cases Fixture Specs.zip

[G] Attachment 6 – LG098.1 Calcs – Vertical LED.xls

[H] Attachment 5 - 3&4ft. LEDs.zip

[I] Attachment 7 – LG098.1 Calcs – Horizontal LED 3ft.xls

[J] Attachment 8 – LG098.1 Calcs – Horizontal LED 4ft.xls

[K]  DEER 2014 (2014). “DEER Database: 2014 Update Documentation”.

[L]  IES, 9th Edition, Fig 6.2

[M]  Thermal Management of White LEDs. DOE. February 2007

[N] ASHRAE. (1982). Climatic Data for Region X

[O]  SCE’s Analysis of Compressor Manufacturer Data for Reciprocating Compressors. 2004

[P]  2001 Express Efficiency.  New Refrigeration Measure Computer Simulation Report.  pp. 20-21, Table 2

[Q]  Attachment 4 – Single Compressor Reach-in DisplayCase.pdf

[R]  Attachment 1 – Calculation Template v4.0.xlsm

[S] Revised DEER Measure Cost Summary (05_30_2008) Revised(06_02_2008).xls

[T]  Attachment 9 – LED Cost.txt

[U] D.12.05.015 Attachment A, A - 1

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |