Work Paper SCE13LG106

Revision 2

Southern California Edison Company

MR16, PAR20, PAR30, PAR38, A-Type, Candelabra Lamps, and Residential LED Lamp Giveaway

# At-a-Glance Summary

| Applicable Measure Codes: | Various |
| --- | --- |
| Measure Description: | MR, PAR, A, and Candelabra LED lamps |
| Base Case Description: | MR, PAR, A, and Candelabra halogen/incandescent lamps |
| Energy Impact Common Units: | lamp |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | Varies by lamp and building type |
| Measure Application Type: | Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | DI: 0.85, Com default: 0.60, Res default: 0.55 |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13LG106.0 | No | 05/02/12 | Yun Han/SCE | - Original work paper from WPSCNRLG0106.2 - Updated to latest WP template v0.1 - Added PAR20 measures - Used DEER recommended wattage ratios for all measures to calculate baseline |
| SCE13LG106.1 | Yes | 09/05/13 | Jason Wang/SCE | - Per 3/1/13 ED Lighting Retrofit Disposition, the measure case wattages were adjusted to more conservative values. - Updated code to T20 2012 and T24 2013 - Added in the solution codes for PAR20 measures. - Added EUL_ID of “Non-DEER” - Added new measures from PG&E, including candelabras |
| SCE13LG106.2 | Yes | 02/20/14 | Yun Han/SCE | - New WP template - SCE13LG079.0 merged to this WP (Added LT-10754 8 Watt Giveaway LED) - Work paper updated for reporting period, effective 7/1/14 – 12/31/14 - Savings updated based on 5/30/14 ED disposition - Added A-lamp measures exclusively for hotel/motel (LT-30499, LT-74612) - Changed Non-CFL to CFL factors, including load shape (per D.12-05-015, Attachment A, page 9) |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper documents the E3 Calculator inputs for replacing conventional MR-16, PAR20, PAR30, and PAR38 halogen lamps, and candelabra and A-type incandescent lamps with Energy Star certified LED lamps. The LED lamps shall generate equal or greater lumen output at lower power consumption than their base case counterparts or provide equal or greater center beam candle power for directional lamps to achieve energy savings.  Table 1 lists the measures included in this work paper.

Table 1 Measure Names

| Solution Code | Measure |
| --- | --- |
| LT-12834 | < 10 Watt A-Lamp LED |
| LT-10965 | 10 Watt to 30 Watt A-Lamp LED |
| LT-45662 | < 8 Watt A-Lamp LED |
| LT-22929 | 8 Watt to < 9 Watt A-Lamp LED |
| LT-54980 | 9 Watt to < 10 Watt A-Lamp LED |
| LT-64121 | 10 Watt to < 11 Watt A-Lamp LED |
| LT-78423 | 11 Watt to < 12 Watt A-Lamp LED |
| LT-89542 | 12 Watt to < 13 Watt A-Lamp LED |
| LT-90243 | 13 Watt to < 14 Watt A-Lamp LED |
| LT-10795 | 14 Watt to < 15 Watt A-Lamp LED |
| LT-56673 | 15 Watt to < 16 Watt A-Lamp LED |
| LT-78681 | 16 Watt to < 17 Watt A-Lamp LED |
| LT-95419 | 17 Watt to < 18 Watt A-Lamp LED |
| LT-32283 | 18 Watt to < 19 Watt A-Lamp LED |
| LT-43162 | 19 Watt to < 20 Watt A-Lamp LED |
| LT-62527 | 20 Watt to < 21 Watt A-Lamp LED |
| LT-55248 | 21 Watt to < 22 Watt A-Lamp LED |
| LT-92044 | 22 Watt to < 23 Watt A-Lamp LED |
| LT-39756 | 23 Watt to < 24 Watt A-Lamp LED |
| LT-26164 | 24 Watt to < 25 Watt A-Lamp LED |
| LT-28046 | >= 25 Watt A-Lamp LED |
| LT-28653 | < 10 Watt A-Lamp (Common Area) LED |
| LT-98643 | 10 Watt to 30 Watt A-Lamp (Common Area) LED |
| LT-33509 | < 8 Watt A-Lamp (Common Area) LED |
| LT-67884 | 8 Watt to < 9 Watt A-Lamp (Common Area) LED |
| LT-78625 | 9 Watt to < 10 Watt A-Lamp (Common Area) LED |
| LT-55814 | 10 Watt to < 11 Watt A-Lamp (Common Area) LED |
| LT-61249 | 11 Watt to < 12 Watt A-Lamp (Common Area) LED |
| LT-40712 | 12 Watt to < 13 Watt A-Lamp (Common Area) LED |
| LT-41701 | 13 Watt to < 14 Watt A-Lamp (Common Area) LED |
| LT-27084 | 14 Watt to < 15 Watt A-Lamp (Common Area) LED |
| LT-89729 | 15 Watt to < 16 Watt A-Lamp (Common Area) LED |
| LT-95724 | 16 Watt to < 17 Watt A-Lamp (Common Area) LED |
| LT-16665 | 17 Watt to < 18 Watt A-Lamp (Common Area) LED |
| LT-45182 | 18 Watt to < 19 Watt A-Lamp (Common Area) LED |
| LT-22361 | 19 Watt to < 20 Watt A-Lamp (Common Area) LED |
| LT-27872 | 20 Watt to < 21 Watt A-Lamp (Common Area) LED |
| LT-98958 | 21 Watt to < 22 Watt A-Lamp (Common Area) LED |
| LT-90897 | 22 Watt to < 23 Watt A-Lamp (Common Area) LED |
| LT-75523 | 23 Watt to < 24 Watt A-Lamp (Common Area) LED |
| LT-61474 | 24 Watt to < 25 Watt A-Lamp (Common Area) LED |
| LT-72265 | >= 25 Watt A-Lamp (Common Area) LED |
| LT-37098 | < 10 Watt A-Lamp (Dwelling Area) LED |
| LT-10432 | 10 Watt to 30 Watt A-Lamp (Dwelling Area) LED |
| LT-49398 | < 8 Watt A-Lamp (Dwelling Area) LED |
| LT-53867 | 8 Watt to < 9 Watt A-Lamp (Dwelling Area) LED |
| LT-91742 | 9 Watt to < 10 Watt A-Lamp (Dwelling Area) LED |
| LT-10495 | 10 Watt to < 11 Watt A-Lamp (Dwelling Area) LED |
| LT-63721 | 11 Watt to < 12 Watt A-Lamp (Dwelling Area) LED |
| LT-29876 | 12 Watt to < 13 Watt A-Lamp (Dwelling Area) LED |
| LT-72183 | 13 Watt to < 14 Watt A-Lamp (Dwelling Area) LED |
| LT-37254 | 14 Watt to < 15 Watt A-Lamp (Dwelling Area) LED |
| LT-28893 | 15 Watt to < 16 Watt A-Lamp (Dwelling Area) LED |
| LT-50240 | 16 Watt to < 17 Watt A-Lamp (Dwelling Area) LED |
| LT-73324 | 17 Watt to < 18 Watt A-Lamp (Dwelling Area) LED |
| LT-14853 | 18 Watt to < 19 Watt A-Lamp (Dwelling Area) LED |
| LT-95896 | 19 Watt to < 20 Watt A-Lamp (Dwelling Area) LED |
| LT-13541 | 20 Watt to < 21 Watt A-Lamp (Dwelling Area) LED |
| LT-85821 | 21 Watt to < 22 Watt A-Lamp (Dwelling Area) LED |
| LT-84121 | 22 Watt to < 23 Watt A-Lamp (Dwelling Area) LED |
| LT-90125 | 23 Watt to < 24 Watt A-Lamp (Dwelling Area) LED |
| LT-48765 | 24 Watt to < 25 Watt A-Lamp (Dwelling Area) LED |
| LT-10844 | >= 25 Watt A-Lamp (Dwelling Area) LED |
| LT-89075 | < 8 Watt PAR20 LED |
| LT-91612 | 8 Watt to 12 Watt PAR20 LED |
| LT-20730 | < 6 Watt PAR20 LED |
| LT-49725 | 6 Watt to < 7 Watt PAR20 LED |
| LT-10919 | 7 Watt to < 8 Watt PAR20 LED |
| LT-87178 | 8 Watt to < 9 Watt PAR20 LED |
| LT-89267 | 9 Watt to < 10 Watt PAR20 LED |
| LT-90684 | >= 10 Watt PAR20 LED |
| LT-92433 | < 8 Watt PAR20 (Common Area) LED |
| LT-11912 | 8 Watt to 12 Watt PAR20 (Common Area) LED |
| LT-65597 | < 6 Watt PAR20 (Common Area) LED |
| LT-13017 | 6 Watt to < 7 Watt PAR20 (Common Area) LED |
| LT-18948 | 7 Watt to < 8 Watt PAR20 (Common Area) LED |
| LT-29846 | 8 Watt to < 9 Watt PAR20 (Common Area) LED |
| LT-30941 | 9 Watt to < 10 Watt PAR20 (Common Area) LED |
| LT-29462 | >= 10 Watt PAR20 (Common Area) LED |
| LT-93111 | < 8 Watt PAR20 (Dwelling Area) LED |
| LT-16566 | 8 Watt to 12 Watt PAR20 (Dwelling Area) LED |
| LT-39956 | < 6 Watt PAR20 (Dwelling Area) LED |
| LT-32654 | 6 Watt to < 7 Watt PAR20 (Dwelling Area) LED |
| LT-49596 | 7 Watt to < 8 Watt PAR20 (Dwelling Area) LED |
| LT-46460 | 8 Watt to < 9 Watt PAR20 (Dwelling Area) LED |
| LT-56172 | 9 Watt to < 10 Watt PAR20 (Dwelling Area) LED |
| LT-65498 | >= 10 Watt PAR20 (Dwelling Area) LED |
| LT-65785 | < 15 Watt PAR30 LED |
| LT-89789 | 15 Watt to 21 Watt PAR30 LED |
| LT-29560 | < 10 Watt PAR30 LED |
| LT-38391 | 10 Watt to < 11 Watt PAR30 LED |
| LT-38887 | 11 Watt to < 12 Watt PAR30 LED |
| LT-49889 | 12 Watt to < 13 Watt PAR30 LED |
| LT-85840 | 13 Watt to < 14 Watt PAR30 LED |
| LT-13840 | 14 Watt to < 15 Watt PAR30 LED |
| LT-98682 | 15 Watt to < 16 Watt PAR30 LED |
| LT-76561 | 16 Watt to < 17 Watt PAR30 LED |
| LT-82047 | 17 Watt to < 18 Watt PAR30 LED |
| LT-47333 | 18 Watt to < 19 Watt PAR30 LED |
| LT-53339 | 19 Watt to < 20 Watt PAR30 LED |
| LT-72786 | >= 20 Watt PAR30 LED |
| LT-79453 | < 15 Watt PAR30 (Common Area) LED |
| LT-57621 | 15 Watt to 21 Watt PAR30 (Common Area) LED |
| LT-58543 | < 10 Watt PAR30 (Common Area) LED |
| LT-56977 | 10 Watt to < 11 Watt PAR30 (Common Area) LED |
| LT-23336 | 11 Watt to < 12 Watt PAR30 (Common Area) LED |
| LT-67054 | 12 Watt to < 13 Watt PAR30 (Common Area) LED |
| LT-73654 | 13 Watt to < 14 Watt PAR30 (Common Area) LED |
| LT-15208 | 14 Watt to < 15 Watt PAR30 (Common Area) LED |
| LT-93469 | 15 Watt to < 16 Watt PAR30 (Common Area) LED |
| LT-74244 | 16 Watt to < 17 Watt PAR30 (Common Area) LED |
| LT-35298 | 17 Watt to < 18 Watt PAR30 (Common Area) LED |
| LT-55621 | 18 Watt to < 19 Watt PAR30 (Common Area) LED |
| LT-78587 | 19 Watt to < 20 Watt PAR30 (Common Area) LED |
| LT-61725 | >= 20 Watt PAR30 (Common Area) LED |
| LT-87621 | < 15 Watt PAR30 (Dwelling Area) LED |
| LT-60932 | 15 Watt to 21 Watt PAR30 (Dwelling Area) LED |
| LT-86204 | < 10 Watt PAR30 (Dwelling Area) LED |
| LT-87965 | 10 Watt to < 11 Watt PAR30 (Dwelling Area) LED |
| LT-67912 | 11 Watt to < 12 Watt PAR30 (Dwelling Area) LED |
| LT-98765 | 12 Watt to < 13 Watt PAR30 (Dwelling Area) LED |
| LT-39240 | 13 Watt to < 14 Watt PAR30 (Dwelling Area) LED |
| LT-15476 | 14 Watt to < 15 Watt PAR30 (Dwelling Area) LED |
| LT-87961 | 15 Watt to < 16 Watt PAR30 (Dwelling Area) LED |
| LT-27168 | 16 Watt to < 17 Watt PAR30 (Dwelling Area) LED |
| LT-54713 | 17 Watt to < 18 Watt PAR30 (Dwelling Area) LED |
| LT-46919 | 18 Watt to < 19 Watt PAR30 (Dwelling Area) LED |
| LT-62358 | 19 Watt to < 20 Watt PAR30 (Dwelling Area) LED |
| LT-77038 | >= 20 Watt PAR30 (Dwelling Area) LED |
| LT-90344 | < 17 Watt PAR38 LED |
| LT-92133 | 17 Watt to 25 Watt PAR38 LED |
| LT-22743 | < 12 Watt PAR38 LED |
| LT-71886 | 12 Watt to < 13 Watt PAR38 LED |
| LT-19711 | 13 Watt to < 14 Watt PAR38 LED |
| LT-69480 | 14 Watt to < 15 Watt PAR38 LED |
| LT-34275 | 15 Watt to < 16 Watt PAR38 LED |
| LT-67816 | 16 Watt to < 17 Watt PAR38 LED |
| LT-27996 | 17 Watt to < 18 Watt PAR38 LED |
| LT-71514 | 18 Watt to < 19 Watt PAR38 LED |
| LT-43354 | 19 Watt to < 20 Watt PAR38 LED |
| LT-95006 | 20 Watt to < 21 Watt PAR38 LED |
| LT-20374 | 21 Watt to < 22 Watt PAR38 LED |
| LT-21907 | 22 Watt to < 23 Watt PAR38 LED |
| LT-48709 | 23 Watt to < 24 Watt PAR38 LED |
| LT-43942 | 24 Watt to < 25 Watt PAR38 LED |
| LT-65525 | 25 Watt to < 26 Watt PAR38 LED |
| LT-59745 | 26 Watt to < 27 Watt PAR38 LED |
| LT-58476 | >= 27 Watt PAR38 LED |
| LT-34365 | < 17 Watt PAR38 (Common Area) LED |
| LT-76981 | 17 Watt to 25 Watt PAR38 (Common Area) LED |
| LT-68754 | < 12 Watt PAR38 (Common Area) LED |
| LT-76587 | 12 Watt to < 13 Watt PAR38 (Common Area) LED |
| LT-12326 | 13 Watt to < 14 Watt PAR38 (Common Area) LED |
| LT-89034 | 14 Watt to < 15 Watt PAR38 (Common Area) LED |
| LT-91034 | 15 Watt to < 16 Watt PAR38 (Common Area) LED |
| LT-91663 | 16 Watt to < 17 Watt PAR38 (Common Area) LED |
| LT-67849 | 17 Watt to < 18 Watt PAR38 (Common Area) LED |
| LT-73876 | 18 Watt to < 19 Watt PAR38 (Common Area) LED |
| LT-21719 | 19 Watt to < 20 Watt PAR38 (Common Area) LED |
| LT-28020 | 20 Watt to < 21 Watt PAR38 (Common Area) LED |
| LT-90289 | 21 Watt to < 22 Watt PAR38 (Common Area) LED |
| LT-89886 | 22 Watt to < 23 Watt PAR38 (Common Area) LED |
| LT-44444 | 23 Watt to < 24 Watt PAR38 (Common Area) LED |
| LT-98624 | 24 Watt to < 25 Watt PAR38 (Common Area) LED |
| LT-89165 | 25 Watt to < 26 Watt PAR38 (Common Area) LED |
| LT-25103 | 26 Watt to < 27 Watt PAR38 (Common Area) LED |
| LT-56386 | >= 27 Watt PAR38 (Common Area) LED |
| LT-46598 | < 17 Watt PAR38 (Dwelling Area) LED |
| LT-89543 | 17 Watt to 25 Watt PAR38 (Dwelling Area) LED |
| LT-93897 | < 12 Watt PAR38 (Dwelling Area) LED |
| LT-10395 | 12 Watt to < 13 Watt PAR38 (Dwelling Area) LED |
| LT-43500 | 13 Watt to < 14 Watt PAR38 (Dwelling Area) LED |
| LT-15012 | 14 Watt to < 15 Watt PAR38 (Dwelling Area) LED |
| LT-66727 | 15 Watt to < 16 Watt PAR38 (Dwelling Area) LED |
| LT-97963 | 16 Watt to < 17 Watt PAR38 (Dwelling Area) LED |
| LT-98642 | 17 Watt to < 18 Watt PAR38 (Dwelling Area) LED |
| LT-31995 | 18 Watt to < 19 Watt PAR38 (Dwelling Area) LED |
| LT-35132 | 19 Watt to < 20 Watt PAR38 (Dwelling Area) LED |
| LT-17721 | 20 Watt to < 21 Watt PAR38 (Dwelling Area) LED |
| LT-97480 | 21 Watt to < 22 Watt PAR38 (Dwelling Area) LED |
| LT-20575 | 22 Watt to < 23 Watt PAR38 (Dwelling Area) LED |
| LT-91264 | 23 Watt to < 24 Watt PAR38 (Dwelling Area) LED |
| LT-39507 | 24 Watt to < 25 Watt PAR38 (Dwelling Area) LED |
| LT-21854 | 25 Watt to < 26 Watt PAR38 (Dwelling Area) LED |
| LT-16127 | 26 Watt to < 27 Watt PAR38 (Dwelling Area) LED |
| LT-41095 | >= 27 Watt PAR38 (Dwelling Area) LED |
| LT-19877 | < 6 Watt MR16 LED |
| LT-54654 | 6 Watt to 10 Watt MR16 LED |
| LT-87923 | 6 Watt to < 7 Watt MR16 LED |
| LT-70734 | 7 Watt to < 8 Watt MR16 LED |
| LT-49384 | 8 Watt to < 9 Watt MR16 LED |
| LT-50786 | 9 Watt to < 10 Watt MR16 LED |
| LT-67244 | 10 Watt to < 11 Watt MR16 LED |
| LT-39798 | 11 Watt to < 12 Watt MR16 LED |
| LT-49980 | >= 12 Watt MR16 LED |
| LT-23678 | < 6 Watt MR16 (Common Area) LED |
| LT-46876 | 6 Watt to 10 Watt MR16 (Common Area) LED |
| LT-34578 | 6 Watt to < 7 Watt MR16 (Common Area) LED |
| LT-50832 | 7 Watt to < 8 Watt MR16 (Common Area) LED |
| LT-78066 | 8 Watt to < 9 Watt MR16 (Common Area) LED |
| LT-77649 | 9 Watt to < 10 Watt MR16 (Common Area) LED |
| LT-50434 | 10 Watt to < 11 Watt MR16 (Common Area) LED |
| LT-60980 | 11 Watt to < 12 Watt MR16 (Common Area) LED |
| LT-83345 | >= 12 Watt MR16 (Common Area) LED |
| LT-34091 | < 6 Watt MR16 (Dwelling Area) LED |
| LT-59765 | 6 Watt to 10 Watt MR16 (Dwelling Area) LED |
| LT-34687 | 6 Watt to < 7 Watt MR16 (Dwelling Area) LED |
| LT-89037 | 7 Watt to < 8 Watt MR16 (Dwelling Area) LED |
| LT-18539 | 8 Watt to < 9 Watt MR16 (Dwelling Area) LED |
| LT-78912 | 9 Watt to < 10 Watt MR16 (Dwelling Area) LED |
| LT-98882 | 10 Watt to < 11 Watt MR16 (Dwelling Area) LED |
| LT-90345 | 11 Watt to < 12 Watt MR16 (Dwelling Area) LED |
| LT-27314 | >= 12 Watt MR16 (Dwelling Area) LED |
| LT-76109 | < 1 Watt Candelabra LED |
| LT-79284 | 1 Watt to < 2 Watt Candelabra LED |
| LT-48077 | 2 Watt to < 3 Watt Candelabra LED |
| LT-48560 | 3 Watt to < 4 Watt Candelabra LED |
| LT-48123 | >= 4 Watt Candelabra LED |
| LT-69087 | < 1 Watt Candelabra (Common Area) LED |
| LT-93364 | 1 Watt to < 2 Watt Candelabra (Common Area) LED |
| LT-78570 | 2 Watt to < 3 Watt Candelabra (Common Area) LED |
| LT-39568 | 3 Watt to < 4 Watt Candelabra (Common Area) LED |
| LT-78489 | >= 4 Watt Candelabra (Common Area) LED |
| LT-28818 | < 1 Watt Candelabra (Dwelling Area) LED |
| LT-63685 | 1 Watt to < 2 Watt Candelabra (Dwelling Area) LED |
| LT-34547 | 2 Watt to < 3 Watt Candelabra (Dwelling Area) LED |
| LT-90388 | 3 Watt to < 4 Watt Candelabra (Dwelling Area) LED |
| LT-70545 | >= 4 Watt Candelabra (Dwelling Area) LED |
| LT-10754 | 8 Watt Giveaway LED |
| LT-30499 | < 10 Watt A-Lamp LED (Hotel/Motel) |
| LT-74612 | 10 Watt to 30 Watt A-Lamp LED (Hotel/Motel) |

Measures in this work paper must be on Energy Star’s qualified product list [] to receive incentives.

## 1.2 Technical Description

The lamps in this workpaper come in variety of bases based on the type. A-lamps and all PAR lamps come in a standard E26 screw-base, Candelabra in E12, and MR16 in GU5.3 which match the baseline counterpart. They are used in many different applications around the house that match their base.

## 1.3 Measure Application Type

The delivery method for the LED Giveaway is:

- Financial Support / Giveaway

The delivery methods for Hotel/Motel, Dwelling Area, and Common Area measures are:

- Financial Support / Direct Install

- Financial Support / Down-Stream Incentive - Deemed

The delivery methods for the rest of the measures are:

- Financial Support / Direct Install

- Financial Support / Down-Stream Incentive – Deemed

- Midstream Programs / Mid-Stream Incentive

- Upstream Programs / Up-Stream Incentive

The incentive method for all delivery methods is:

- Replace on Burnout (ROB).

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | Yes |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER does not contain LED lamps |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | Any | 0.60 |
| Ind-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ind | Any | Any | 0.60 |
| Agric-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ag | Any | Any | 0.60 |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | Any | 0.55 |
| Com-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Com | Any | DirInstall | 0.85 |
| Ind-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ind | Any | DirInstall | 0.85 |
| Agricult-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ag | Any | DirInstall | 0.85 |
| Res-Default-HTR-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis. This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the residential/non-residential defaulted NTG value, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measue Case UseCategory | Lighting |
| Measure Case UseSubCats | Indoor General Lighting, Indoor Common Area Lighting |
| Measure Case TechGroups | Ltg_Lamp |
| Measure Case TechTypes | LED_Lamp |
| Base Case TechGroups | Ltg_Lamp |
| Base Case TechTypes | Incan_lamp Hal_lamp Non-DEER |

### 1.4.2 Codes and Standards Analysis

Title 20: According to Title 20 2014 [422], Section 1605.1(k) – Lamps section lists the minimum requirements for incandescent reflector lamps, medium base compact fluorescent lamps, and general service incandescent lamps which affect the measures in this work paper.

Energy Star: Energy Star issued a document, ENERGY STAR Program Requirements for Integral LED Lamps – Partner Commitments Version 1.4 [] which details the Energy Star requirements for Integral LED Lamps. The requirements in the document consist of two parts; general requirement for all LED lamps and lamp type specific requirement. Those requirements are the minimum requirements for an integral LED lamp to be adopted by any SCE energy efficiency program.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | 2013 Non-Residential Compliance Manual | July 1, 2014 |
| Title 20 (2014) | 2014 Appliance Efficiency Regulations | December 3, 2013 |
| Energy Star | Version 1.4 | 2012 |

Although code exists, this work paper uses recommended wattage reduction ratios from the Energy Division’s Workpaper Disposition for Lighting Retrofits (30May2014 []) to calculate the base case wattage. Therefore, Title 20 code does not apply.

Replacing lamps does not trigger Title 24 2013 [355].

### 1.4.3 Non-DEER Study Review

ET 10.29 LED A-19 Lamps [417], ET07.14 LED MR16 [418], and ET07.12 LED Screw-in Directional Lamps [419] reports were used to qualify the technologies in this workpaper.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2015 program cycle extension on www.deeresources.com. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436] was consulted. Table 7 below identifies the value/methodology used for the measures in this work paper.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| ILtg-Com-LED-20000hr | Non-Residential, Residential | Lighting | LED Lamps | Varies by building type EUL = Rated Life of Lamp / Annual Usage | N/A |
| ILtg-Com-LED-15000hr | Non-Residential, Residential | Lighting | LED Lamps | Varies by building type EUL = Rated Life of Lamp / Annual Usage | N/A |

Table 8 shows the EUL for the measures in this work paper.  According to the disposition, the rated life of the lamp for all LEDs is 20,000 hours (Table 8), except for Candelabras which are 15,000 hours (Table 9). The maximum EUL for Nonresidential is 12 years and 16 for Residential.

Table 8 Effective Useful Life for Different Building Types (Non-Candelabra)

| Building Types | Annual CFL Hours | EUL (years) |
| --- | --- | --- |
| Agricultural | 2708.0 | 7.4 |
| Assembly | 2297.7 | 8.7 |
| Education - Primary School | 2236.7 | 8.9 |
| Education - Secondary School | 2327.0 | 8.6 |
| Education - Relocatable Classroom | 2594.7 | 7.7 |
| Education - Community College | 2414.7 | 8.3 |
| Education - University | 2364.7 | 8.5 |
| Grocery | 3887.5 | 5.1 |
| Food Store | 3948.8 | 5.1 |
| Health/Medical - Hospital | 4199.6 | 4.8 |
| Health/Medical - Nursing Home | 3568.4 | 5.6 |
| Health/Medical - Clinic | 2965.8 | 6.7 |
| Lodging - Hotel | 1668.8 | 12.0 |
| Lodging - Guest Rooms | 1368.4 | 12.0 |
| Lodging - Motel | 1368.4 | 12.0 |
| Manufacturing - Bio/Tech | 3087.1 | 6.5 |
| Manufacturing - Light Industrial | 2580.0 | 7.8 |
| Industrial | 2833.6 | 7.1 |
| Misc - Commercial | 3089.2 | 6.5 |
| Office - Large | 2996.8 | 6.7 |
| Office - Small | 2965.8 | 6.7 |
| Restaurant - Fast-Food | 4810.0 | 4.2 |
| Restaurant - Sit-Down | 4830.0 | 4.1 |
| Retail - Multistory Large | 3710.0 | 5.4 |
| Retail - Single-Story Large | 4349.4 | 4.6 |
| Retail - Small | 4010.0 | 5.0 |
| Storage - Conditioned | 2758.8 | 7.2 |
| Storage - Unconditioned | 2758.8 | 7.2 |
| Transportation - Communication - Utilities | 2812.0 | 7.1 |
| Warehouse - Refrigerated | 4725.2 | 4.2 |
| Residential Single Family | 541.0 | 16.0 |
| Residential Multi-family | 541.0 | 16.0 |
| Residential Mobile Home - Double-Wide | 541.0 | 16.0 |
| Residential Single Family (Common Area) | 541.0 | 16.0 |
| Residential Multi-family (Common Area) | 6132.0 | 3.3 |
| Residential Mobile Home - Double-Wide (Common Area) | 6132.0 | 3.3 |
| Residential Single Family (Dwelling Area) | 541.00 | 16.0 |
| Residential Multi-family (Dwelling Area) | 541.00 | 16.0 |
| Residential Mobile Home - Double-Wide | 541.00 | 16.0 |

Table 9 Effective Useful Life for Different Building Types (Candelabra)

| Building Types | Annual CFL Hours | EUL (years) |
| --- | --- | --- |
| Agricultural | 2708.0 | 5.5 |
| Assembly | 2297.7 | 6.5 |
| Education - Primary School | 2236.7 | 6.7 |
| Education - Secondary School | 2327.0 | 6.4 |
| Education - Relocatable Classroom | 2594.7 | 5.8 |
| Education - Community College | 2414.7 | 6.2 |
| Education - University | 2364.7 | 6.3 |
| Grocery | 3887.5 | 3.9 |
| Food Store | 3948.8 | 3.8 |
| Health/Medical - Hospital | 4199.6 | 3.6 |
| Health/Medical - Nursing Home | 3568.4 | 4.2 |
| Health/Medical - Clinic | 2965.8 | 5.1 |
| Lodging - Hotel | 1668.8 | 9.0 |
| Lodging - Guest Rooms | 1368.4 | 11.0 |
| Lodging - Motel | 1368.4 | 11.0 |
| Manufacturing - Bio/Tech | 3087.1 | 4.9 |
| Manufacturing - Light Industrial | 2580.0 | 5.8 |
| Industrial | 2833.6 | 5.3 |
| Misc - Commercial | 3089.2 | 4.9 |
| Office - Large | 2996.8 | 5.0 |
| Office - Small | 2965.8 | 5.1 |
| Restaurant - Fast-Food | 4810.0 | 3.1 |
| Restaurant - Sit-Down | 4830.0 | 3.1 |
| Retail - Multistory Large | 3710.0 | 4.0 |
| Retail - Single-Story Large | 4349.4 | 3.4 |
| Retail - Small | 4010.0 | 3.7 |
| Storage - Conditioned | 2758.8 | 5.4 |
| Storage - Unconditioned | 2758.8 | 5.4 |
| Transportation - Communication - Utilities | 2812.0 | 5.3 |
| Warehouse - Refrigerated | 4725.2 | 3.2 |
| Residential Single Family | 541.0 | 16.0 |
| Residential Multi-family | 541.0 | 16.0 |
| Residential Mobile Home - Double-Wide | 541.0 | 16.0 |
| Residential Single Family (Common Area) | 541.00 | 16.0 |
| Residential Multi-family (Common Area) | 6132.00 | 2.4 |
| Residential Mobile Home - Double-Wide (Common Area) | 6132.00 | 2.4 |
| Residential Single Family (Dwelling Area) | 541.00 | 16.0 |
| Residential Multi-family (Dwelling Area) | 541.00 | 16.0 |
| Residential Mobile Home - Double-Wide | 541.00 | 16.0 |

# Section 2. Energy Savings & Demand Reduction Calculations

The energy savings estimates are calculated as follows:

The annual energy savings are based on wattage difference per lamp, DEER annual hours, and interactive effects by Building Type.

Omnidirectional Lamps (A Type Lamp)

This work paper contains the following A-Lamp LED measures:

Table 10 A-lamp Measures and Wattages

| Measure* | Measure Case Wattage (W) | Source of Measure Case Wattage Value | Base Case Wattage (W) | Delta Watts (W) |
| --- | --- | --- | --- | --- |
| < 10 Watt A-Lamp LED | 4 | ED Disposition | 11.84 | 7.84 |
| 10 Watt to 30 Watt A-Lamp LED | 10 | ED Disposition | 29.6 | 19.6 |
| < 8 Watt A-Lamp LED | 6 | Determined by SCE | 17.76 | 11.76 |
| 8 Watt to < 9 Watt A-Lamp LED | 8 | Determined by SCE | 23.68 | 15.68 |
| 9 Watt to < 10 Watt A-Lamp LED | 9 | Determined by SCE | 26.64 | 17.64 |
| 10 Watt to < 11 Watt A-Lamp LED | 10 | Determined by SCE | 29.6 | 19.6 |
| 11 Watt to < 12 Watt A-Lamp LED | 11 | Determined by SCE | 32.56 | 21.56 |
| 12 Watt to < 13 Watt A-Lamp LED | 12 | Determined by SCE | 35.52 | 23.52 |
| 13 Watt to < 14 Watt A-Lamp LED | 13 | Determined by SCE | 38.48 | 25.48 |
| 14 Watt to < 15 Watt A-Lamp LED | 14 | Determined by SCE | 41.44 | 27.44 |
| 15 Watt to < 16 Watt A-Lamp LED | 15 | Determined by SCE | 44.4 | 29.4 |
| 16 Watt to < 17 Watt A-Lamp LED | 16 | Determined by SCE | 47.36 | 31.36 |
| 17 Watt to < 18 Watt A-Lamp LED | 17 | Determined by SCE | 50.32 | 33.32 |
| 18 Watt to < 19 Watt A-Lamp LED | 18 | Determined by SCE | 53.28 | 35.28 |
| 19 Watt to < 20 Watt A-Lamp LED | 19 | Determined by SCE | 56.24 | 37.24 |
| 20 Watt to < 21 Watt A-Lamp LED | 20 | Determined by SCE | 59.2 | 39.2 |
| 21 Watt to < 22 Watt A-Lamp LED | 21 | Determined by SCE | 62.16 | 41.16 |
| 22 Watt to < 23 Watt A-Lamp LED | 22 | Determined by SCE | 65.12 | 43.12 |
| 23 Watt to < 24 Watt A-Lamp LED | 23 | Determined by SCE | 68.08 | 45.08 |
| 24 Watt to < 25 Watt A-Lamp LED | 24 | Determined by SCE | 71.04 | 47.04 |
| >= 25 Watt A-Lamp LED | 25 | Determined by SCE | 74 | 49 |
| 8 Watt Giveaway LED | 8 | ED Disposition | 23.68 | 15.68 |
| < 10 Watt A-Lamp LED (Hotel/Motel) | 4 | ED Disposition | 11.84 | 7.84 |
| 10 Watt to 30 Watt A-Lamp LED (Hotel/Motel) | 10 | ED Disposition | 29.6 | 19.6 |

*Each of these measures has a Common Area and Dwelling Area variant, which share the same delta watts but are not shown here.

Energy Star Program Requirements for Integral LED Lamps, Version 1.4; Section 7A [B] defines the Minimum Light Output using the IES LM-79-08 Test Procedure. Based on Energy Star’s minimum criteria, A-lamps must output 50 lm/W for LEDs <10W and 55 lm/W for LEDs ≥10W.  Using the minimum light output required for nominal incandescent watts, “LED watts” are calculated as shown in Table 11 for both efficacies. By using the wattage limitations, the “Average Watts” values in Table 11 are the A-lamp LED watts to be used in this work paper. The calculations can be found in the attachment [].

Table 11 LED Watts

| Energy Star Range |  | LED Watts |  | Average Watts |  |
| --- | --- | --- | --- | --- | --- |
| Nominal Incandescent Watts | Minimum Light output of LED Lamps* (Lumen) | 50 lm/W (<10W) | 55 lm/W (≥10W) | Measure | Average Wattage |
| 25 | 200 | 4.00 | 3.64 | < 10 Watt A-Lamp LED | 6.50 |
| 35 | 325 | 6.50 | 5.91 |  |  |
| 40 | 450 | 9.00 | 8.18 |  |  |
| 60 | 800 | 16.00 | 14.55 | 10 Watt to 30 Watt A-Lamp LED | 21.21 |
| 75 | 1,100 | 22.00 | 20.00 |  |  |
| 100 | 1,600 | 32.00 | 29.09 |  |  |

*Energy Star’s Integral Lamp specs.

Instead of using the calculated wattages in Table 11, ED’s disposition [C] recommends the measure wattage to be 4W for first range and 10 W for second range. ED also recommends wattage ratios for calculating baseline lamp wattage. The recommended wattage ratio of 2.96 is multiplied by the A-lamp LED Watts to calculate the base case. Based on the disposition, the new wattages are shown in Table 12. Measures determined by SCE in Table 10 also use the same wattage reduction ratio to calculate the base watts.

Table 12 A-Lamp Base and Measure Watts

| Measure Name | Measure Watts | Base Watts | ΔWatts |
| --- | --- | --- | --- |
| Up to 10 Watt Exterior A-Lamp LED | 4 | 11.84 | 7.84 |
| Up to 30 Watt Exterior A-Lamp LED | 10 | 29.6 | 19.6 |

Directional Lamps (MR and PAR Lamps)

This work paper contains the following MR and PAR LED measures:

Table 13 MR and PAR Measures and Wattages

| Measure* | Measure Case Wattage (W) | Source of Measure Case Wattage Value | Base Case Wattage (W) | Delta Watts (W) |
| --- | --- | --- | --- | --- |
| < 6 Watt MR16 LED | 3 | ED Disposition | 12.72 | 9.72 |
| 6 Watt to 10 Watt MR16 LED | 6 | ED Disposition | 25.44 | 19.44 |
| 6 Watt to < 7 Watt MR16 LED | 6 | Determined by SCE | 25.44 | 19.44 |
| 7 Watt to < 8 Watt MR16 LED | 7 | Determined by SCE | 29.68 | 22.68 |
| 8 Watt to < 9 Watt MR16 LED | 8 | Determined by SCE | 33.92 | 25.92 |
| 9 Watt to < 10 Watt MR16 LED | 9 | Determined by SCE | 38.16 | 29.16 |
| 10 Watt to < 11 Watt MR16 LED | 10 | Determined by SCE | 42.4 | 32.4 |
| 11 Watt to < 12 Watt MR16 LED | 11 | Determined by SCE | 46.64 | 35.64 |
| >= 12 Watt MR16 LED | 12 | Determined by SCE | 50.88 | 38.88 |
| < 8 Watt PAR20 LED | 6 | ED Disposition | 28.2 | 22.2 |
| 8 Watt to 12 Watt PAR20 LED | 8 | ED Disposition | 37.6 | 29.6 |
| < 6 Watt PAR20 LED | 4 | Determined by SCE | 18.8 | 14.8 |
| 6 Watt to < 7 Watt PAR20 LED | 6 | Determined by SCE | 28.2 | 22.2 |
| 7 Watt to < 8 Watt PAR20 LED | 7 | Determined by SCE | 32.9 | 25.9 |
| 8 Watt to < 9 Watt PAR20 LED | 8 | Determined by SCE | 37.6 | 29.6 |
| 9 Watt to < 10 Watt PAR20 LED | 9 | Determined by SCE | 42.3 | 33.3 |
| >= 10 Watt PAR20 LED | 10 | Determined by SCE | 47 | 37 |
| < 15 Watt PAR30 LED | 6 | ED Disposition | 20.52 | 14.52 |
| 15 Watt to 21 Watt PAR30 LED | 15 | ED Disposition | 51.3 | 36.3 |
| < 10 Watt PAR30 LED | 8 | Determined by SCE | 27.36 | 19.36 |
| 10 Watt to < 11 Watt PAR30 LED | 10 | Determined by SCE | 34.2 | 24.2 |
| 11 Watt to < 12 Watt PAR30 LED | 11 | Determined by SCE | 37.62 | 26.62 |
| 12 Watt to < 13 Watt PAR30 LED | 12 | Determined by SCE | 41.04 | 29.04 |
| 13 Watt to < 14 Watt PAR30 LED | 13 | Determined by SCE | 44.46 | 31.46 |
| 14 Watt to < 15 Watt PAR30 LED | 14 | Determined by SCE | 47.88 | 33.88 |
| 15 Watt to < 16 Watt PAR30 LED | 15 | Determined by SCE | 51.3 | 36.3 |
| 16 Watt to < 17 Watt PAR30 LED | 16 | Determined by SCE | 54.72 | 38.72 |
| 17 Watt to < 18 Watt PAR30 LED | 17 | Determined by SCE | 58.14 | 41.14 |
| 18 Watt to < 19 Watt PAR30 LED | 18 | Determined by SCE | 61.56 | 43.56 |
| 19 Watt to < 20 Watt PAR30 LED | 19 | Determined by SCE | 64.98 | 45.98 |
| >= 20 Watt PAR30 LED | 20 | Determined by SCE | 68.4 | 48.4 |
| < 17 Watt PAR38 LED | 7 | ED Disposition | 26.67 | 19.67 |
| 17 Watt to 25 Watt PAR38 LED | 17 | ED Disposition | 64.77 | 47.77 |
| < 12 Watt PAR38 LED | 10 | Determined by SCE | 38.1 | 28.1 |
| 12 Watt to < 13 Watt PAR38 LED | 12 | Determined by SCE | 45.72 | 33.72 |
| 13 Watt to < 14 Watt PAR38 LED | 13 | Determined by SCE | 49.53 | 36.53 |
| 14 Watt to < 15 Watt PAR38 LED | 14 | Determined by SCE | 53.34 | 39.34 |
| 15 Watt to < 16 Watt PAR38 LED | 15 | Determined by SCE | 57.15 | 42.15 |
| 16 Watt to < 17 Watt PAR38 LED | 16 | Determined by SCE | 60.96 | 44.96 |
| 17 Watt to < 18 Watt PAR38 LED | 17 | Determined by SCE | 64.77 | 47.77 |
| 18 Watt to < 19 Watt PAR38 LED | 18 | Determined by SCE | 68.58 | 50.58 |
| 19 Watt to < 20 Watt PAR38 LED | 19 | Determined by SCE | 72.39 | 53.39 |
| 20 Watt to < 21 Watt PAR38 LED | 20 | Determined by SCE | 76.2 | 56.2 |
| 21 Watt to < 22 Watt PAR38 LED | 21 | Determined by SCE | 80.01 | 59.01 |
| 22 Watt to < 23 Watt PAR38 LED | 22 | Determined by SCE | 83.82 | 61.82 |
| 23 Watt to < 24 Watt PAR38 LED | 23 | Determined by SCE | 87.63 | 64.63 |
| 24 Watt to < 25 Watt PAR38 LED | 24 | Determined by SCE | 91.44 | 67.44 |
| 25 Watt to < 26 Watt PAR38 LED | 25 | Determined by SCE | 95.25 | 70.25 |
| 26 Watt to < 27 Watt PAR38 LED | 26 | Determined by SCE | 99.06 | 73.06 |
| >= 27 Watt PAR38 LED | 27 | Determined by SCE | 102.87 | 75.87 |

*Each of these measures has a Common Area and Dwelling Area variant, which share the same delta watts but are not shown here.

For the measures in Table 13 where the source of the measure case wattage is “ED Disposition”, the Energy Star Program Requirements for Integral LED Lamps, Version 1.4; Section 7C [B] defines the Minimum Center Beam Intensity (or Center Beam Candle Power, CBCP) for directional lamps as well as to provide a calculator to determine the CBCP value based on the base case lamp wattage and beam angle. The maximum allowable beam angle for MR16 lamps is 50° and 65° for PAR30, and PAR38 lamps. Table 14 lists the CBCP bands per lamp types and base case wattages.

Table 14 Minimum CBCP Bands for Directional Lamps

| Lamp Type | Base Case Power (W) | CBCP Bands (cd) |
| --- | --- | --- |
| MR16 | 20 | CBCP>293 |
| MR16 | 35 | CBCP>536 |
| MR16 | 50 | CBCP>777 |
| PAR20 | 35 | CBCP>293 |
| PAR20 | 50 | CBCP>455 |
| PAR20 | 75 | CBCP>893 |
| PAR30 | 35 | CBCP>340 |
| PAR30 | 50 | CBCP>489 |
| PAR30 | 75 | CBCP>842 |
| PAR38 | 50 | CBCP>436 |
| PAR38 | 75 | CBCP>677 |
| PAR38 | 90 | CBCP>850 |

The measure case wattage was established using Department of Energy, SSL Lamp list and the CBCP bands. The CBCP bands are used to group the listed LED lamps on the SSL Lamp List []. The average wattages of the lamps in each group are used as the measure case wattage as shown in Table 15. A detail description of the calculation can be found in the attachment [D].

Table 15 Original Directional Lamps Delta Watts

| Target Lamp Description | Base Nominal (W) | LED (W) | Measures | Average LED (W) |
| --- | --- | --- | --- | --- |
| MR16 | 20 | 4.23 | < 6 Watt MR16 LED | 3.83 |
| MR16 | 35 | 3.44 |  |  |
| MR16 | 50 | 5.15 | 6 Watt to 10 Watt MR16 LED | 5.15 |
| PAR20 | 35 | 6.04 | < 8 Watt PAR20 LED | 6.79 |
| PAR20 | 50 | 7.55 |  |  |
| PAR20 | 75 | 9.00 | 8 Watt to 12 Watt PAR20 LED | 9 |
| PAR30 | 35 | 9.00 | < 15 Watt PAR30 LED | 9.19 |
| PAR30 | 50 | 9.37 |  |  |
| PAR30 | 75 | 9.99 | < 10 Watt PAR30 LED | 9.99 |
| PAR38 | 50 | 16.30 | < 17 Watt PAR38 LED | 16.3 |
| PAR38 | 75 | 16.20 | 17 Watt to 25 Watt PAR38 LED | 15.6 |
| PAR38 | 90 | 15.01 |  |  |

Instead of using the calculated wattages in Table 15, ED’s disposition [C] recommends using the specified measure wattage with the calculated base case wattage using WRR as shown in Table 16. Measures determined by SCE in Table 13 also use the same wattage reduction ratio to calculate the base watts.

Table 16 New Directional Lamps Delta Watts

| Target Lamp Description | Measure Watts | WRR | Base Watts | ΔWatts |
| --- | --- | --- | --- | --- |
| Up to 6 Watt Exterior MR16 LED | 3 | 4.24 | 12.72 | 9.72 |
| Up to 10 Watt Exterior MR16 LED | 6 | 4.24 | 25.44 | 19.44 |
| Up to 8 Watt Exterior PAR20 LED | 6 | 4.7 | 28.20 | 22.20 |
| Up to 12 Watt Exterior PAR20 LED | 8 | 4.7 | 37.6 | 29.6 |
| Up to 15 Watt Exterior PAR30 LED | 6 | 3.42 | 20.52 | 14.52 |
| Up to 21 Watt Exterior PAR30 LED | 15 | 3.42 | 51.3 | 36.3 |
| Up to 17 Watt Exterior PAR38 LED | 7 | 3.81 | 26.67 | 19.67 |
| Up to 25 Watt Exterior PAR38 LED | 17 | 3.81 | 64.77 | 47.77 |

Candelabra Lamps

This work paper contains the following Candelabra LED measures:

Table 17 Candelabra Measures and Wattages

| Measure* | Measure Case Wattage (W) | Source of Measure Case Wattage Value | Base Case Wattage (W) | Delta Watts (W) |
| --- | --- | --- | --- | --- |
| < 1 Watt Candelabra LED | 1 | Determined by SCE | 7.35 | 6.35 |
| 1 Watt to < 2 Watt Candelabra LED | 2 | Determined by SCE | 14.7 | 12.7 |
| 2 Watt to < 3 Watt Candelabra LED | 3 | Determined by SCE | 22.05 | 19.05 |
| 3 Watt to < 4 Watt Candelabra LED | 4 | Determined by SCE | 29.4 | 25.4 |
| >= 4 Watt Candelabra LED | 5 | Determined by SCE | 36.75 | 31.75 |

*Each of these measures has a Common Area and Dwelling Area variant, which share the same delta watts but are not shown here.

ED’s disposition [C] recommends multiplying the measure case wattage by 7.35 to calculate for the base case as shown in Table 17.

## 2.1 Energy Savings Estimation Methodologies

The following is a sample energy savings calculation for MR16 LED up to 10 Watts in an Agricultural building type in Climate Zone 6.

EnergySavingskWhUnit×Year=19.44×2708×1.057371,000WatthourskWh

EnergySavingskWhUnit×Year=55.66

## 2.2 Demand Reduction Estimation Methodologies

The following is a sample demand reduction calculation for MR16 LED up to 10 Watts in an Agricultural building type in Climate Zone 6.

DemandReductionkWUnit=19.44×0.665278×1.102721,000WatthourskWh

DemandReductionkWUnit=0.01426

Savings for other measures in different building types and climate zones can be found in the attachment [].

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the DEER:Indoor_CFL_Ltg load shape.  See Table 18 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 18 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Agricultural | NON_RES | DEER:Indoor_CFL_Ltg |
| Assembly | NON_RES | DEER:Indoor_CFL_Ltg |
| Education - Primary School | NON_RES | DEER:Indoor_CFL_Ltg |
| Education - Secondary School | NON_RES | DEER:Indoor_CFL_Ltg |
| Education - Relocatable Classroom | NON_RES | DEER:Indoor_CFL_Ltg |
| Education - Community College | NON_RES | DEER:Indoor_CFL_Ltg |
| Education - University | NON_RES | DEER:Indoor_CFL_Ltg |
| Grocery | NON_RES | DEER:Indoor_CFL_Ltg |
| Food Store | NON_RES | DEER:Indoor_CFL_Ltg |
| Health/Medical - Hospital | NON_RES | DEER:Indoor_CFL_Ltg |
| Health/Medical - Nursing Home | NON_RES | DEER:Indoor_CFL_Ltg |
| Health/Medical - Clinic | NON_RES | DEER:Indoor_CFL_Ltg |
| Lodging - Hotel | NON_RES | DEER:Indoor_CFL_Ltg |
| Lodging - Guest Rooms | NON_RES | DEER:Indoor_CFL_Ltg |
| Lodging - Motel | NON_RES | DEER:Indoor_CFL_Ltg |
| Manufacturing - Bio/Tech | NON_RES | DEER:Indoor_CFL_Ltg |
| Manufacturing - Light Industrial | NON_RES | DEER:Indoor_CFL_Ltg |
| Industrial | NON_RES | DEER:Indoor_CFL_Ltg |
| Misc - Commercial | NON_RES | DEER:Indoor_CFL_Ltg |
| Office - Large | NON_RES | DEER:Indoor_CFL_Ltg |
| Office - Small | NON_RES | DEER:Indoor_CFL_Ltg |
| Restaurant - Fast-Food | NON_RES | DEER:Indoor_CFL_Ltg |
| Restaurant - Sit-Down | NON_RES | DEER:Indoor_CFL_Ltg |
| Retail - Multistory Large | NON_RES | DEER:Indoor_CFL_Ltg |
| Retail - Single-Story Large | NON_RES | DEER:Indoor_CFL_Ltg |
| Retail - Small | NON_RES | DEER:Indoor_CFL_Ltg |
| Storage - Conditioned | NON_RES | DEER:Indoor_CFL_Ltg |
| Storage - Unconditioned | NON_RES | DEER:Indoor_CFL_Ltg |
| Transportation - Communication - Utilities | NON_RES | DEER:Indoor_CFL_Ltg |
| Warehouse - Refrigerated | NON_RES | DEER:Indoor_CFL_Ltg |
| Residential Single Family | RES | DEER:Indoor_CFL_Ltg |
| Residential Multi-family | RES | DEER:Indoor_CFL_Ltg |
| Residential Mobile Home - Double-Wide | RES | DEER:Indoor_CFL_Ltg |

# Section 4. Base Case & Measure Costs

Direct Install measures use program tracking systems for measure costs. Costs with climate zone multiplier can be found in the attachment [F].

For the Financial Support – Giveaway delivery method, measures are reported with program contractor costs and may vary by contractor. It is the contractor costs that are used for reporting and entered into the cost effectiveness calculator. Please see program specific files to get the actual costs.

## 4.1 Base Case Cost

Base case costs are taken from the statewide costs [] developed in response to the ED LED Disposition. The labor cost is $5.89 per lamp from DEER 2008 for installing a screw-in CFL lamp.

This work paper contains measures covering either a wattage range (e.g. “< 15 Watt PAR30 LED”) as well as measures covering a 1-Watt increment (e.g. “15 Watt to < 21 Watt PAR30 LED”). For the A, MR, and PAR in 1-Watt increment measures, no additional cost analysis was performed, so their costs are taken from the wattage range measures that they fall into.

Table 19 Base Cost

| Measure Name | Base Equipment Cost | Labor Cost | Total Cost |
| --- | --- | --- | --- |
| Up to 10 Watt A-Lamp LED | $3.32 | $5.89 | $9.21 |
| Up to 30 Watt A-Lamp LED | $4.61 | $5.89 | $10.50 |
| Up to 6 Watt MR16 LED | $6.78 | $5.89 | $12.67 |
| Up to 10 Watt MR16 LED | $6.59 | $5.89 | $12.48 |
| Up to 8 Watt PAR20 LED | $9.53 | $5.89 | $15.42 |
| Up to 12 Watt PAR20 LED | $9.53 | $5.89 | $15.42 |
| Up to 15 Watt PAR30 LED | $9.98 | $5.89 | $15.87 |
| Up to 21 Watt PAR30 LED | $10.24 | $5.89 | $16.13 |
| Up to 17 Watt PAR38 LED | $9.80 | $5.89 | $15.69 |
| Up to 25 Watt PAR38 LED | $9.60 | $5.89 | $15.49 |
| All Candelabra | $2.77 | $5.89 | $8.66 |
| 8 Watt Giveaway LED | $3.32 | $5.89 | $9.21 |

## 4.2 Measure Case Cost

Measure costs are also taken from the statewide costs [G] as shown in Table 20.

Table 20 Measure Cost

| Measure Name | Measure Equipment Cost | Labor Cost | Total Cost |
| --- | --- | --- | --- |
| Up to 10 Watt A-Lamp LED | $19.97 | $5.89 | $25.86 |
| Up to 30 Watt A-Lamp LED | $25.47 | $5.89 | $31.36 |
| Up to 6 Watt MR16 LED | $21.85 | $5.89 | $27.74 |
| Up to 10 Watt MR16 LED | $27.90 | $5.89 | $33.79 |
| Up to 8 Watt PAR20 LED | $33.97 | $5.89 | $39.86 |
| Up to 12 Watt PAR20 LED | $33.97 | $5.89 | $39.86 |
| Up to 15 Watt PAR30 LED | $45.23 | $5.89 | $51.12 |
| Up to 21 Watt PAR30 LED | $37.14 | $5.89 | $43.03 |
| Up to 17 Watt PAR38 LED | $44.97 | $5.89 | $50.86 |
| Up to 25 Watt PAR38 LED | $45.98 | $5.89 | $51.87 |
| All Candelabra | $16.76 | $5.89 | $22.65 |
| 8 Watt Giveaway LED | $19.97 | $5.89 | $25.86 |

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For ROB, GMC is represented by the equation below and shown in Table 21.

GMC 	= Measure Equipment Cost – Base Case Equipment Cost

Table 21 Gross Measure Cost

| Measure Name | Measure Equipment Cost | Base Equipment Cost | Gross Measure Cost |
| --- | --- | --- | --- |
| Up to 10 Watt A-Lamp LED | $19.97 | $3.32 | $16.65 |
| Up to 30 Watt A-Lamp LED | $25.47 | $4.61 | $20.86 |
| Up to 6 Watt MR16 LED | $21.85 | $6.78 | $15.07 |
| Up to 10 Watt MR16 LED | $27.90 | $6.59 | $21.31 |
| Up to 8 Watt PAR20 LED | $33.97 | $9.53 | $24.44 |
| Up to 12 Watt PAR20 LED | $33.97 | $9.53 | $24.44 |
| Up to 15 Watt PAR30 LED | $45.23 | $9.98 | $35.25 |
| Up to 21 Watt PAR30 LED | $37.14 | $10.24 | $26.90 |
| Up to 17 Watt PAR38 LED | $44.97 | $9.80 | $35.17 |
| Up to 25 Watt PAR38 LED | $45.98 | $9.60 | $36.38 |
| All Candelabra | $16.76 | $2.77 | $13.99 |
| 8 Watt Giveaway LED | $19.97 | $3.32 | $16.65 |

### 4.3.2 Incremental Measure Cost

Incremental Measure Cost is the same as Gross Measure Cost as shown in Section 4.3.1.

# Attachments

1.  2. 3.  4.5.

# References

[31]

[351]

[355]

[417]

[418]

[419]

[422]

[436]

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |

http://www.energystar.gov/certified-products/detail/light_bulbs

ENERGY STAR® Program Requirements for Integral LED Lamps Partner Commitments, DOE/Energy Star Program

Attachment 2 – 2013-2014_LightingRetrofit_Disposition-30May2014.xlsx

Attachment 3 – LG106 Calcs.xlsx

Attachment 4 – DOE SSL Product List and Analysis.xls

Attachment 1 – Calculation Template 2015 v2.xlsm

Attachment 5 – IMC Analysis 052912-mam.xls