Work Paper SCE13LG108

Revision 2

Southern California Edison Company

Exterior LED Wall Pack Fixtures

# At-a-Glance Summary

| Applicable Measure Codes: | LT-79024, LT-29069, LT-38903, LT-17893, LT-37685 |
| --- | --- |
| Measure Description: | LED exterior wall packs |
| Base Case Description: | Metal halide, compact fluorescent, or high pressure sodium exterior wall packs |
| Energy Impact Common Units: | Fixture |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | Refer to Table 7. |
| Measure Application Type: | Retrofit (RET), Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | Downstream: 0.6 (Non-Res) and 0.55 (Res), Direct Install: 0.85 |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13LG108.0 |  | 03/30/2012 | Ajay Wadhera/SCE | Updated Work paper to new template 2013 v0.1 from original WPSCNRLG0108.0 for the 2013-2014 bridge period |
|  |  |  | Brian V. O’Keefe/SCE | -Added ROB for downstream deemed, included cost section update -Updated the operating hours for the residential measures to reflector exterior res hours. |
| SCE13LG108.1 | No | 08/01/2013 | Jason Wang/SCE | - Updated measure ranges per 3/1/13 ED Lighting Retrofit Disposition titled “2013-2014_LightingRetrofit_Disposition-1March2013.docx.” - Added Title 24 2013 code, which added a lighting control requirement. |
| SCE13LG108.2 | No | 4/17/2014 | Jason Wang/SCE | -Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. -Adjusted wattages based on May 30, 2014 ED disposition -Updated costs based on ED disposition |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the replacement of metal halide (MH), compact fluorescent (CFL), and high pressure sodium (HPS) exterior wall packs with LED exterior wall packs. The measures are broken out into the wattage ranges as shown in Table 1.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| LT-79024 | 20 to 40 Watt Wall Pack LED replacing up to 175 Watt Metal Halide |
| LT-29069 | 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt Metal Halide |
| LT-38903 | 20 to 40 Watt Wall Pack LED replacing up to 175 Watt HPS |
| LT-17893 | 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt HPS |
| LT-37685 | 20 to 40 Watt Wall Pack LED replacing up to 126 Watt CFL |

## Products must be listed on Design Lights Consortium’s (DLC) qualified product list (QPL).

## 1.2 Technical Description

Wall packs are exterior lighting fixtures that are commonly used in walkways, parking areas, building facades, garages, and other outdoor spaces. They have photocell control and operate from dusk to dawn.

## 1.3 Measure Application Type

Note: See Appendix A for a comparison of the application types used by and incorporated into SCE systems versus the application types available in the newest revision of DEER 2014. Appendix A will serve as a translation between the outputs of this workpaper and application types used by READi.

The delivery methods are:

- Financial Support – Direct Install

- Financial Support – Down-Stream Incentive

The install types are:

- Retrofit (RET)

- Replace on Burnout (ROB)

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

The measures in this work paper are not included in DEER 2014, although DEER does contain similar outdoor lighting retrofit measures.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | N/A |
| Scaled DEER Measure | N/A |
| DEER Building Prototypes Used | N/A |
| Deviation from DEER | N/A |
| DEER Version | DEER 2014 |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID* | NTG* |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | Any | 0.55 |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | Any | 0.6 |
| Ind-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ind | Any | Any | 0.6 |
| Agric-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ag | Any | Any | 0.6 |
| Res-Default-HTR-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |
| Com-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Com | Any | DirInstall | 0.85 |
| Ind-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ind | Any | DirInstall | 0.85 |
| Agricult-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ag | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis. This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the default NTG values, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID* | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | Lighting |
| Measure Case UseSubCats | Outdoor General Lighting |
| Measure Case TechGroups | Lighting - Fixtures |
| Measure Case TechTypes | LED Fixture |
| Base Case TechGroups | Lighting - Fixtures |
| Base Case TechTypes | HID Fixture, CFL Fixture |

### 1.4.2 Codes and Standards Analysis

Title 20 2014 [422]: California Energy Commission (CEC) Title 20 defines that a “LED luminaire” is a complete lighting unit consisting of an LED light source, meaning one or more LED lamps or LED light engines, together with parts to distribute light, to position and protect the light source, and to connect the light source to the electrical power. Title 20 does not provide efficiency requirements for the LED fixtures in this work paper.

Title 24 2013 [355]: Title 24 Section 130.2(c)5D states that outdoor wall mounted luminaires having a bilaterally symmetric distribution as described in the IES Handbook (typically referred to as “wall packs”) where the bottom of the lumnaire is mounted 24 feet or less above the ground shall comply with the applicable requirements in Section 130.2(c)3.

Section 130.2(c)3 states that:

All installed outdoor lighting, where the bottom of the luminaire is mounted 24 feet or less above the ground, shall be controlled with automatic lighting controls that meet all of the following requirements:

- Shall be motion sensors or other lighting control systems that automatically controls lighting in accordance with item B in response to the area being vacated of occupants.; and

- Shall be capable of automatically reducing the lighting power of each luminaire by at least 40 percent but not exceeding 80 percent, or provide continuous dimming through a range that includes 40 percent through 80 percent, and

- Shall employ auto-ON functionality when the area becomes occupied, and

- No more than 1,500 watts of lighting power shall be controlled together.

EXCEPTION 1 to Section 130.2(c)3: Lighting for Outdoor Sales Frontage, Outdoor Sales Lots, and Outdoor Sales Canopies complying with Section 130.2(c)4.

EXCEPTION 2 to Section 130.2(c)3: Lighting for Building Facades, Ornamental Hardscape and Outdoor Dining complying with Section 130.2(c)5.

EXCEPTION 3 to Section 130.2(c)3: Outdoor lighting, where luminaire rated wattage is determined in accordance with Section 130.0(c), and which meet one of the following conditions:

- Pole-mounted luminaires with a maximum rated wattage of 75 watts each; or

- Non-pole mounted luminaires each with a maximum rated wattage of 30 watts each; or

- Linear lighting with a maximum wattage of 4 watts per linear foot of luminaire.

EXCEPTION 4 to Section 130.2(c)3: Applications listed as Exceptions to Section 140.7(a) shall not be required to meet the requirements of Section 130.2(c)3.

Section 140.7 contains lighting power requirements that apply to all outdoor lighting.

Section 149 contains requirements related to additions, alterations, and repairs to existing buildings that will be nonresidential, high-rise residential, and hotel/motel occupancies and to existing outdoor lighting for these occupancies and to internally and externally illuminated signs.

Lighting controls will be required for this measure unless the application meets the exception criteria in Title 24 Section 130.2(c)3 or Section 140.7(a). Table 6 shows the code analysis summary for these measure types.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Sections 130.2(c), 140.7, 149 | July 1, 2014 |

### 1.4.3 Non-DEER Study Review

No Non-DEER studies were reviewed for this work paper.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 7 below identifies the value/methodology used for the measures in this work paper. The maximum EUL that can be claimed is the CFL fixture life, which is 12 years for nonresidential fixtures and 16 years for residential fixtures.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Description | Sector | Enduse | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| OLtg-Com-LED-50000hr | LED Fixture - Outdoor- Commercial | Com | Lighting | 12 years. Rated Life of Fixture (50,000 hrs) / Annual Usage (4,100 hrs) = 12.2 years. Maximum of 12 years. | For CFLs, the Base Case EUL is 12 (Non-res) or 16 (Res) years, so the RUL is 4 (Non-res) or 5.3 (Res) years. For MH and HPS, Base Case EUL is 15 years (minimum of 15 years and 70,000/4,100), so the RUL is 5 years. |
| OLtg-Res-LED-50000hr | LED Fixture - Outdoor- Residential | Res | Lighting | 12.2 years. Rated Life of Fixture (50,000 hrs) / Annual Usage (4,100 hrs) = 12.2 years. Maximum of 16 years. |  |

# Section 2. Energy Savings & Demand Reduction Calculations

The measure, base, and code case wattages for this work paper are from the May 30 Energy Division disposition (Attachment 2) and shown in Table 12.

Table 8 Measure, Base, and Code Case Wattages

| DEER Measure ID* | Measure Name | Measure Case Wattage (W) | Base Case Wattage (W) | Code Case Wattage (W) |
| --- | --- | --- | --- | --- |
| C-Out-LEDFixt-WM-Ext-4(40w)-dWP32 | 20 to 40 Watt Wall Pack LED replacing up to 175 Metal Halide | 40 | 72 | 72 |
| C-Out-LEDFixt-WM-Ext(80w)-dWP215-dWC152 | 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt Metal Halide | 80 | 295 | 232 |
| C-Out-LEDFixt-WM-Ext-4(40w)-dWP6-2 | 20 to 40 Watt Wall Pack LED replacing up to 175 Watt HPS | 40 | 46 | 46 |
| C-Out-LEDFixt-WM-Ext(80w)-dWP215 | 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt HPS | 80 | 295 | 295 |
| C-Out-LEDFixt-WM-Ext-4(40w)-dWP6-1 | 20 to 40 Watt Wall Pack LED replacing up to 126 Watt CFL | 40 | 46 | 46 |

*All of these Measure IDs also have a residential version, e.g. “R-Out-LEDFixt-WM-Ext-4(40w)-dWP32.”

Example:  20 to 40 Watt LED Wall Pack replacing MH up to 175 Watts, Any building type and climate zone

Annual operating hours is based on a dusk-to-dawn operation of 4,100 hours.

Energy Savings kWhyr= 72-40x 4,1001000 W/kW

Energy Savings kWhyr= 131.2 kWh/year

No demand reduction is reported because exterior fixtures do not operate during DEER peak periods.

All savings are in Attachment 1.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Outdoor Lt load shape.  See Table 13 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 9 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Agricultural | Misc._Commercial | Outdoor Lt |
| Assembly | Misc._Commercial | Outdoor Lt |
| Education - Primary School | Misc._Commercial | Outdoor Lt |
| Education - Secondary School | Misc._Commercial | Outdoor Lt |
| Education - Relocatable Classroom | Misc._Commercial | Outdoor Lt |
| Education - Community College | Misc._Commercial | Outdoor Lt |
| Education - University | Misc._Commercial | Outdoor Lt |
| Grocery | Misc._Commercial | Outdoor Lt |
| Food Store | Misc._Commercial | Outdoor Lt |
| Health/Medical - Hospital | Misc._Commercial | Outdoor Lt |
| Health/Medical - Nursing Home | Misc._Commercial | Outdoor Lt |
| Health/Medical - Clinic | Misc._Commercial | Outdoor Lt |
| Lodging - Hotel | Misc._Commercial | Outdoor Lt |
| Lodging - Guest Rooms | Misc._Commercial | Outdoor Lt |
| Lodging - Motel | Misc._Commercial | Outdoor Lt |
| Manufacturing - Bio/Tech | Misc._Commercial | Outdoor Lt |
| Manufacturing - Light Industrial | Misc._Commercial | Outdoor Lt |
| Industrial | Misc._Commercial | Outdoor Lt |
| Misc - Commercial | Misc._Commercial | Outdoor Lt |
| Office - Large | Misc._Commercial | Outdoor Lt |
| Office - Small | Misc._Commercial | Outdoor Lt |
| Restaurant - Fast-Food | Misc._Commercial | Outdoor Lt |
| Restaurant - Sit-Down | Misc._Commercial | Outdoor Lt |
| Retail - Multistory Large | Misc._Commercial | Outdoor Lt |
| Retail - Single-Story Large | Misc._Commercial | Outdoor Lt |
| Retail - Small | Misc._Commercial | Outdoor Lt |
| Storage - Conditioned | Misc._Commercial | Outdoor Lt |
| Storage - Unconditioned | Misc._Commercial | Outdoor Lt |
| Transportation - Communication - Utilities | Misc._Commercial | Outdoor Lt |
| Warehouse - Refrigerated | Misc._Commercial | Outdoor Lt |
| Residential Single Family | Misc._Commercial | Outdoor Lt |
| Residential Multi-family | Misc._Commercial | Outdoor Lt |
| Residential Mobile Home - Double-Wide | Misc._Commercial | Outdoor Lt |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

Base case costs are from DEER 2008 and averages of retailer prices; see Table 14.

## 4.2 Measure Case Cost

The costs of the LED Wall Packs were found from various online sources. The labor cost is taken from DEER 2008. The DEER labor cost is for installing a metal halide lamp, not specifically for a wall pack. It is assumed they have the same cost.

Table 10 Base and Measure Costs

| Measure Name | Measure Cost | Base Cost | Labor Cost |
| --- | --- | --- | --- |
| 20 to 40 Watt Wall Pack LED replacing up to 175 Metal Halide | $496.14 | $131.05 | $36.09 |
| 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt Metal Halide | $702.21 | $139.67 | $72.17 |
| 20 to 40 Watt Wall Pack LED replacing up to 175 Watt HPS | $496.14 | $174.99 | $36.09 |
| 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt HPS | $702.21 | $347.99 | $72.17 |
| 20 to 40 Watt Wall Pack LED replacing up to 126 Watt CFL | $496.14 | $205.08 | $36.09 |

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For ROB, gross measure cost (GMC) is defined as the difference of measure equipment cost and base equipment cost to install the energy efficient measure:

GMC 	= (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

For RET 1st baseline, the GMC is the full measure cost:

GMC = Measure Equipment Cost + Measure Labor Cost

For RET 2st baseline, the GMC is:

GMC 	= (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

Table 11 GMC and IMC

| Measure Name | RET 1st Baseline GMC | RET 2nd Baseline and ROB GMC ROB and RET IMC |
| --- | --- | --- |
| 20 to 40 Watt Wall Pack LED replacing up to 175 Metal Halide | $532.23 | $365.09 |
| 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt Metal Halide | $774.39 | $562.55 |
| 20 to 40 Watt Wall Pack LED replacing up to 175 Watt HPS | $532.23 | $321.15 |
| 41 to 80 Watt Wall Pack LED replacing 176 to 250 Watt HPS | $774.39 | $354.22 |
| 20 to 40 Watt Wall Pack LED replacing up to 126 Watt CFL | $532.23 | $291.06 |

### 4.3.2 Incremental Measure Cost

For ROB and RET, the Incremental Measure Cost (IMC) is:

IMC 	= (Measure Equipment Cost + Measure Labor Cost) –

(Base Case Equipment Cost + Base Case Labor Cost)

All cost calculations are in Attachment 3.

# Attachments

# References

| [31] | Load Shape Update Initiative - KEMA / JJ Hirsch and Assoc. / Itron Inc. - November 17, 2006 |
| --- | --- |
| [351] | Energy Efficiency Policy Manual-Version 5 |
| [355] | 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings (Title 24) |
| [422] | 2014 Appliance Efficiency Regulations (Title 20) |
| [436] | 2014 DEER EUL Table - Update |

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |