Work Paper SCE13LG107

Revision 1

Southern California Edison Company

Battery- and Self-Powered Wireless Occupancy Sensors – Ceiling or Wall Mounted

### Core Measure Summary Table

| General Measure Information |  |  |  |  |  |  |  | PT |  | 1st Baseline Period |  |  |  | 2nd Baseline Period |  |  |  | TOU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Measure RunID | Solution Code | CZ | Building Type | Load Shape | EUL | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | Gas Savings (Therms) | 1st Baseline Useful Life | kWh Saving per unit (kWh/unit) | kW Savings per unit (kW/unit) | Gas Savings (Therms) | 2nd Baseline Useful Life | % TOU |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 06 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 103.11 | 0.02 | -0.08 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 08 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 103.93 | 0.02 | -0.07 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 09 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 104.31 | 0.02 | -0.06 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 10 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 102.71 | 0.02 | -0.08 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 13 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 102.31 | 0.02 | -0.25 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 14 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 101.42 | 0.02 | -0.28 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 15 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 105.05 | 0.02 | -0.03 | 5.00 |  |  |  | 0.00 | 0.00 |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control |  | LT-81984 | 16 | Agricultural | Occupancy Sensor | 5.0 | Sensor | REA | No | 97.77 | 0.02 | -0.62 | 5.00 |  |  |  | 0.00 | 0.00 |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

### Costing and NTG Summary Table

| General Measure Information |  |  |  | PT |  | NTG |  |  | IR | 1st Baseline Period | 2nd Baseline Period | IMC | DIM |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Name | Solution Code | CZ | Unit Definition | Program Type (NEW, ROB, RET) | Applicable Code | NTG Non-Res. | NTG Res. | NTG Multi Family | Installation Rate | Gross Measure Cost per unit | Gross Measure Cost per unit | Incremental Measure Cost per unit | Delivery & Incentive Method |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 6 | Sensor | REA | No | 0.60 |  |  | 1.00 | $225.43 | $0.00 | $225.43 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 8 | Sensor | REA | No | 0.60 |  |  | 1.00 | $237.97 | $0.00 | $237.97 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 9 | Sensor | REA | No | 0.60 |  |  | 1.00 | $247.38 | $0.00 | $247.38 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 10 | Sensor | REA | No | 0.60 |  |  | 1.00 | $230.49 | $0.00 | $230.49 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 13 | Sensor | REA | No | 0.60 |  |  | 1.00 | $224.70 | $0.00 | $224.70 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 14 | Sensor | REA | No | 0.60 |  |  | 1.00 | $223.17 | $0.00 | $223.17 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 15 | Sensor | REA | No | 0.60 |  |  | 1.00 | $237.05 | $0.00 | $237.05 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 16 | Sensor | REA | No | 0.60 |  |  | 1.00 | $248.33 | $0.00 | $248.33 | Financial Support / Down-Stream Incentive - Deemed |
| Wall or Ceiling Mounted Battery Powered Wireless Lighting Sensor Control | LT-81984 | 6 | Sensor | REA | No | 0.60 |  |  | 1.00 | $225.43 | $0.00 | $225.43 | Financial Support / Down-Stream Incentive - Deemed |

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Document Revision History

| Revision # | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 4/04/2013 | David Pruitt/PL Energy | -Original work paper draft for 2013-2014 program cycle -Updated version of 2010-2012 work paper WPSCNRLG0107.1 - Updated vendor costs to reflect current prices stated on vendor websites (current as of 4/5/12). |
| 1 | 06/25/13 | Yun Han/ SCE | Updated: - Occupancy time off adjusted to ED’s 13-14 work paper disposition - EUL reference to DEER 2011 w/EUL ID - T24 code language updated for 2013 code change |

# Section 1. General Measure & Baseline Data

## 1.1  Measure & Delivery Description

This work paper details the energy and demand impacts of a battery-powered or a self-powered wireless wall- or ceiling-mounted occupancy sensor and associated device, such as a receiver to control the fixtures in a non-residential setting.  A lighting occupancy sensor is a device that automatically turns the lights on when a person enters a room and off when the space has been vacant for a specified period of time. Energy savings are achieved by reducing the amount of time the lights are on.

### 1.1a Measure Description

The Measure Case is one or more T8 lighting fixtures with occupancy sensor(s) that turn lights on/off based on room vacancy.

Measures controlling less than 500 Watts assume that the battery-powered or self-powered wireless occupancy sensors control three 32 Watt 2-lamp T8 (F42ILL) fixtures with electronic ballast. According to the Table of Standard Fixture Wattages, this set of fixtures draws 177 Watts. Measures not referencing any Wattage fall under the less than 500 Watts measure.

Measures controlling more than 500 Watts assume that the battery-powered or self-powered wireless sensors control ten 32 Watt 2-lamp T8 (F42ILL) fixtures with electronic ballasts. According to the Table of Standard Fixture Wattages, this set of fixtures draws 590 Watts.  For measures controlling more than 500 Watts, a sensor coverage chart must be used to identify the maximum radius of coverage and the ceiling height it will be installed in for correct operation.

The Base Case for these measures is the T8 lighting fixtures described above without occupancy sensor control (fixtures are manually controlled).

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| LT-81984 | Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control |
| LT-36254 | <500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control |
| LT-10867 | >=500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control |
| LT-20964 | Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control |
| LT-86543 | <500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control |
| LT-30078 | >=500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control |

### 1.1b Delivery and Incentive Mechanism

The delivery / incentive mechanisms methods are:

- Financial Support / Down-stream Incentive – Deemed

- Financial Support / Direct Install

The install type is Retrofit Add-on (REA).  This is a subtype of RET that is specifically for adding a piece of equipment to an existing system or piece of equipment to make the overall system or equipment more efficient.

### 1.1c Measure Requirements

Eligibility Requirements: To be eligible for these programs, a customer must install wireless detectors to control interior lighting fixtures. Sensors that are installed to comply with Title 24 code are not eligible for rebates. See Section 1.3 for more information.

Documentation Requirements: For the Down-Stream Incentive method, the customer must provide invoices.

## 1.2  DEER Differences Analysis

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | Yes |
| DEER Building Prototypes Used | Yes |
| Deviation from DEER | The measure for this WP is for battery-powered and self-powered wireless occupancy lighting sensors. This differs from the DEER 2005 Measure, which is for hard-wired sensors. |
| DEER Version | DEER 2011 v4.01 |
| DEER Run ID and Measure Name (Sample) | Occupancy Sensor Pack-200 SF D03-003 |

## 1.3  Code Analysis

Table 3 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | 2013 Non-Residential Compliance manual, Section 130.1 (c), Shut-Off Controls | January 1, 2014 |

This measure is affected by the California Energy Commission 2013 Building Energy Efficiency Standards Nonresidential Compliance Manual (Title 24). Section 130.1(c) requires that design and installation of all lighting systems in nonresidential buildings have automatic shut-off mechanisms for interior lighting. For example, lights may be controlled by an occupant sensing control, automatic time-switch control, or signal from other building system.

If an occupancy sensor is required by or used to comply with code, then it cannot be used to claim energy and demand savings. Therefore, this measure is only eligible in buildings built before 2014 in which the lighting fixtures are not being replaced.

## 1.4  Measure Effective Useful Life

DEER 2011 documentation provides EUL and RUL information to be used for the 13-14 program cycle. To obtain the EUL and RUL values the DEER 2011 documentation, Support Table_EUL.csv, was consulted. Table 4 identifies the value/methodology used for the measures in this work paper. The EUL ID for this measure is ILtg-OccSens. The DEER documentation “Summary of EUL-RUL Analysis for the April 2008 Update to DEER” provides the RUL value as a flat 1/3 of the EUL value.

Table 4 DEER11 EUL Value/Methodology

| Market | Enduse | Measure | EUL (Years) | RUL (Years) | EUL ID |
| --- | --- | --- | --- | --- | --- |
| Non-Residential | Indoor Lighting | Occupancy Sensors | 8 | 2.67 | ILtg-OccSens |

For measures that utilize either CR123 lithium or AA batteries as the source of power, the battery life of the wireless occupancy sensors is listed at 10 years, although this will vary by usage and application.  An LED indicator light, either on the sensor itself or on the switch, is used to inform users of when the battery is low. However, SCE’s current policy on wireless battery-powered devices is that the EUL will be the battery life in years divided by two or the DEER life, whichever is smaller.  Using the rated 10 year battery life, the EUL of the battery-powered wireless occupancy sensor is 5 years. Table 5 summarizes the EUL values for the battery powered measures versus the self-powered measures.

Table 5 EUL Values

| Market | Enduse | Measure | EUL (Years) |
| --- | --- | --- | --- |
| Non-Residential | Lighting | Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | 5 |
| Non-Residential | Lighting | <500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | 5 |
| Non-Residential | Lighting | >=500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | 5 |
| Non-Residential | Lighting | Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | 8 |
| Non-Residential | Lighting | <500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | 8 |
| Non-Residential | Lighting | >=500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | 8 |

## 1.5  Net-to-Gross Ratios for Different Program Strategies

The NTG value was obtained from “DEER2011_NTGR_2012-05-16.xls” on the DEER website (www.deeresources.com) as required by Version 4 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [132]. The relevant NTGR for this measure is shown in Table 6.

Table 6 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mOccSens | Occupancy Sensors | Com | Any | PreRebDown | 0.6 |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | All | 0.6 |

*Denotes that the column is taken from the DEER NTG Table.

The installation rate (IR) is identified in the calculation attachment. This value is obtained from a spreadsheet created by the DEER team titled “GrossSavingsAdjustments.xlsx”. The installation rate varies by end use, sector, technology, application, and delivery method.

## Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

## 1.6  Time-of-Use Adjustment Factor

As directed by the CPUC in decision 06-06-063 dated June 29, 2006, time-of-use (TOU) adjustment factors are to be applied for residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only.   Since this is not an A/C measure, the TOU adjustment factor is 0.  Additionally, if a measure is assigned a DEER08 load shape, i.e. the load shape starts with “DEER:” the TOU assigned to that measure should also be zero.

Table 7  TOU Summary Table

| Measure | % |
| --- | --- |
| Wireless Occupancy Sensor - Lighting | 0 |

# Section 2. Energy Savings & Demand Reduction Calculations

This work paper considers three measures with two types of control each involving the addition of wall- or ceiling-mounted occupancy sensors to interior lighting systems. The base case assumptions for these measures are as follows:

Table 8 Base Case Assumptions

| Measure Name | Controlled Fixtures | Controlled Wattage |
| --- | --- | --- |
| Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | (3) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 177 W |
| <500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | (3) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 177 W |
| >=500 watts Wall- or Ceiling-Mounted Battery-Powered Wireless Lighting Sensor Control | (10) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 590 W |
| Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | (3) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 177 W |
| <500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | (3) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 177 W |
| >=500 watts Wall- or Ceiling-Mounted Self-Powered Wireless Lighting Sensor Control | (10) 4’ 2-lamp T8 fixtures (F42ILL) with electronic ballasts | 590 W |

To calculate the energy savings for occupancy sensors, an estimated percent time off value is used; see Table 9.  For each building type, the space type can be DEER, Non-DEER, or ED-weighted. DEER space types are specified by a name (e.g. Classroom/Lecture or Corridor) and use values provided by the Energy Division’s 2013‒2014 Workpaper Disposition for Occupancy Sensor Lighting Controls [B]. ED-weighted space types also use values provided by the disposition. Non-DEER space types use an average from DEER building types.

Table 9 only shows one space type and its kWh reduction factor per building type. Full list of space types and reduction used by ED for a given building type can be found in the attachment [B].

Table 9 Occupancy Sensor Percent Time Off by Market Sector

| Building Type | Space Type | Occupancy Sensor Time Off |
| --- | --- | --- |
| Agricultural | Non-DEER | Average |
| Assembly | ED Weighted | 20% |
| Education - Primary School | Classroom/Lecture | 20% |
| Education - Secondary School | Classroom/Lecture | 20% |
| Education - Relocatable Classroom | Classroom/Lecture | 20% |
| Education - Community College | Classroom/Lecture | 20% |
| Education - University | Classroom/Lecture | 20% |
| Grocery | ED Weighted | 16% |
| Food Store | Non-DEER | Average |
| Health/Medical - Hospital | Office (General) | 16% |
| Health/Medical - Nursing Home | Corridor | 16% |
| Health/Medical - Clinic | Non-DEER | Average |
| Lodging - Hotel | Corridor | 16% |
| Lodging - Guest Rooms | Non-DEER | Average |
| Lodging - Motel | Corridor | 16% |
| Manufacturing - Bio/Tech | ED Weighted | 15% |
| Manufacturing - Light Industrial | ED Weighted | 15% |
| Industrial | Non-DEER | Average |
| Misc - Commercial | Non-DEER | Average |
| Office - Large | Conference Room | 16% |
| Office - Small | Conference Room | 16% |
| Restaurant - Fast-Food | ED Weighted | 15% |
| Restaurant - Sit-Down | ED Weighted | 15% |
| Retail - Multistory Large | ED Weighted | 15% |
| Retail - Single-Story Large | ED Weighted | 0% |
| Retail - Small | ED Weighted | 0% |
| Storage - Conditioned | ED Weighted | 16% |
| Storage - Unconditioned | ED Weighted | 16% |
| Warehouse - Refrigerated | ED Weighted | 15% |
| Transportation - Communication - Utilities | Non-DEER | Average |

To calculate the peak demand reduction for occupancy sensors, an estimated Fraction of Usage Reduction During “Weekday Open” period value [B] is used; see Table 10.

Table 10 DEER Fraction of Usage Reduction During “Weekday Open” Period

| Building Type | Demand Direct Impact (kW) - Lighting Peak Demand Reduction - Weighted Average |
| --- | --- |
| Assembly | 0.0773 |
| Grocery | 0.0203 |
| Manufacturing - Bio/Tech | 0.1141 |
| Manufacturing - Light Industrial | 0.1124 |
| Restaurant - Sit-Down | 0.1585 |
| Restaurant - Fast-Food | 0.1374 |
| Retail - 3-Story Large | 0.0074 |
| Retail - Single-Story Large | 0.0085 |
| Retail - Small | 0.0140 |
| Storage - Conditioned | 0.0578 |
| Storage - Unconditioned | 0.0578 |
| Storage - Refrigerated Warehouse | 0.1892 |

## Energy Savings Methodology for ED Weighted Building Type

The annual energy savings per occupancy sensor is the product of the controlled wattage, annual hours of use, energy interactive effects (EIE), and occupancy sensor percent time off (PTO). The calculation is shown in Equation 1.

Equation 1

The energy savings vary by solution code, building type, and climate zone because of different values for controlled wattage, operating hours, percent time off, and interactive effects. For example, Equation 2 shows the calculation for a sensor controlling less than 500 Watts in an Assembly building located in climate zone 6. The operating hours and interactive effects values were taken from DEER 08 v4.0 assumptions.

Equation 2

The calculation spreadsheet attached at the end of this document shows the calculation for all the permutations of solution code, building type, and climate zone [A]. DEER and ED Weighted space types use savings values given in the 13-14 ED Disposition [B]. Non-DEER space types use an average from DEER building types.

## Demand Reduction Methodology for ED Weighted Building Type

The demand reduction per occupancy sensor is the product of the controlled wattage, interactive effects (DIE), and lighting peak demand reduction factor.  The calculation is shown in Equation 3.

Equation 3

As with the energy savings, the demand reduction varies by solution code, building type, and climate zone because of different values for controlled wattage, interactive effects, and peak demand reduction. For example, Equation 4 shows the calculation for a sensor controlling less than 500 Watts in a Assembly building type located in climate zone 6.

Equation 4

The calculation spreadsheet attached at the end of this document shows the calculation for all the permutations of solution code, building type, and climate zone. DEER and ED Weighted space types use savings values given in the 13-14 ED Disposition [B]. Non-DEER space types use an average from DEER building types.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Occupancy Sensor load shape.  See Table 11 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 11 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Agricultural | Agricultural | Occupancy Sensor |
| Assembly | Misc._Commercial | Occupancy Sensor |
| Education - Primary School | K_thru_12_School | Occupancy Sensor |
| Education - Secondary School | K_thru_12_School | Occupancy Sensor |
| Education - Relocatable Classroom | K_thru_12_School | Occupancy Sensor |
| Education - Community College | K_thru_12_School | Occupancy Sensor |
| Education - University | K_thru_12_School | Occupancy Sensor |
| Grocery | Misc._Commercial | Occupancy Sensor |
| Food Store | Misc._Commercial | Occupancy Sensor |
| Health/Medical - Hospital | Misc._Commercial | Occupancy Sensor |
| Health/Medical - Nursing Home | Misc._Commercial | Occupancy Sensor |
| Health/Medical - Clinic | Misc._Commercial | Occupancy Sensor |
| Lodging - Hotel | Hotel_Motel | Occupancy Sensor |
| Lodging - Guest Rooms | Hotel_Motel | Occupancy Sensor |
| Lodging - Motel | Hotel_Motel | Occupancy Sensor |
| Manufacturing - Bio/Tech | Industrial | Occupancy Sensor |
| Manufacturing - Light Industrial | Industrial | Occupancy Sensor |
| Industrial | Industrial | Occupancy Sensor |
| Misc - Commercial | Misc._Commercial | Occupancy Sensor |
| Office - Large | Large_Office | Occupancy Sensor |
| Office - Small | Small_Office | Occupancy Sensor |
| Restaurant - Fast-Food | Misc._Commercial | Occupancy Sensor |
| Restaurant - Sit-Down | Misc._Commercial | Occupancy Sensor |
| Retail - Multistory Large | Large_Retail_Store | Occupancy Sensor |
| Retail - Single-Story Large | Large_Retail_Store | Occupancy Sensor |
| Retail - Small | Small_Retail_Store | Occupancy Sensor |
| Storage - Conditioned | Misc._Commercial | Occupancy Sensor |
| Storage - Unconditioned | Misc._Commercial | Occupancy Sensor |
| Transportation - Communication - Utilities | Trans_Comm_Util | Occupancy Sensor |
| Warehouse - Refrigerated | Misc._Commercial | Occupancy Sensor |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

For this measure category, the base case cost is assumed to be zero because a piece of equipment is being added to an existing system to make the overall system more efficient.

## 4.2 Gross Measure Cost

Retrofit add-on

For retrofit add-on measures, the gross measure cost is defined as the cost incurred to install the energy efficient measure. The gross cost includes both the equipment cost and all associated labor cost to install the measure.  For retrofit measures the gross measure cost is used for reporting in the cost effectiveness calculations.  In the current E3 calculator this value is inserted into the column titled “Gross Measure Cost ($/unit)”.

Gross Measure Cost

The material cost of wireless occupancy sensors and switches/dimmers as one package were taken from various online vendors and averaged [C].  The material cost of self-powered occupancy sensors and switches/dimmers as one package was taken from the actual manufacturer’s website. The labor was taken from the DEER 2008 cost spreadsheet [215] which listed the Retrofit Installation Labor Cost as shown in Table 12.

Table 12 Gross Measure Cost

| Measure | Measure Cost | Labor Cost | Gross Measure Cost |
| --- | --- | --- | --- |
| Battery-Powered Sensor with Switch | $204.75 | $44.12 | $248.87 |
| Self-Powered Sensor with Switch | $274.98 | $44.12 | $319.10 |

## 4.3 Incremental Measure Cost

The Incremental Measure Cost is the same as Gross Measure Cost shown in Table 12.

# Attachments

1. 2. 3.

# References

[31]

[65]

[132]

[213]

[215]

[220]

[A] Calculation Template v2.2.xlsm

[B] 2013-2014_LightingControl_Disposition-6Sep2013.docx

[C] Cost.xlsx