Work Paper SCE13LG117

Revision 0

Southern California Edison

LED T8 Replacement Lamps UL Type A

# At-a-Glance Summary

| Measure Codes | LT-11950 , LT-11966 |
| --- | --- |
| Measure Description | 4-foot LED T8 Replacement Lamp UL Type A |
| Base Case Description | 4-foot Linear Fluorescent T8 Lamps |
| Units | Per lamp |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | ILtg-Lfluor-Elec – varies by building type |
| Measure Installation Type | Retrofit or Early Retirement (RET/ER) |
| Net-to-Gross Ratio | All-Default<=2yrs: 0.70 |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 4/29/16 | Yun Han/SCE | - New work paper |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |
| 0 | CS | 5/23/16 | 6/6/16 |  |  |
|  |  |  |  |  | - [Attachment 5] |
| 0 | Cal TF | 3/6/15 | 3/6/15 |  | - Result is an ET study mentioned in Section 1.5.2 |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the replacement of 4-foot Linear Fluorescent T8 lamps with LED T8 Lamp UL Type A.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | LED T8 Lamp UL Type A 4 foot |
| Existing Condition | Linear Fluorescent T8 Lamp 4 foot |
| Code/Standard | F32T8 Linear Fluorescent Lamp |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | LT-11950 |  | 4 foot LED T8 Lamp UL Type A Replacing Linear Fluorescent T8 Lamp |
|  |  | LT-11966 |  | 4 foot LED T8 Lamp UL Type A Replacing Linear Fluorescent T8 Lamp (Common Area) |

Eligibility Requirements

The measures in this work paper are eligible in all Commercial building types and Residential Multifamily and Double-Wide Mobile Home building types including Common Areas in all Climate Zones.

To qualify for incentives, the LED tube must be 4-foot and designated as UL Type A. The lamp must be listed under the Primary Use Category “Replacement Lamps (“plug and play”) (UL Type A)” on the DLC’s Qualified Products List (QPL) and meet additional criteria outlined below. The LED T8 Lamp specification sheet must also list all of the compatible ballast model numbers to ensure proper operation of the measure.

The products on the QPL will be filtered and must meet the specs as listed below. DLC Premium is not available for a lamp category.

SCE Program Requirement

| Performance Metric | DLC Requirement | DLC Tolerance | SCE Program Requirement (no tolerance) |
| --- | --- | --- | --- |
| Luminaire Efficacy | ≥100 LPW | -3% | ≥100 LPW |
| CRI | ≥80 | -2 points | ≥80 |
| CCT | ≤ 5,000K | N/A | ≤ 5,000K |
| Power Factor | ≥0.9 | -3% | ≥0.9 |
| Total Harmonic Distortion | ≤20% | +5% | ≤20% |
| Lumen Maintenance | L70>50,000 | N/A | L70>50,000 |
| Minimum Warranty | 5 years | N/A | 5 years |

Commercial Direct Install Program contractors have extensive knowledge of the lighting products they use for the DI Program.  Direct Install contractors will confirm LED T8 lamps installed are compatible, per manufacturer’s specifications, with the existing ballasts.  Documentation can be provided regarding the lamp/ballast compatibility for the various components used and encountered in their Direct Install. The sampling rate for pre-inspection is 6% and post-inspection between 10-20%.

Commercial Downstream Deemed Program would require applicants to submit manufacturer’s specification sheets detailing compatible ballasts and circling the one in their location. LED T8 tubes without this information available will not be eligible for the program. Ballasts will then be checked during inspections aligned with current inspection policy.

Midstream Program will verify the LED T8 Lamp spec. sheet by working with lighting distributors who provide incentives on qualified lighting products.  Distributors have extensive knowledge of their lighting inventory and will provide incentives on products that meet SCE’s requirements.  LED T8 Lamps will be pre-approved for use in the Midstream program to ensure that only LED T8 lamps with specification sheets that list the ballast model tested are eligible for incentives.  Distributors will provide the necessary documentation to SCE to verify the product is eligible for incentives.  Distributors will also let their customers know that they carry products that list compatible ballasts and should be verified before making the purchase.

The SCE Multifamily Energy Efficiency Rebate (MFEER) Program offers rebates on a wide variety of energy-saving products and services to motivate the multifamily property owners/managers to install energy efficient products in both common and dwelling areas of multifamily complexes.  The MFEER program addresses the ongoing concern with “split incentives”, where the residents are not the owners of the property, so they lack incentive to improve their energy usage. Similarly, the property owners do not live on-site and pay higher utility expenses due to inefficient appliances, thus lack any incentive to upgrade. The MFEER is designed to drive this customer segment toward participation by offering property owners a variety of energy efficiency measures and services.

The MFEER program also offers select energy-efficient products and services at “no-cost” to customers implemented via direct install.  Direct install measures are implemented by authorized-program contractors who perform program outreach and provide project management which includes energy audits, customer enrollment, product procurement, installation and quality assurance.

The MFEER program quality control ensures product eligibility by verifying qualified products lists and product specifications of the energy efficient product installed.  Pre-inspection isn’t performed, but data is collected. All projects that receive over $20,000 in incentives require a 100% post-inspection while all others will require 10% post-inspection. SCE requires a detailed Product Location Form (PLF) for each project submitted for rebate or incentive.  The PLF is an Excel spreadsheet with a tab for measures installed.  Consistent with program policies and procedures, field inspections are also conducted to verify installations and accuracy of the information provided in submitted incentive applications.

To ensure proper operation of the measure technology, customers will be required to submit the product specification sheet listing all of the compatible ballast model numbers indicating which ballast model is currently installed at their location.

## 1.2 Technical Description

LED T8 lamp Design Lights Consortium (DLC) defines the UL Type A as:

Four-foot or two-foot LED "tubes" designed to replace four-foot or two-foot fluorescent lamps, respectively. Products in this category employ lamp holders to connect to the fixture being retrofitted and are designed to be "plug and play" replacements for fluorescent lamps. That is, products in this category can operate off an existing fluorescent ballast, and do not require mechanical or electrical changes to the fixture. Note that due to testing considerations, at this time only products that can operate off electronic instant start ballasts are eligible. Replacement lamps designed to operate off existing magnetic ballasts, or off other types of electronic ballasts, are not eligible.

UL Type A Configuration

## 1.3 Installation Types and Delivery Mechanisms

The Installation Types are:

- Early Retirement (ER)

The delivery methods are:

- Financial Support / Direct Install

- Financial Support / Down-Stream Incentive – Deemed

- Midstream Programs / Mid-Stream Incentive

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | No |
| DEER Version | Non-DEER |
| Reason for Deviation from DEER | DEER does not contain this type of measure. |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG value for the measures are in the table below. To address potential concerns related to both quality and persistence, two Emerging Technology studies were conducted for the measure in this work paper.   These two studies provided the basis/assurance upon which this wider offer was developed.

The timeline below illustrates the work that SCE’s ET program has taken on for this measure and how it has supported bringing this technology into the mass market EE portfolio.

The first study initiated in October of 2012 was a Recessed LED Luminaire project (ET10SCE1190) that included LED Tubes in the scope of work. This study concluded that LED Tubes’ light output at the time was only comparable to the lowest lumen linear fluorescent 2x4 fixtures and wasn’t ready for the market. Concerns regarding tubes installed in various fixture styles such as non-planar, basket, and direct/indirect were also raised, therefore, not recommended at the time.

The second study proposal was initiated in May of 2014 and approved to start in June of 2014 (ET14SCE1040) which assessed the performance of LED T8 lamps installed with an existing linear fluorescent ballast.   Measurements included lumen degradation, safety, ballast temperature, and power quality as referenced in Section 1.5.1 in a laboratory setting. The lab test was not intended to provide the equivalent wattage of the baseline technology.   Second phase of the lumen degradation testing is on-going and scheduled to be completed by September 2016. Details of the short term testing can be found in Section 1.5.1.

The Statewide IOUs engaged the Commission Staff in October of 2014, several months after initiating the lab study for guidance on LED Tube offering. Based on the comments, SCE launched a third study as a scaled field placement (ET15SCE8040) which was initiated in May of 2015 to address concerns regarding persistence, ballast life, lamp quality, and customer satisfaction as referenced in Section 1.5.2 for a field trial of the lamps. This trial also collected illuminance, ballast info and pre-post wattages.  This study is ongoing as it will address customer satisfaction and ballast inspection after 4,380 hours or one year after installation.

Based on feedback, the ET NTG will not be used.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | Any | Any | Any | 0.70 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

This work paper replaces the linear fluorescent lamp with an LED lamp while using the existing linear fluorescent ballast. Based on guidance from the Commission Staff, the EUL is the RUL of the host equipment. Although field data gathered suggests 7 years ballast RUL, this work paper will use 70,000 hours/3 to calculate the EUL.

CS also recommended that LtgFixture-Default is used for Res building types since ILtg-Lfluor-Elec is limited to commercial installations.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| ILtg-Lfluor-Elec | Linear Fluorescent with Electronic Ballast | Any | Lighting | (70,000/HOU)/3 | N/A |
| LtgFixture-Default | CS recommended for Res | Res | Lighting | (70,000/HOU)/3 | N/A |

### 1.4.2 Codes and Standards Analysis

Title 24 2013 [355], Section 141.0(b)2I states:

Lighting System Alterations shall meet the applicable requirements in TABLE 141.0-E and the following:

- Lighting System Alterations include alterations where an existing lighting system is modified, luminaires are replaced, or luminaires are disconnected from the circuit, removed and reinstalled, whether in the same location or installed elsewhere.

EXCEPTION 1 to Section 141.0(b)2Iii: Alterations that qualify as a Luminaire Modification-in-

Place.

EXCEPTION 2 to Section 141.0(b)2Iii: Portable luminaires, luminaires affixed to moveable partitions, and lighting excluded in accordance to Section 140.6(a)3.

Luminaire Modifications-in-Place shall meet the applicable requirements in TABLE 141.0-F and the following:

- To qualify as a Luminaire Modification-in-Place, luminaires shall only be modified by one or more of the following methods:

  - Replacing lamps and ballasts with like type or quantity in a manner that preserves the original luminaire listing.

  - Changing the number or type of light source in a luminaire including: socket renewal, removal or relocation of sockets or lampholders, and/or related wiring internal to the luminaire including the addition of safety disconnecting devices.

  - Changing the optical system of a luminaire in part or in whole.

  - Replacement of whole luminaires one for one in which the only electrical modification involves disconnecting the existing luminaire and reconnecting the replacement luminaire.

- Luminaire Modifications-In-Place shall include only alterations to lighting system meeting the following conditions:

  - Luminaire Modifications-in-Place shall not be part of or the result of any general remodeling or renovation of the enclosed space in which they are located.

  - Luminaire Modifications-in-Place shall not cause, be the result of, or involve any changes to the panelboard or branch circuit wiring, including line voltage switches, relays, contactors, dimmers and other control devices, providing power to the lighting system.

EXCEPTION to Section 141.0(b)2Iiii2. Circuit modifications strictly limited to the addition of occupancy or vacancy sensors and class two lighting controls are permitted for Luminaire

Modifications-in-Place

Title 20 2012 [493] includes regulations to fluorescent lamp ballasts, replacement fluorescent lamp ballasts, and lamps.

2012 Federal Standards for General Service Fluorescent Lamps issued by Department of Energy effective July 14, 2012 contains Energy Conservation Standards that applies to various linear fluorescent lamp types [].

This measure is a lamp only replacement and does not trigger code.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Section 141.0(b)2Iii Lighting System Alterations, 141.0(b)2Iii Luminaire Modifications-in-Place | July 1, 2014 |
| Title 20 (2015) | 2015 Appliance Efficiency Regulations | July 1, 2015 |
| NEMA (2012) | Federal standards for general service fluorescent lamps issued by DOE | July 14, 2012 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

Two Department of Energy CALiPER studies related to LED tubes application and cost effectiveness are attached [6, 7].  These studies provide context related to the quickly evolving improvement in LED lamps as well as the analysis related to applications where they are most cost effective.

The following two Emerging Technology studies outline the basis for savings and quality of installation considered for this measure.

### 1.5.1 ET14SCE1040 - LED Tube Retrofit Lab Assessment [497, Attachment 3]

- Emerging Technologies Assessment, Alvaro Mendoza, October 2015 (Note: Ongoing long term lumen depreciation testing with cycling)

- Late 2014 through 2015, Linear LED Tube replacement lamps (Ballast Compatible, Internal Driver, External Driver)

- Photometric and Electrical Measurements

- Photometric and Electrical performance

- Multiple lamp manufacturers tested

Based on the long term testing, no major lumen degradation has been observed and no negative effects were observed for the fluorescent ballasts after about 3,500 hours of cycled testing. Measured temperatures of the lamps and ballast have been stable since the beginning of the test.

Temperature measurements taken inside four different open fixtures in various lamp configurations showed that LEDs have considerably lower temperature than the linear fluorescent lamps. LED lamps were below 100°F while linear fluorescent lamps were greater than 125°F. LED T8 lamps also showed better performance across the entire dimming range than linear fluorescent lamps in terms of efficacy and visible flicker. The figure below shows the internal fixture ambient temperature of the LED and Linear Fluorescent lamps.

Internal Fixture Ambient Temperature

The Figure below shows the current Total Harmonic Distortion (THDi) caused by each of the lamps on a 2-lamp setup. Ballast compatible lamps performed similar to linear fluorescent lamps and showed no negative signs.

THDi of 2-Lamp Tests

The Figure below shows the Ballast Luminous Efficacy (BLE) of the LED T8 lamps tested. After eight months of continuous on-off fixture cycling with 3500 hours of on-time operation, the Ballast Luminous Efficiency (BLE) measurements, which measure the ratio of electrical output to electrical input as defined by DOE test procedures, indicate that the fluorescent ballast have not been affected by the operation of replacement LED tubes. The BLE values obtained from lab testing with LED T8 lamps are consistent with typical BLE values observed on the fluorescent ballasts when operating with T8 fluorescent lamps (above 80%). This chart demonstrates that there is no indication that replacement LED tubes degrade the performance of compatible fluorescent ballasts.

Ballast Luminous Efficacy

### 1.5.2 ET15SCE8040 – LED Tube Retrofit Scaled Field Placement (SFP)

- Draft Emerging Technologies Assessment, expected Q4 2016

- See filtered DLC List, Linear LED Tube replacement lamps (Ballast Compatible Only)

- Sampling of installations, tracking, surveys, light measurements (pre and post)

- Average RUL, Average Lamp Wattage, Equivalency

- Number of customer satisfaction surveys received

During the LED Tube Retrofit SFP, account managers were provided with a check-list of items the projects must meet before moving forward as shown below. More details can be found in the attachment [Attachment 4]. This form was intended only for the SFP and will not be used during the launch of this deemed measure.

- LED T8 lamp must be a Type A,

- Must use existing linear fluorescent ballast,

- 4-foot long,

- Required check for ballast compatibility,

- Dimmable ballast if existing system was dimmable,

- Warranty on QPL must match the specification sheet.

- Lamps were to only be installed in pre-qualified fixture types such as strip, cove, wrap, and prismatic troffers.

Data such as baseline/measure information, type of fixture, pre/post light measurement, and ballast life were gathered. Raw data can be found in the attachments [Attachment 5].

Ballast life was either taken from the date stamp on the ballast or verbally from the customer. Some customers did not know how long the existing ballasts have been in operation. Averaging all the remaining useful life of the ballasts resulted in a RUL of 6.9 years, which is higher than the typical DEER lamp life of 20,000 hours.

Based on customer satisfaction surveys, customers who installed LED T8 lamps were mostly satisfied and would recommend the same technology to others. Although this is not a complete list of surveys received, customers who did take the survey were very satisfied with color, installation, and aesthetics. Survey chart is shown below. A total of 12 surveys out of 35 projects were provided. A complete set of surveys will be available upon completion of the report.

Customer Satisfaction Survey

A follow review up occurred 6 weeks after installation to monitor ballast replacements. Although 95% were unchanged, less than 2% were replaced within the 6-week period and 4% initially replaced due to compatibility issues as shown in figure below. SCE’s Program Requirements for this measure will address this potential compatibility problem by requiring that the LED T8 lamp documentation to provide a list of compatible ballast model numbers.   Note that the compatible ballast testing will also address the potential issue of mis-matching differing ballast factors and lamps.

A 1-year or 4,380 hours follow-up is also scheduled from the field trial to further monitor the persistence and the replacement of the ballast.

Ballast Replacements

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

The draft Emerging Technology study referenced in Section 1.5.2 utilized data from 35 Customized projects which provided a total of 118,628 lamps for the sample.

Light measurements were taken pre- and post- to show the difference in light level measured with a calibrated Konica Minolta Illuminance Meter. The measurements were taken at the recommended points by Department of Energy’s Standard Measurement and Verification Plan for Lighting Retrofit Projects for Buildings and Building Sites document, shown in the figure below.

Light Measurement Points

The partial figure below shows the percent difference of the light measurement from pre- and post-measurements.

Light Measurement

Normalizing the LED wattage to within 10% of overlit/underlit spaces resulted in 11 delta Watts. Delta Watts on a straight average of all the lamp for both baseline and measure resulted in 11 Watts. Breaking out the measures by baseline lamp type also yielded the same delta Watts.

Tables below shows the average data collected from the Customized projects, not normalized by light output difference.

Baseline Average

| Nominal LF Watts | # of Fixtures | # of Lamps | Avg. Watts | Weighting | Weighted Average |
| --- | --- | --- | --- | --- | --- |
| 32 | 24389 | 65146 | 0.029424 | 0.456716209 | 0.013438194 |
| 28 | 3638 | 7675 | 0.025075 | 0.053806786 | 0.001349222 |
| 25 | 34149 | 69819 | 0.022904 | 0.489477005 | 0.011211098 |
| Baseline Weighted Average |  |  |  |  | 0.026 |

Measure Average

| Nominal LF Watts | # of Fixtures | # of Lamps | Avg. Watts | Weighting | Weighted Average |
| --- | --- | --- | --- | --- | --- |
| 32 | 24389 | 65146 | 0.013281 | 0.456985325 | 0.006069133 |
| 28 | 3638 | 7591 | 0.014548 | 0.053249249 | 0.000774682 |
| 25 | 34149 | 69819 | 0.015099 | 0.489765426 | 0.007394989 |
| Measure Weighted Average |  |  |  |  | 0.014 |
| Delta |  |  |  |  | 0.012 |

Measure Average using DLC Rated Data

| Nominal LF Watts | # of Fixtures | # of Lamps | Avg. Watts | Weighting | Weighted Average |
| --- | --- | --- | --- | --- | --- |
| 32 | 24389 | 65146 | 0.015390836 | 0.456985 | 0.007033386 |
| 28 | 3638 | 7591 | 0.015484312 | 0.053249 | 0.000824528 |
| 25 | 34149 | 69819 | 0.015588164 | 0.489765 | 0.007634544 |
| Measure Weighted Average |  |  |  |  | 0.015 |
| Delta |  |  |  |  | 0.011 |

Based on feedback, the data collected through Customized Program were not relative to how the measures would be offered under the Deemed Program. Therefore, the recommended values are shown in the table below.

Measure and Base Wattage

| Technology | Average Watts |
| --- | --- |
| Linear Fluorescent | 26 |
| LED T8 Lamp Type A | 18 |

The energy savings estimates are calculated as follows:

The following is a sample energy savings calculation for a 4-foot LED T8 Lamp UL Type A replacing Linear Fluorescent T8 Lamp in an Assembly building type, Climate Zone 6, and RET install type.

EnergySavingskWhUnit×Year=26-18×1170×1.11,000WatthourskWh

EnergySavingskWhUnit×Year=10.296

The demand reduction estimates are calculated as follows:

The following is a sample demand reduction calculation for a 4-foot LED T8 Lamp UL Type A replacing Linear Fluorescent T8 Lamp in an Assembly building type, Climate Zone 6, and RET install type.

Demand ReductionkWUnit=26-18×.264×1.231,000WatthourskWh

Demand ReductionkWUnit=0.00260

Energy savings for other building types and climate zones can be found in the attachments section [Attachment 1].

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Community College | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Primary School | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Relocatable Classroom | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Secondary School | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - University | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Grocery | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Health/Medical - Hospital | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Health/Medical - Nursing Home | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Guest Rooms | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Hotel | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Motel | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Manufacturing - Bio/Tech | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Manufacturing - Light Industrial | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Office - Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Office - Small | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Restaurant - Fast-Food | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Restaurant - Sit-Down | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Multistory Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Single-Story Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Small | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Storage - Conditioned | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Storage - Unconditioned | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Warehouse - Refrigerated | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Residential Mobile Home - Double-Wide | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Residential Multi-family | DEER:Indoor_Non-CFL_Ltg | NON_RES |

# Section 4. Costs

## 4.1 Base Case Cost

Base material cost was taken from the Work Order 17 calculator [Attachment 2]. Labor cost is based upon the measure labor cost taken from the SFP ET study as the required installation effort is the same.

Base Cost

| Measure Code | Measure Name | Material | Labor | Total |
| --- | --- | --- | --- | --- |
| LT-11950 | 4 foot LED T8 Lamp UL Type A Replacing Linear Fluorescent T8 Lamp | $3.61 | $8.47 | $12.08 |

## 4.2 Measure Case Cost

Measure and labor cost was taken from a sample of lamps from the ET study [Attachment 5] consisting of 29 projects and 64,094 LED T8 lamps. The total cost of the material and the total number of lamps were used to come up with an average cost.

Measure Cost

| Measure Code | Measure Name | Material | Labor | Total |
| --- | --- | --- | --- | --- |
| LT-11950 | 4 foot LED T8 Lamp UL Type A Replacing Linear Fluorescent T8 Lamp | $16.25 | $8.47 | $24.72 |

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| LT-11950 | RET | $12.64 | $24.72 | $12.64 |

# Attachments

1.  2. 3. 4.

5. 6. 7. 8.

# References

[355]

[493]

[497]

http://www.ncaee.org/modules/info/files/files_4adcd38174d01.pdf