Work Paper SCE13LG118

Revision 1

Southern California Edison

LED Ambient Commercial Fixtures and Retrofit Kits

For Work Paper Reviewer Use Only

List all major comments that occurred during the review. This table may only be removed during management review.

| Major Comment | Reviewer Name | Date | Outcome/Resolution |
| --- | --- | --- | --- |
| E.g. Please remove measure LT-12345 (LD123) from this work paper because it is no longer eligible for incentives. | Reviewer 1 | 6/1/15 | E.g. Comment incorporated. LT-12345 was removed. |

# At-a-Glance Summary

| Measure Codes | Refer to Excel Calculation Attachment |
| --- | --- |
| Measure Description | 2x2/1x4/2x4 LED Luminaire/Retrofit Kit |
| Base Case Description | 2x2/1x4/2x4 Linear Fluorescent Fixture |
| Units | Per kilolumen |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | ILtg-Com-LED-50000hr – 12 years |
| Measure Installation Type | Replace on Burnout (ROB) |
| Net-to-Gross Ratio | ET-Default – 0.85 All-Default<=2yrs – 0.7 Com-Default-HTR-di, Ind-Default-HTR-di, Agricult-Default-HTR-di – 0.85 |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 3/2/15 | Yun Han | - New WP for 2015 Cycle - WP not approved/submitted/filed |
| 1 | 10/1/15 | Yun Han | - Copy of PGECOLTG179r0 - Added Mid-stream Delivery Method for SCE |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |
| 0 | CS |  |  |  |  |
| 0 | Cal TF |  |  |  |  |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This workpaper details the replacement of linear fluorescent fixtures with LED Ambient Commercial Fixtures & Integrated Retrofit Kits.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | 2x2/1x4/2x4 LED Luminaire/Retrofit Kit |
| Existing Condition | 2x2/1x4/2x4 Linear Fluorescent Fixture |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | LT-68379 | LT040 | 2x4 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-95819 | LT041 | 2x4 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-50221 | LT042 | 2x4 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-63572 | LT043 | 2x4 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-60238 | LT044 | 2x2 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-93682 | LT045 | 2x2 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-56629 | LT046 | 2x2 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-81067 | LT047 | 2x2 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-81197 | LT048 | 1x4 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-57366 | LT049 | 1x4 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-65579 | LT050 | 1x4 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-77660 | LT051 | 1x4 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-54695 | LT052 | 2x4 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-73590 | LT053 | 2x4 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-53627 | LT054 | 2x4 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-76794 | LT055 | 2x4 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-94014 | LT056 | 2x2 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-68913 | LT057 | 2x2 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-94216 | LT058 | 2x2 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-55027 | LT059 | 2x2 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-99153 | LT060 | 1x4 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-66777 | LT061 | 1x4 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-50625 | LT062 | 1x4 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces |
|  |  | LT-72522 | LT063 | 1x4 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces |

The measures in this work paper are available for all Commercial building types in all SCE climate zones.

Requirements:

- Must be a one for one replacement for a Linear Fluorescent Fixture with T8 or T5 lamps

- Must be a Design Lights Consortium (DLC) approved New Luminaire or an Integrated Retrofit Kit, listed on the SCE qualified product list as Luminaires/Integrated Retrofit Kits for Ambient Lighting of Interior Commercial Spaces in one of the following sizes: 2x4, 2x2, 1x4

- DLC-listed initial light output must be ≥ 2200 lm and ≤ 6500 lm

- Linear LED replacement lamps do not qualify

- Only Fixtures and Retrofit kits that include new lenses between the LED package and the viewer qualify

- Self-ballasted or screw-based lamps do not qualify

- 5-year warranty minimum

- Must meet the minimum efficacy requirements listed in the table above

DLC requirements for Integrated Retrofit Kits and Luminaires for Ambient Lighting of Interior Commercial Spaces include:

- 5-year warranty

- 50,000 hour L70 Lumen Maintenance

- ≥ 80 Color Rendering Index (CRI)

- ≥ 85 lumens / Watt

- ≤ 5000 Kelvin Correlated Color Temperature (CCT)

- Spacing Criteria from 1.0 to 2.0 in both the 0-180° and 90-270° directions

- ≥75% of Lumen Output in the 0-60° zone

DLC Categories Eligible under this Workpaper

- Must be on SCE Qualified Products List, in one of 6 DLC categories: - 2x2 Luminaires for Ambient Lighting of Interior Commercial Spaces - Integrated Retrofit Kits for 2x2 Luminaires for Ambient Lighting of Interior Commercial Spaces - 1x4 Luminaires for Ambient Lighting of Interior Commercial Spaces - Integrated Retrofit Kits for 1x4 Luminaires for Ambient Lighting of Interior Commercial Spaces - 2x4 Luminaires for Ambient Lighting of Interior Commercial Spaces - Integrated Retrofit Kits for 2x4 Luminaires for Ambient Lighting of Interior Commercial Spaces

Furthermore, the DLC’s QPL is filtered by eliminating tolerances outside of the DLC defined technical requirements for the following performance metrics:

- Light output

- Luminaire efficacy

- Allowable CCT

- CRI

- Power Factor

- Total Harmonic Distortion

- Zonal Lumen Density

Products must meet exact technical requirements listed on DLC for these product categories stated above.

| Performance Metric | DLC Requirement | DLC Tolerance | SCE Program Requirement (1st 6 months) |
| --- | --- | --- | --- |
| Total Light Output | ≥1,500 lumens | -10% | ≥2,200 lumens ≤6,500 lumens |
| Luminaire Efficacy | ≥85 LPW | -3% | ≥85 LPW |
| CRI | ≥80 | -2 points | ≥80 |
| CCT | ≤ 5,000K | N/A | ≤ 5,000K |
| Power Factor | ≥0.9 | -3% | ≥0.9 |
| Total Harmonic Distortion | ≤20% | +5% | ≤20% |
| Zonal Lumen Density for 2x2, 1x4, 2x4 Luminaires & Integrated Retrofit Kits | 1.0-2.0 for SC 0-180° & 90-270° ≥75% for ZL 0-60° | ±0.1 -3% | 1.0-2.0 for SC 0-180° & 90-270° ≥75% for ZL 0-60° |
| Lumen Maintenance | L70>50,000 | N/A | L70>50,000 |
| Minimum Warranty | 5 years | N/A | 5 years |

## 1.2 Technical Description

Light emitting diode (LED) sources have improved over the past decade making them an efficient and reliable lighting technology. Many LED products have successfully replaced other lighting sources in some applications and made their way into the market through continuous improvement and compete with more established sources across many applications.

Recessed rectangular light fixtures, sometimes known as troffers, have traditionally used linear fluorescent light sources: T8 lamps predominate currently, with small T5 market share and a diminishing T12 presence in non-residential building stock. Similar fixture shapes are in use for much less common surface mountings in non-residential buildings, for spaces where recessed ceiling space is unavailable but ease of maintenance dictates a common lamp type. 4 foot lamps predominate, with 2 foot or U-bent 4 foot lamps also common.

LED products offer advantages over linear fluorescent products for the general commercial fixture market. LED chip efficacies now routinely surpass the best fluorescent lamp-and-ballast system efficacies, and the superior directional light control of LEDs allows even greater fixture efficacy improvements. LED products reduce maintenance costs relative to linear fluorescent products that require re-lamping. Linear fluorescent lighting represents 72% of energy use in the commercial lighting sector and 80% of all commercial light fixtures, and therefore represents an enormous opportunity for potential LED savings [A].

LED Ambient Commercial products, which are most commonly used in recessed ceilings but may also be surface-mounted or suspended, are available both as complete new fixtures (a.k.a. luminaires) and as integrated retrofit kits. Both options include new LED chips, an LED driver or power supply, and optical control or lenses.  Retrofit kits allow these components to be fit into existing linear fluorescent metal housing, whereas new LED luminaires are sold complete with a new metal housing.

Two Emerging Technology reports commissioned by PG&E’s ET Program have demonstrated savings potential from these measures and allowed PG&E to refine the requirements and specifications for these measures: ET12PGE1481 and ET11PGE3251.[H,I]

Improvements in LED technology, particularly improving efficacies able to compete with and exceed the best T8 lamp-and-ballast systems producing over 95 lumens per Watt, have made LED panel fixtures feasible. These are fixtures with output of at least 1,500 lumens.  Currently DLC requires LED panels and kits achieve output of at least 1,500 lumens.  Panels eligible for these measure codes shall have initial light output rated between 2,200 lumens and 6,500 lumens.

LED fixtures under this workpaper are assigned a measure code according to efficacy, fixture type, and fixture size. The energy impact common unit is the kilolumen of initial rated light output for the LED fixture, according to the DLC listing.

This workpaper describes the energy savings associated with the replacement of linear fluorescent fixtures.

## 1.3 Installation Types and Delivery Mechanisms

The delivery methods available for these measures are:

- Financial Support – Down-Stream Incentive

- Financial Support – Direct Install

- Midstream Programs – Mid-stream Incentive

The program/install type for the above measures is:

- Replace on Burnout (ROB)

The Midstream Lighting Program provides incentives on certain pre-approved energy-efficient products at the point of sale in order to decrease electricity consumption in SCE’s service territory.  SCE reimburses the distributor a pre-authorized incentive amount for each qualifying product sold to a qualifying purchaser for which the distributor has provided a point of sale discount in the amount of such incentive verified through invoice, subject to program requirements described in the midstream program agreement.

The Non Residential Direct Install program quality control ensures correct documentation of existing measure, base case, and specification of the energy efficient product installed.  SCE requires a detailed Product Location Form (PLF) for each project submitted for rebate or incentive.  The PLF is a form which information for measures installed in all building types related to the Non Residential Direct Install program.  The PLF contains the following fields: Service Account Address, Measures Proposed/Installed, Product Make/Model, Install Locations (detailed to define separate spaces/floors, as well as specific locations within the space including but not limited to:  Bathrooms, Hallways, Meeting Rooms, Offices, Warehouse, etc.).

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |
| Partnership | The program implements projects through a partnership between the utility and an institutional, government, or community-based organization. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | No |
| DEER Version | DEER 2016, READI v2.3.0 |
| Reason for Deviation from DEER | All measures are from DEER |
| DEER Measure IDs Used | LEDFixt-RetKit-2x2(11.8w) |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| ET-Default | Emerging Technologies approved by ED through work paper review | Any | Any | Any | 0.85 |
| All-Default<=2yrs | All other EEM with no evaluated NTGR; new technology in program for 2 or fewer years | Any | Any | Any | 0.7 |
| Com-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Com | Any | Any | 0.85 |
| Ind-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ind | Any | Any | 0.85 |
| Agricult-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Ag | Any | Any | 0.85 |

Note: Direct install measures that are not hard-to-reach will use the default NTG value.

This work paper includes measures that are offered via direct install activities into hard-to-reach (HTR) customer facilities.  “Final Resolution E-4700”, dated December 18, 2014, defines specific criteria to classify customer facilities as HTR and also states that two criteria are sufficient to identify HTR customers if one of the criteria met is the geographic criteria.

SCE’s Commercial Direct Install program delivers free and low cost energy efficiency hardware retrofits through installation contractors to reduce peak demand and energy savings for small and medium commercial customers.  The barriers for customer participation include limited capital resources, lack of expertise and understanding of the understanding of the benefits of energy efficiency, a suspicion of the “free offer” and its legitimacy, and language and cultural barriers.  The program also addresses the ongoing concern with “split incentives”, where the customer is not the owner of the property, and therefore, lack incentive to improve their energy usage.  SCE’s Commercial Direct Install program will track the following three (3) customer data points to identify direct install activities in HTR customer facilities.  If geography and business size criteria are satisfied, SCE will identify the customer as HTR.  If geography and language criteria are satisfied, SCE will identify the customer as HTR.  Other measures in the Commercial Direct Install program will receive default NTG (NTGR_ID: Com-Default>2), unless otherwise specified in DEER.

- Business Size – Customer must have less than ten employees

- Language – Customer’s primary language spoken is not English

- Geography – Businesses in areas other than the United States Office of Management and Budget (OMB) Combined Statistical Areas (CSA) of the San Francisco Bay Area,  the Greater Los Angeles Area and the Greater Sacramento Area  or the OBM metropolitan statistical areas or San Diego County

The “Required Corrections to Measure Level Input Parameters Identified by Commission Staff per D.14-10-046 Order Paragraph 16”, dated November 3, 2014, includes additional clarification for the geographic criteria:

“Notes on OMB CSA designations:

The OMB has designated a 12-county CSA titled the San Jose-San Francisco-Oakland, CA Combined Statistical Area which includes the nine counties of Alameda, Contra Costa, Marin, Napa, San Francisco, San Mateo, Santa Clara, Solano, and Sonoma which border the San Francisco Bay plus the three counties of San Joaquin, Santa Cruz, and San Benito that are economically tied to the nine counties that that border the San Francisco Bay.”

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| ILtg-Com-LED-50000hr | LED Fixture - Indoor- Commercial | Com | Lighting | 12 | 4 |

### 1.4.2 Codes and Standards Analysis

These measures do not fall under Title 24 [355] of the California Energy Regulations. The Lighting Power Densities of both measure and base case are capped by Title 24, but both measure and base cases are configured so as to be compliant with Title 24, with the measure capturing savings above Title 24 minimums.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | N/A | July 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### 1.5.1 CALiPER Application Summary Report 13 [B]

A few of the conclusions that CALiPER reported in its most recent application summary report on LED Panels (#13 from 2011) from tests of 6 LED 2x2 troffer fixtures:

- LED products tested were more efficacious and produced more light output that some, but not all, of the fluorescent benchmark products

- 5 of 6 products performed as claimed in product literature, and one significantly underperformed

5 LED troffers had been tested in a few previous CALiPER reports in 2009 or earlier, with 4 of the 5 having efficacies similar to fluorescent benchmarks, and with typically lower spacing criteria.

### 1.5.2 PG&E ET Studies

PG&E commissioned two Emerging Technology studies in recent years to identify and develop information on interior commercial applications.

Project ET12PGE1481 conducted a comprehensive LED retrofit in a retail store environment with multiple fixture and lamp types. It confirmed that completing a store-wide, comprehensive LED retrofit is not only feasible, but cost-effective as well. Overall, the project achieved a 58% reduction in energy use for LEDA eligible products, and 47% on a store-wide basis. The study participant was very satisfied with the energy savings, projected maintenance savings, and lighting quality provided by the LED products that were installed [H].

This project evaluated six different lighting applications in eight store study areas, evaluating energy consumption and lighting performance in each area. Interior applications included A-lamp shape, Directional, MR16, Decorative, Downlight, Troffer, and High-bay. The projects found cost-effective retrofit options store-wide, including a return-on-investment of 17.3% for measures eligible for the LEDA advanced incentive program.

Project ET11PGE3251 demonstrated LED panel fixtures in an office lighting application with an Advanced Lighting Control System (ALCS). It demonstrated that it is easier to integrate controls with the latest LED products in the market which can help achieve even deeper savings. An initial energy savings of 21% resulted from replacing fluorescent lighting with LED lighting in an office. A further energy savings of 41% resulted from adding the ALCS [I].

This study focused on a Class A commercial office space, and used a phased approach to study different levels of control (task-tuning, occupancy-sensing, daylight-sensing, individual dimming) in conjunction with LED fixtures.  The LED luminaires were found to be highly configurable for these multiple control strategies, making them attractive to customers at the leading edge of technology adoption in both the workplace data and lighting product segments. Customers who have interest in maximizing both individualized distributed environmental control and sustainable energy saving practices will be particularly attracted to these options. The payback on the combined luminaire and controls retrofit was very high (generally > 50 years), but customers looking for workplace data benefits or already planning fixture replacement will see a lower incremental cost. The study recommended LED sources for this application based on several benefits: “lighting distribution, color rendering, and color temperature which are comparable to or better than fluorescent sources.”

Linear fluorescent lighting represents 72% of energy use in the commercial lighting sector and 80% of all commercial light fixtures, and therefore represents an enormous opportunity for potential LED savings. Due to the high efficacy of linear fluorescent lamps, there have only recently been suitable LED replacements for traditionally linear fluorescent applications, such as general purpose commercial lighting.

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

The fixture performance in the applicable categories of the DLC list—LED Luminaires and Retrofit Kits for Ambient Lighting of Interior Commercial Spaces—was analyzed to justify the light output equivalency assumptions. The 6,840 fixtures in these categories were analyzed for luminaire efficacy.

Delta Wattage Assumption (ΔW)

The base case linear fluorescent fixtures were modeled across the DLC light output range according to the most common fixture type in a configuration meeting appropriate Federal lamp standards, Federal ballast standards, and California Title 24 (T24) interior commercial lumen power density (LPD) requirements. Rather than assume a single base case lamp-and-ballast-and-fixture combination as a base case, the efficacy of a standards-compliant base case fixture in terms of lumens per Watt (LPW) is used to calculate savings.

The code-compliant base case fixture model used is from the 2011 Codes and Standards Enhancement (CASE) Report for Indoor Lighting Controls [C]. This report developed the most thorough commercial interior lighting model available in California standards proceedings. The model used by CASE author offers a combination of interior spaces: large open-plan areas as found in many offices, as well as small spaces typical of private offices or meeting rooms. The panel fixtures modeled are 2x4 3-lamp T8 parabolic fixtures, matching a typical parabolic luminaire with 74.7% fixture efficacy.

The model was updated to 2013-T24 LPD specifications, which reduce LPDs for Office Buildings via the Complete Building Method from 0.9 W/sf to 0.8 W/sf [E]. The 0.8 W/s.f. value used is lower than other applicable building types in Table 140.6-B of 2013-T24: 1.0 W/s.f. for General Commercial/Industrial Work Buildings, 1.2 W/s.f. for Restaurant Buildings, and 1.0 W/s.f. for School Buildings. The model was changed to reflect Federal fluorescent lamp minimum standards with a 2950-lumen lamp, but the ballast was unchanged as it reflected a premium electronic ballast listed by the Consortium for Energy Efficiency’s HPT8 standard and the National Electrical Manufacturers Association’s NEMA Premium listing. The CASE Report model’s assumption for Light Loss of 9.7% was used. The model suggests that illumination from recessed fluorescent fixtures compliant with current code can be obtained at maintained fixture efficacy of 58.8 LPW. This figure is higher, accounting for 9.7% lumen depreciation, than the 5 fluorescent benchmark troffer fixtures tested in CALiPER Rounds 9 and 13 (all of which were 2x2 fixtures) [F].

The DOE Solid-State Lighting CALiPER Reports have examined 12 LED panel fixtures combined in application summary reports 1, 5, 7, 9 and 13, but none of these tests are dated more recently than September of 2011, making them of limited relevance for a workpaper in 2015 given LED improvements. Given their age, CALiPER reports were not used for determining equivalency.

Initial LED lumen efficacy assumptions are set by the measure code minimum requirements, starting with 85 LPW for the lowest-efficacy measure code corresponding with DLC’s minimum efficacy.  Calculating the wattage corresponding to this efficacy for a unit of one kilolumen can be accomplished by dividing 1000 lumens by 85 lumens per watt, resulting in 11.8 Watts per kilolumen for the measure case. The LED fixture performance calculation relies on the fact that test lamp performance for LED fixtures is measured via absolute photometry, compared to the relative photometry which is the standard for linear fluorescent fixtures. The practical implication of this is that the LED product efficacies found in the DLC listing, 85 LPW and higher, already reflect the light losses inside the fixture, giving an 85-LPW LED fixture a significant advantage in supplying illumination over a fluorescent fixture with an 85 LPW lamp-and-ballast system.

Maintained lumen output equivalency was based on the full list of DLC products and on LED lumen maintenance data from the Lighting Facts database. All 156 Lighting Facts fixtures with lumen maintenance information were considered as a full dataset, as well as the subset of 20 fixtures that were both DLC-listed and available with lumen maintenance values for the 25,000-hour mark, the mid-point of the 50,000 DLC specification minimum. The full dataset is provided in the calculations file for this workpaper. Analysis of both the full set and subset, in accordance with the LED lumen output extrapolation formula published in Federal rulemaking [G], suggests LED fixture lumen maintenance at EUL of 87.0% for the blended Commercial building type with 3077.9 DEER Measure hours per year for 16 years, based on the following calculation:

Com EUL hours per DEER	= DEER Annual Measure HOUstd  ͯ  EUL fixture maximum

= 3077.9 hours/year  ͯ  16 year maximum EUL

= 49,246.4 hours

This is less than 50,000, so 49,246 hour EUL is used for Com building type

LED lumen maintenance varies by building type due to differing DEER run hours. Motel annual run hours of 1500 result in 24,000 run hours over 16 year EUL, and thus 93.4% lumen maintenance. DEER annual run hours in half of the DEER building types, including the Large Retail, Restaurant and Grocery, over 16 years will exceed 50,000 hours, so the 50,000 DLC-minimum rated life fixture is used, along with an 87.0% lumen maintenance figure. The calculation, based on the Federal extrapolation formula, is taken across all 20 DLC-listed fixtures with 25,000-hour Lighting Facts data available, as follows:

Lumen Maintenance at Com EUL =
eComEUL hours×lnLumen Maintenance % @ 25,000 hours÷25,000 hours

=e49,246×ln93.16 ÷25,000

=87.0% lumen maintenance

This workpaper does not group base and measure case fixtures by wattages. The base case and measure wattages are determined by the methods described above.

LED Ambient Commercial Fixtures & Retrofit Kits Base and Measure Wattages

| Base Case | Base Case Wattage | Measure Case Wattage | Delta Wattage |
| --- | --- | --- | --- |
| LED Luminaires/Retrofit Kits rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | 14.8 – 15.9 | 11.8 | 3.0 – 4.1 |
| LED Luminaires/Retrofit Kits rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | 14.8 – 15.9 | 10.5 | 4.3 – 5.3 |
| LED Luminaires/Retrofit Kits rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | 14.8 – 15.9 | 9.1 | 5.7 – 6.8 |
| LED Luminaires/Retrofit Kits rated ≥125 LPW, Ambient Interior Commercial Spaces | 14.8 – 15.9 | 8.0 | 6.8 – 7.9 |

Base case wattage varies by building type

Energy Savings

The lighting wattage difference (Watts per unit) is the difference between the electric demand of the base case unit and the electric demand of the measure case unit. The hours of operation and interactive effects are from DEER 2014.

∆Watts/kilolumen: The demand difference (watts per kilolumen) is simply the difference between the electric demand of a kilolumen unit of the base case fixture and the electric demand of a kilolumen unit of the measure case fixture.

∆Watts/kilolumen = Base Case Watts/kilolumen - Measure Case Watts/kilolumen

Example:

∆Watts/kilolumen = 14.8 W – 11.8 W = 3.0 ∆Watts/kilolumen

Annual Electric Savings:

Annual Energy Savings [kWh/kilolumen] = (∆Watts/kilolumen) x (Annual Hours of Operation) x (Energy Interactive Effects) / (1,000 Watts / kW)

Demand Reduction

This measure includes HVAC interactive effects savings. This measure is not an Early Retirement measure.

∆Watts/kilolumen: The demand difference (watts per kilolumen) is simply the difference between the electric demand of a kilolumen unit of the base fixture and the electric demand of a kilolumen unit of the energy efficient fixture.

∆Watts/kilolumen = Base Watts/kilolumen - Energy Efficient Watts/kilolumen

Where:

Base Case Watts/Kilolumen represents code/industry standard base unit demand.

Demand Reduction:

Demand Reduction [kW/kilolumen] = (∆Watts/kilolumen) x (Lighting Coincident Demand) x (Demand Interactive Effects) / (1,000 Watts/kW)

Gas Energy Savings

Gas estimates are entirely based on the estimated increased gas use through calculated interactive effects. This measure includes HVAC interactive effects impacts. This measure is not an Early Retirement measure.

∆Watts/kilolumen: The demand difference (watts per kilolumen) is simply the difference between the electric demand of a kilolumen unit of the base fixture and the electric demand of a kilolumen unit of the energy efficient fixture.

∆Watts/kilolumen = Base Watts/kilolumen - Energy Efficient Watts/kilolumen

Annual Gas Savings:

Annual Gas Savings [∆Therms/kilolumen] = (∆Watts/kilolumen) x (Annual Hours of Operation) x (Gas Interactive Effects) / 1,000 Watts/kW

Complete list of savings in all building types and climate zones can be found in the attachment [attachment 1].

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Community College | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Primary School | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Relocatable Classroom | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Secondary School | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - University | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Grocery | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Guest Rooms | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Health/Medical - Hospital | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Hotel | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Manufacturing - Bio/Tech | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Manufacturing - Light Industrial | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Lodging - Motel | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Health/Medical - Nursing Home | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Office - Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Office - Small | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Restaurant - Fast-Food | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Restaurant - Sit-Down | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Multistory Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Single-Story Large | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Retail - Small | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Storage - Conditioned | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Storage - Unconditioned | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Warehouse - Refrigerated | DEER:Indoor_Non-CFL_Ltg | NON_RES |

# Section 4. Costs

Costs are taken from READI. The outputs can be found in the attachment [Attachment 1].

## 4.1 Base Case Cost

It is assumed the labor cost of replacing the measure case fixture would be the same as the base case fixture. The base case and measure case costs include just equipment costs.  The base case costs are taken from distributor catalogs and websites and confirmed with manufacturer representatives where possible.

Base Cost

| Solution Code | Measure Name | Base Labor Cost | Base Cost | Total Base Cost |
| --- | --- | --- | --- | --- |
| All | All LED Luminaires/Retrofit Kits Measures for Ambient Interior Commercial Spaces | $27.06 | $15.10 | $42.16 |

## 4.2 Measure Case Cost

The measure equipment costs were developed from California distributor catalogs and websites and confirmed with manufacturer representatives where possible.

Measure Cost

| Solution Code | Measure Name | Measure Labor Cost | Measure Cost | Total Measure Cost |
| --- | --- | --- | --- | --- |
| LT-68379 | 2x4 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-95819 | 2x4 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-50221 | 2x4 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-63572 | 2x4 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |
| LT-60238 | 2x2 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-93682 | 2x2 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-56629 | 2x2 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-81067 | 2x2 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |
| LT-81197 | 1x4 LED new Luminaire rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-57366 | 1x4 LED new Luminaire rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-65579 | 1x4 LED new Luminaire rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-77660 | 1x4 LED new Luminaire rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |
| LT-54695 | 2x4 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-73590 | 2x4 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-53627 | 2x4 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-76794 | 2x4 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |
| LT-94014 | 2x2 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-68913 | 2x2 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-94216 | 2x2 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-55027 | 2x2 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |
| LT-99153 | 1x4 LED Integrated retrofit kit rated ≥85 and <95 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.46 | $68.52 |
| LT-66777 | 1x4 LED Integrated retrofit kit rated ≥95 and <110 LPW, Ambient Interior Commercial Spaces | $27.06 | $41.72 | $68.78 |
| LT-50625 | 1x4 LED Integrated retrofit kit rated ≥110 and <125 LPW, Ambient Interior Commercial Spaces | $27.06 | $65.40 | $92.46 |
| LT-72522 | 1x4 LED Integrated retrofit kit rated ≥125 LPW, Ambient Interior Commercial Spaces | $27.06 | $67.10 | $94.16 |

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| LT-68379 | ROB | $26.36 | $26.36 | N/A |
| LT-95819 | ROB | $26.62 | $26.62 | N/A |
| LT-50221 | ROB | $50.30 | $50.30 | N/A |
| LT-63572 | ROB | $52.00 | $52.00 | N/A |
| LT-60238 | ROB | $26.36 | $26.36 | N/A |
| LT-93682 | ROB | $26.62 | $26.62 | N/A |
| LT-56629 | ROB | $50.30 | $50.30 | N/A |
| LT-81067 | ROB | $52.00 | $52.00 | N/A |
| LT-81197 | ROB | $26.36 | $26.36 | N/A |
| LT-57366 | ROB | $26.62 | $26.62 | N/A |
| LT-65579 | ROB | $50.30 | $50.30 | N/A |
| LT-77660 | ROB | $52.00 | $52.00 | N/A |
| LT-54695 | ROB | $26.36 | $26.36 | N/A |
| LT-73590 | ROB | $26.62 | $26.62 | N/A |
| LT-53627 | ROB | $50.30 | $50.30 | N/A |
| LT-76794 | ROB | $52.00 | $52.00 | N/A |
| LT-94014 | ROB | $26.36 | $26.36 | N/A |
| LT-68913 | ROB | $26.62 | $26.62 | N/A |
| LT-94216 | ROB | $50.30 | $50.30 | N/A |
| LT-55027 | ROB | $52.00 | $52.00 | N/A |
| LT-99153 | ROB | $26.36 | $26.36 | N/A |
| LT-66777 | ROB | $26.62 | $26.62 | N/A |
| LT-50625 | ROB | $50.30 | $50.30 | N/A |
| LT-72522 | ROB | $52.00 | $52.00 | N/A |

# Attachments

1.

# References

[355]

[A] US Department of Energy, “2010 U.S. Lighting Market Characterization,” prepared by Navigant Consulting. January 2012. Accessed at http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/2010-lmc-final-jan-2012.pdf. 72% energy use is shown in Table 4.8; 80% lamp penetration shown in Table 4.2.

[B] CALiPER Summary Report Round 13. DOE. October 2011.

[C] CASE_Nonres_Indoor_Lighting_Controls.pdf; accessed at http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/2011-04-04_workshop/review/Nonres_Indoor_Lighting_Controls.pdf

[D] Cooper_2P2GAX332_3L_T8_18C_spec-sheet.pdf; accessed at http://www.cooperindustries.com/content/dam/public/lighting/products/documents/metalux/spec_sheets/090386_2P2GAX332_3L_T8_18C.pdf

[E] CEC-Title24-2013.pdf, p. 205 (header indicating p. 190); accessed at http://www.energy.ca.gov/2012publications/CEC-400-2012-004/CEC-400-2012-004-CMF-REV2.pdf

[F] CALiPER Summary Report Round 13, chart p. 21. DOE. October 2011.

[G] Fed Register 2014-12127.pdf p. 17; accessed at http://www.gpo.gov/fdsys/pkg/FR-2014-06-03/pdf/2014-12127.pdf

[H] DEER2013 v1.0, see calculations workbook, NTGR worksheet

[I] A Comprehensive Store Retrofit to LED lighting in Common Lighting Applications. PG&E Emerging Technologies Program. Accessed at http://www.etcc-ca.com/sites/default/files/reports/ET12PGE1481%20Retail%20LED%20updated%2003132014.pdf.