Work Paper SCE13PR007

Revision 3

Southern California Edison

Cycling Air Dryers for Compressed Air Systems

# At-a-Glance Summary

| Measure Codes | PR-80888 |
| --- | --- |
| Measure Description | Cycling refrigerated air dryer installed on a compressed air system |
| Base Case Description | Standard refrigerated (non-cycling) air dryer installed on a compressed air system |
| Units | Standard cubic feet per min (scfm) |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 13 years (DEER EUL ID: CompAir-CycAirDryr) |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.6 (DEER NTGR ID: Ind-Default>2yrs) 0.6 (DEER NTGR ID: Ag-Default>2yrs) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 5/25/12 | Sabarish Vinod/Lincus,Inc. | Original work paper template for 2013 PC |
| 1 | 12/6/13 | Jason Wang/SCE/EAS | Added a measure for cycling dryers 100-200 hp. |
| 2 | 11/7/14 | Rob Guajardo /SCE/EAS | Removed PR-59959 for cycling dryers 100-200 hp and all associated savings/costs. Changed NTG from 0.7 to 0.6 for Industrial and added NTG of 0.6 for Agricultural. Changed install type from ROB to REA and associated measure costs. Revised peak kW calculations for the correct 2013 T24 average peak temperatures. Updated DEER technology fields and to new WP template. |
| 3 | 2/2/16 | Ryan Cho/SCE | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -Removed SCE building types -No value modifications |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper involves the installation of a cycling refrigerated air dryer on an existing compressed air system.  The base case for this work paper is a standard non-cycling refrigerated air dryer installed on an existing compressed air system.  The savings in this work paper are provided per standard cubic feet per minute (scfm) of compressed air.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Cycling refrigerated air dryer installed on a compressed air system |
| Existing Condition | Standard refrigerated (non-cycling) air dryer installed on a compressed air system |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
|  |  | PR-80888 |  | Cycling Air Dryers for Compressed Air Systems < 100 hp |

This measure is applicable to air compressors less than 100 hp that have non-cycling dryers. The dryers must have a rated capacity less than or equal to 400 scfm.  The applicant must submit the Compressed Air and Gas Institute (CAGI) spec sheet per Standard ADF 100 for this measure.

The measure in this work paper is eligible for all SCE climate zones for the following building types:

- Education – University

- Manufacturing – Bio/Tech

- Manufacturing – Light Industrial

## 1.2 Technical Description

Refrigerated air dryers remove water vapor from compressed air in order to prevent condensation from contaminating tools, machinery, and piping. They do this by chilling the air until the moisture condenses and then removing it.

- Standard non-cycling refrigerated air dryers use a heat exchanger to transfer heat between air and refrigerant.  Non-cycling dryers usually operate at full capacity regardless of how much air is being used.

- Cycling refrigerated air dryers use a thermal mass (usually water with glycol) to absorb heat from the incoming air. There is one heat exchanger between the refrigerant and the thermal mass, and another between the thermal mass and the incoming compressed air. When the dryer is not needed at full capacity, the extra refrigeration capacity is used to cool the thermal mass down a specified point. Then the dryer compressor is unloaded until the thermal mass is exhausted. This configuration saves energy by matching dryer usage with incoming load.

## 1.3 Installation Types and Delivery Mechanisms

The delivery mechanism is Financial Support - Down-Stream Incentive - Deemed.   The measure installation type is Retrofit Add-on (REA).

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | No |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | N/A |
| Reason for Deviation from DEER | DEER does not contain this type of measure. |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| Ind-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ind | Any | Any | 0.6 |
| Agric-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Ag | Any | Any | 0.6 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| CompAir-CycAirDryr | Cycling Air Dryers for Compressed Air Systems | Ind | CompAir | 13 | N/A |

### 1.4.2 Codes and Standards Analysis

The 2013 Title 24 Standards have requirements for compressed air systems but not for air dryers.  These requirements will not be triggered solely by replacing the dryer in an existing compressed air system; therefore, they do not apply to the calculations in this work paper.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| N/A | N/A | N/A |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### 1.5.1 Non-DEER Study Review

This work paper utilized a study by XENERGY [B, Attachment 4]] to determine the average annual operating hours of compressed air systems.  The AIRMaster+ Tool [E], Aspen System Corporation study [D, Attachment 6], XENERGY study [B, Attachment 4], and a Cadmus study [C, Attachment 5] was consulted/utilized for the energy calculations in this work paper.  A study by The Connecticut Light and Power Company and The United Illuminating Company [A, Attachment 3] was utilized to determine the EUL for cycling air dryers.

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

This section deals with the assumptions and generalizations associated with calculating savings from installing a cycling dryer.

Hours of Operation

Using hours of operation values from a study performed by XENERGY [B, Attachment 4], the average annual operating hours of compressed air system operations is estimated at 5,578 hours.

Measure Categorization

- A market assessment by the Aspen Systems Corporation [D, Attachment 6] stated that about 78% of industrial customers had compressed air systems less than 100 hp, and the average air compressor size was 67 hp. Therefore, a measure was created for the under 100 hp category. The measure calculations are based on a 75 hp air compressor because it is the closest standard compressor size included in the AIRMaster+ data set.

AIRMaster+ Data

Dryers are specified, per the Compressed Air and Gas Institute (CAGI) ADF 100 standard, at an inlet compressed air temperature of 100F, inlet air pressure of 100psig, maximum ambient air temperature of 100F and an inlet compressed air relative humidity of 100% (saturated). Based on these conditions, flow parameters for 75 hp at 100 psig were obtained from AIRMaster+ [E]. Depending on the average rated capacity of the air compressor (in actual cubic feet per minute, acfm), a complementary air dryer size (in standard cubic feet per minute, scfm) was selected; see the table shown below below.

Compressor Flow Data

| Air compressor size (hp) | System pressure (psig) | Average AIRMaster+ rated capacity (acfm) | Standard capacity of air dryer selected to match the compressor (scfm) |
| --- | --- | --- | --- |
| 75 | 100 | 374 | 400 |

CAGI Data

CAGI sheets for several non-cycling and cycling dryers were obtained from manufacturer websites. Using this data, power usage estimates at 100% and 10% load were determined.

Air Dryer Power Requirements from CAGI Sheets

| Air dryer capacity (scfm) | Dryer type | Average power and full load (kW) | Average power at 10% Flow (kW) |
| --- | --- | --- | --- |
| 400 | Non-cycling | 3.03 | 2.93 |
|  | Cycling | 2.75 | 0.47 |

The following figures show the assumed linear relationships between load and power for the dryers.

Figure 1 Dryer Characteristics, 400 scfm

400 scfm dryer

- Non-cycling Dryer (blue line):

Percent Full Load Power%= 0.03847* Load(%)+0.96153

- Cycling Dryer (red line):

Percent Full Load Power%= 0.92121* Load(%)+0.07879

Capacity Correction Factors

Dryers are tested and rated under standard CAGI ADF 100 standard conditions, so to estimate actual performance in each of SCE’s climate zones, several capacity correction factors [Attachment 7] are used:

Correction for Ambient Air Temperature

| Ambient Temperature (°F) | 70 | 80 | 90 | 100 | 110 | 115 | 120 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Correction Factor, C1 | 1.1 | 1.07 | 1.05 | 1 | 0.94 | 0.85 | 0.65 |

The appropriate ambient air temperature correction factors were selected by determining the average monthly dry bulb temperature (from 2013 Title 24 weather files) for each climate zone and interpolating the factors in the table shown above. For example, if climate zone 8 has an average ambient temperature of 71.86 oF in August, the correction factor would be:

C1June,CZ6=1.1-71.86-7080-70*1.1-1.07=1.0944

For the kWh calculations, the C1 factors for all 12 months were averaged to determine a final C1 factor for each climate zone [Attachment 2]. For the kW demand reduction calculations, the C1 factor for the month containing the DEER peak period was used [Attachment 2].

Correction for Inlet Air Temperature

| Inlet Temperature (°F) | 80 | 90 | 100 | 110 | 120 | 140 |
| --- | --- | --- | --- | --- | --- | --- |
| Correction Factor, C2 | 1.5 | 1.21 | 1 | 0.82 | 0.72 | 0.61 |

Correction for System Air Pressure

| System Pressure (°psig) | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Correction Factor, C3 | 0.85 | 0.95 | 1 | 1.07 | 1.13 | 1.18 | 1.2 | 1.22 | 1.24 |

Correction for Dew Point

| Dew Point (°F) | 38 | 41 | 45 | 50 |
| --- | --- | --- | --- | --- |
| Correction Factor, C4 | 1 | 1.12 | 1.17 | 1.22 |

The correction factors for inlet air temperature, system air pressure, and dew point were all assumed to be 1. All four factors are used in the following equation to determine corrected capacity for an air dryer under non-standard conditions:

Corrected flow scfm=Rated flow * C1* C2* C3*C4

Utilization Factor

If an air dryer is left on 24 hours a day, 7 days a week for a whole year, the utilization factor represents what percentage of the dryer’s capacity is actually used by the air compressor, assuming that the air compressor is operated at full load for 5,578 hours/year.

Utilization Factor=Compressor Flow*Annual Hours of OperationCorrected Air Dryer Capacity*8760

To determine the baseline and measure power dryer consumption, it is assumed that the utilization factor represents the average % load on the air dryer. The power consumption equations shown earlier in the section “CAGI Data” are used to find percent full load power, which is then multiplied by full load power to find power consumption.

Power Consumption=Percent Full Load Power%*Full Load Power

Average kW Reduction=Power Consumption Base - Power Consumption Post

kWh Savings=Average kW Reduction*Annual Hours of Operation

DEER peak period kW demand reduction is calculated similarly to Average kW Reduction, except that the ambient temperature correction factors may be different.

Example Calculation: Air Compressor System <100 hp, Climate Zone 9, All Building Types

Energy Savings

Assumptions:

- The average ambient temperature correction factor (C1) is 1.0970. Factors C2, C3, C4 are assumed to remain constant at 1.0.

- The average flow for a 75 hp air compressor is 373.89 acfm, from the AIRMaster+ data set.

- The average power consumption for a 400 scfm non-cycling dryer is 3.03 kW, and 2.75 kW for a 400 scfm cycling dryer.

Corrected Capacity=400 scfm*1.0970*1.0*1.0*1.0=438.80 scfm

Utilization Factor=(373.89  scfm*5578)(438.80 scfm*8760)=54.26%

kWh Savings=Noncycling Dryer Power -Cycling Dryer Power*Hours of Operation

=0.03847*54.26%+0.96153*3.03 kW-0.92121*54.26%+0.07879*2.75 kW*5578

=7,742.13 kWh

kWh Savingsunit=7,742.13 kWh400 scfm=19.36kWhscfm

Peak kW Demand Reduction

Per the following table, the DEER peak period in climate zone 9 occurs in September when the average temperature during peak period is 86.6 °F. This corresponds to an ambient temperature correction factor (C1) of 1.0568 [Attachment 2].

2013 DEER Peak Periods

| Climate Zone | 3-Weekday Period |
| --- | --- |
| 1 | Sep 16 – Sep 18 |
| 2 | July 8 – July 10 |
| 3 | July 8 – July 10 |
| 4 | Sep 1 – Sep 3 |
| 5 | Sep 8 – Sep 10 |
| 6 | Sep 1 – Sep 3 |
| 7 | Sep 1 – Sep 3 |
| 8 | Sep 1 – Sep 3 |
| 9 | Sep 1 – Sep 3 |
| 10 | Sep 1 – Sep 3 |
| 11 | July 8 – July 10 |
| 12 | July 8 – July 10 |
| 13 | July 8 – July 10 |
| 14 | Aug 26 – Aug 28 |

Corrected Capacity=400 scfm*1.0568*1.0*1.0*1.0=422.72 scfm

Utilization Factor=(373.89  scfm*5578)(422.72 scfm*8760)=56.32%

kW Reduction=Noncycling Dryer Power -Cycling Dryer Power

=0.03847*56.32%+0.96153*3.03 kW-0.92121*56.32%+0.07879*2.75 kW

=1.33 kW

kW Reductionunit=1.34 kW400 scfm=0.00335kWscfm

Savings Summary

|  | Cycling Air Dryers for Compressed Air Systems < 100 hp |  |
| --- | --- | --- |
| Climate Zone | kWh/scfm | kW/scfm |
| 6 | 19.41 | 0.00341 |
| 8 | 19.38 | 0.00339 |
| 9 | 19.36 | 0.00335 |
| 10 | 19.33 | 0.00335 |
| 13 | 19.24 | 0.00334 |
| 14 | 19.25 | 0.00334 |
| 15 | 18.98 | 0.00320 |
| 16 | 19.39 | 0.00340 |

See Attachment 1 for the final energy savings and Attachment 2 for the savings calculations.

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Education – University | Industrial | Industrial |
| Manufacturing – Bio/Tech | Industrial | Industrial |
| Manufacturing – Light Industrial | Industrial | Industrial |

# Section 4. Costs

## 4.1 Base Case Cost

For REA measures the customer is making a conscious decision to install/replace add on equipment that will improve the efficiency of the host equipment before its useful life has expired.  Since this is a discretionary choice by the customer the base case cost is $0.

## 4.2 Measure Case Cost

The average measure case equipment costs were determined based on online retailer prices and calculated on a per scfm basis. Since the online quotes did not include labor costs they were assumed to be 25% of the equipment cost.  The results of this analysis is shown in the table shown below.  Please see Attachment 2 for the complete measure cost analysis.

Measure Case Costs

|  | Average Measure Equipment Cost per scfm | Measure Labor Cost per scfm |
| --- | --- | --- |
| Cycling Air Dryers for Compressed Air Systems < 100 hp | $20.93 | $5.23 |

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| PR-80888 | REA | $26.16 | $26.16 | N/A |

# Attachments

- Savings/Cost Calculations

- Study containing EUL

- XENERGY Study

- Cadmus Study

- Aspen Study

- Dryer Capacity Correction Factors

# References

[A] Attachment 3 – The Connecticut Light and Power Company and The United Illuminating Company (2010). UI and CL&P Program Savings Documentation for 2011 Program Year.

[B] Attachment 4 – XENERGY Inc. (2001). Assessment of the Market for Compressed Air Efficiency Services (DOE Publication GO-102001-1197). <http://www1.eere.energy.gov/manufacturing/tech_deployment/compressed_air_ma.html>

[C] Attachment 5 – Cadmus Group Inc. (2008). Small Compressed Air Market Assessment, study of the energy efficiency of compressed air system ≤100 hp.

[D] Attachment 6 – Aspen Systems Corporation (2001). Compressed Air Systems Market Assessment In the Public Service Electric and Gas Service Territory.

[E] AIRMaster+ <http://www1.eere.energy.gov/manufacturing/tech_deployment/software_airmaster.html>