Work Paper SCE13RN027

Revision 0

Southern California Edison Company

Add Doors to Open

Medium Temperature Cases

# At-a-Glance Summary

| Applicable Measure Codes: | RF-22948, RF-46390 |
| --- | --- |
| Measure Description: | Retrofit Add-on of glass doors to medium temperature open vertical refrigerated display case. |
| Base Case Description: | Existing medium temperature open vertical refrigerated display case. Case may or may not have night covers in place. |
| Energy Impact Common Units: | Len-ft (Display case length in feet) |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | $521.55 / Len-ft |
| Measure Incremental Cost ($/unit): | $521.55 / Len-ft |
| Effective Useful Life (years): | 4 years |
| Measure Application Type: | Retrofit Add On (REA) |
| Net-to-Gross Ratios: | 0.60 (NTGR ID: Com-Default>2yrs) 0.85 (NTGR ID: Com-Default-HTR-di) |
| Important Comments: | - This is an “original” work paper from the PG&E. However, it is based on the work paper titled “Vertical Refrigerated Case, Medium Temperature: Open to Closed” with file name “WP_PECIREF_PGE604_R0 110701” by Michele Friedrich and Eric Mullendore of PECI. - This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13RN027.0 | No | 07/21/2014 | Thomas Tseng/SCE, Jason Wang/SCE | Original workpaper based on PG&E and PECI. |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

The measure retrofits glass doors onto medium-temperature, open-vertical, refrigerated display cases (also known as open multideck cases).  The existing cases may or may not have night covers; each scenario has its own measure.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| RF-22948 | Add Door to Open Vertical Refrigerated Display Case, Medium Temperature |
| RF-46390 | Add Door to Open Vertical Refrigerated Display Case with Night Covers, Medium Temperature |

Measure Requirements

- Must add glass doors to an existing open-vertical, medium-temperature display case. Completely removing existing display cases replacing them with new cases with glass doors is not eligible.

- Existing night covers must be removed during the retrofit.

- Total lighting power in the case after the retrofit may not exceed total lighting power in the existing case.

- No anti-sweat heaters may be present in the glass doors or door mounting.

## 1.2 Technical Description

Display cases are heavily represented in a typical supermarket and can also be found in a variety of other food retail settings such as smaller grocery stores and some large convenience stores. They can be self-contained systems with a refrigeration compressor and condenser built into the case structure, but more commonly they are served by remote compressors and condensers. In supermarkets, the remote compressors are generally arranged into combined suction groups described as a multiplex system.

Though air curtains are used to reduce the infiltration of non-refrigerated air into the case, infiltration of warm air and moisture is responsible for 70-80% of the refrigeration load on open-vertical refrigerated display cases [446]. Several studies have shown that this infiltration, and thus the total refrigeration load, can be significantly reduced by adding double-paned glass to the existing case [446, 447, 448, 449].

In addition to retrofitting the doors and door frames, the measure may require changes to the refrigeration system serving the affected display case(s). These changes may include but are not limited to: replacing the expansion valve and/or EPR, adjusting the evaporator temperature/pressure set point, resizing refrigeration piping, replacing the flood back valve on the condenser, resizing the coil/piping on applicable heat reclaim systems, and replacing or removing compressors. All of these potential changes stem from the significant reduction in the overall refrigeration load. Due to the complexity in determining which system alterations will be required at a particular site in order to maintain optimum system performance, a refrigeration contractor with design experience should be consulted before proceeding with the retrofit.

## 1.3 Measure Application Type

The delivery methods are:

- Financial Support - Down Stream Incentive – Deemed

- Financial Support – On-bill Finance – loan

- Financial Support – Direct Install

- Partnership – Down-Stream Incentive – Deemed

- Partnership – On-bill Finance – Loan

The application type is Retrofit (REA).

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

DEER 2014 Measure D03-206 is intended to represent retrofitting glass doors to medium-temperature, open-vertical refrigerated display cases. It differs from the measures discussed in this work paper in several key ways. The DEER measure assumed that additional lighting and anti-sweat heaters (ASH) would be installed as part of the retrofit. This work paper specifically excludes adding such equipment load. Additionally, the DEER measure does not allow for night covers in the base case. Because night covers have gained in market acceptance since the DEER team modeled the refrigeration measures and because significant savings potential still exists for cases with existing night covers, this work paper has specific measure iterations to account for night covers in the base case.

Differences in the model used in this work paper and the DEER model:

- The DEER models have a reduced case evaporator coil capacity to match the smaller load found after the measure has been implemented. Evaporator coil adjustments are not part of the retrofits currently being offered on the market so coil capacity was not changed in the models used to develop this work paper.

- The DEER models represent a store with two multiplex refrigeration systems. The models developed in support of this work paper represent a mix of multiplex and stand alone compressors for the refrigeration system. The ratio of compressors for each system is based on market data collected during California EnergySmart Grocer program implementation (n=4,550).

- The DEER models reduce the differential temperature from the supply to the return air in the display case from the base to the measure case.  The models, used to develop this work paper, have a reduced approach temperature between evaporator coil and supply air in the measure case runs instead. This phenomenon occurs as a result of the coil being designed to meet a significantly larger load. The oversized coil supplies air to display case that is closer to the coil temperature than it did before the retrofit occurred.

- This work paper has two base cases. The first is equivalent to the DEER base case. The second uses a reduced infiltration schedule for 6 hours at night time to model night covers in use.

- The models used to develop this work paper used test data by SCE Research and Thermal Test Center (RTTC) and an ASHRAE research project to inform the models for changes in display case infiltration, conduction and refrigeration load for open cases versus cases with doors.

- The DEER models increased the lighting W/ft and added ASH to the retrofit doors.  The terms and conditions of this measure do not allow ASH to be used and requires that total lighting power remains the same or decreases.  The models used in this work paper maintain a consistent auxiliary load between the base case and measure runs.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | Yes (Modified) |
| Deviation from DEER | See Above |
| DEER Version | DEER2014 |
| DEER Run ID and Measure Name (Sample) | Legacy Measure D03-206 |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Com-Default>2yrs | All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | Com | Any | All | 0.6 |
| Com-Default-HTR-di | All other EEM with no evaluated NTGR; direct install to hard-to-reach only. | Com | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis. This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the non-residential defaulted NTG value, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID* | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | Commercial Refrigeration |
| Measure Case UseSubCats | Refrigerated Display |
| Measure Case TechGroups | Refrigerated Storage |
| Measure Case TechTypes | Vertical (multi-deck) Display Fixture |
| Base Case TechGroups | Refrigerated Storage |
| Base Case TechTypes | Vertical (multi-deck) Display Fixture |

### 1.4.2 Codes and Standards Analysis

Federal Standards: The Code of Federal Regulations, Title 10 provides standards for refrigerated cases produced on or after January 1st, 2012. These standards limit the total energy consumption of the units when tested under conditions outlined in ARI Standard 1200-2006 [393]; see below for RC/VOP and SC/VOP:

These standards are not applied to the analysis presented in this work paper as they apply only to new equipment. Such equipment is not expected to significantly influence the typical base case condition until the codes have been in place for several years.

Title 20: These measures do not fall under Title 20 of the California Energy Regulations.

Title 24: These measures do not fall under Title 24 of the California Energy Regulations.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| FS 10CFR (2012) | Section 431.66 | January 1, 2012 |

### 1.4.3 Non-DEER Study Review

Several studies have been conducted on the energy savings associated with the measures described in this paper:

Performance and Energy Impact of Installing Glass Doors on an Open Vertical Deli/Dairy Display Case (2002) [446]: One commonly cited study, conducted by researchers at Southern California Edison’s Research and Thermal Test Center, found that after retrofitting doors on an open display case the cooling load attributable to infiltration was reduced by 68%. This conclusion was based on lab testing conducted with static ambient temperature and humidity levels. The retrofit in this work paper differs from the measure described in the paper because the added doors included anti-sweat heaters, which introduce an additional cooling load on the refrigeration system.

Vertical Display Case Cabinets without and with Doors (2010) [447]: This report, based on lab testing, concluded that the cooling load of open cases decreased 66% versus cases without doors or night covers and 53% when compared to an open case with night covers in place at night.

Comparison of Vertical Display Cases: Energy and Productivity Impacts of Glass Doors Versus Open Vertical Display Cases (2009) [450]: The American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) funded a research project (RP-1402) to compare energy and sales results of open multi-deck vs. reach-in case for medium temperature applications. The display cases tested held alcoholic beverages and dairy and were located in 2 stores in Kansas. The report summary showed an 18% reduction in energy, using calculated compressor savings and measured refrigeration load. Even though this research compared a new open multi-deck case to a new reach-in case, not adding doors to an existing open multideck case, many of the measurements that were taken are valid for comparison to values used in this work paper including: 1) mean door open time for the reach-in case was 12 sec, occurring 6 times an hour; 2) average lighting power = 0.014 kW/ft in the open case; 3) average fan power = 0.009 kW/ft in the open case; and 4) supply to return air delta temp = 10°F for the open case and 2°F for the reach-in case.

Inventory of Direct and Indirect GHG Emissions from Stationary Air Conditioning and Refrigeration Sources, with Special Emphasis on Retail Food Refrigeration and Unitary Air Conditioning (2009) [451]: The State of California Air Resources Board has estimated that adding doors to all viable open vertical refrigerated display cases in the state would reduce energy consumption by more than 1,000 GWH, or 5% of the total energy consumption attributed to the grocery sector.

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 7 below identifies the value/methodology used for the measures in this work paper.

The EUL of a display case door is assumed to be the RUL of the customer existing display case because the door is only considered useful when the display case itself is still functional. The DEER EUL for new display cases (“GrocDisp-FixtDoors”) is 12 years, so the EUL for a door is 4 years.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| GrocDisp-FixtDoors | Non-Residential | ComRefrig | New case with Doors | 4 | N/A |

# Section 2. Energy Savings & Demand Reduction Calculations

## 2.1 Electric Energy Savings Estimation Methodologies

The energy savings for this measure were determined by using detailed computer simulations based on the eQUEST Refrigeration Version 3.61/DOE-2.2R energy analysis program. The program calculates hour-by-hour building and refrigeration system energy consumption over an entire year (8760 hours) using CEC’s Title 24 weather data for a representative city in each CEC-defined climate zone. Model outputs and the associated calculations are available in Attachment 2.

This section describes the modeling methodologies and inputs to DOE2.2R as well as results of a sensitivity analysis to the model inputs.

## 2.1.1 Model Description

The base case model is designed to be representative of existing grocery building stock in California. Figure 1 displays the general site layout and orientation.

Figure 1 eQuest Model Layout

The model shares many building and space characteristics with the DEER 2005 grocery models as evident from Table 8, which lists a number of basic input values and their source.

Table 8 Basic eQUEST Model Characteristics

| Building Characteristic | Input Value | Source |
| --- | --- | --- |
| Area | 50,000 ft2 | DEER 2005 Grocery Model |
| Shell (Walls, Windows, Roof) | Construction and 1978-85 vintage insulation | DEER 2005 Grocery Model |
| Lighting Power Density | 2.0 Watts/SF | DEER 2005 Grocery Model, NREL [452] and T24 Code |
| Miscellaneous Equipment | 0.5 Watts/SF | NREL [452] |
| Whole Building Infiltration | 0.07 CFM/SF | DEER 2005 Grocery Model |
| Sales floor HVAC System Type | Package Variable Volume Variable Temperature set to Constant Volume | DEER 2005 Grocery Model |
| Sales Floor Cooling Capacity | Annual cooling peaks *1.15 - rounded up to the nearest 5 tons with minimum size of 20 tons | Engineering judgment |
| Sales Floor Heating Capacity | Annual heating peaks * 1.2 - rounded up to the nearest 100,000 BTU | Engineering judgment |
| Sales Floor Design Supply Air | 37,200 CFM (equal to 0.85CFM/ft2) | Engineering judgment |
| Outside Air | 15 CFM per person | ASHRAE standard 62 |
| Refrigeration System | Mix of multiplex and stand-alone compressors, air-cooled condensers in most climate zones. Described in Appendix B. | Audit Data from EnergySmart Grocer Program |
| Occupancy schedule | Varying throughout day with peak occupancy at 125 ft2 per person | NREL [452] |

The primary-building system impacted by the measure is the refrigeration system with secondary impacts on the HVAC system. Accordingly particular attention was paid to ensuring that the modeled refrigeration system represented the arrangements common to the current grocery building stock and that the HVAC system was adequately sized to maintain a store temperature of 70o F. This temperature setpoint represents the average temperature recorded by ADM & Associates in their work preparing the 2010 High Impact Measure (HIM) report on door gaskets [453].  A detailed description of refrigeration system model is in Attachment 3.

The whole-building EUI of the base case models averaged 177 kBtu/yr-ft2. One analysis of the CBECS data from 2003 found an average EUI of 203.6 kBtu/yr-ft2 for grocery sites within ASHRAE climate zone 3, which covers most of California [452]. Another analysis of the same data done by Oakridge National Laboratory in support of the ASHRAE standard 100-2006 revision [454] show grocery median values in ASHRAE climate zone 3b and 3c as 163-169 kBtu/yr-ft2 and 178 kBtu/yr-ft2, respectively.

## 2.1.2 Model Refrigeration System

The display cases impacted by the measure are modeled with remote compressors and air-cooled condensers, with the exception of Climate Zones 15 and 16 where an evaporative-cooled condenser was used in the model. There was no modeling of integral units, i.e. display cases with compressor and condenser contained within case. The majority of the open vertical cases are on a suction group connected to a multiplex compressor system, with the minority served by a stand-alone compressor in a condensing unit, i.e. a packaged compressor and condenser. PECI industry experience indicates multiplexes make up a majority of the targeted market for this measure therefore multiplexes were used for the measure modeled refrigeration systems. A survey of EnergySmart Grocer auditors and grocery store design engineers found that 90% of stand-alone refrigeration compressors are in condensing units and 10% are with remote compressors.  The stand alone systems modeled for this work paper used only compressors in condensing units with 1 fan. Additional details of the refrigeration system are outlined in Attachment 3.

## 2.1.3 Model Measures

A sensitivity analysis was completed to quantify the magnitude of effect of key input variables for the modeled measures.  Key input variables were chosen with minimum, maximum and typical ranges obtained from research papers, discussions with manufacturers, display case specification sheets and grocery store design engineers. The max and min values are not absolute max and min values but approximate the top 10% and the bottom 10% on a distribution graph.  Table 9 shows the display case model minimum, typical and maximum values and source for each of the values that were changed between the base case and post-implementation versions of the model.

Table 9 Model Sensitivity Analysis Changes

| Variable | Min Value | Typical Value | Max Value | Source |
| --- | --- | --- | --- | --- |
| Supply Air Temp (deg F) (base/post) | 28/24 | 32/28 | 37/33 | Display case Manufacturer Specifications/SCE report [446] |
| Night covers (base only) | Reduce infiltration to 0.6 for 6 hrs/night | No reduction | _ | SCE report [455] |
| Case light density (W/ft) (base/post) | 8/16 16/11 | 16/16 | 48/48 16/29.8 | Display case Manufacturer Specifications/LED specs |
| Case fan demand (W/ft) (base=post) | 5 | 10 | 15 | Display case Manufacturer Specifications |
| Increase Suction temperature (deg F) (post only) | 4 | 0 | _ | SCE report [446], display case with doors manufacturer specs |
| Anti-Sweat heaters (W/ft) (post only) | _ | 0 | 16.8 | door manufacturer specifications, frame heat |
| Coil Capacity (BTU/hr-ft) Infiltration (BTU/hr-ft) Conduction/Radiation (BTU/hr-ft) (base/post) | 1100 896/195 143/46.2 | 1600 1331/324 208/67.2 | 2000 1679/427 260/84.0 | Display case Manufacturer Specifications, SCE [455] and ASHRAE RP-1402 report [450] |

A parametric analysis was conducted in CA climate zone 3, using eQUEST/DOE-2.2R, changing one variable at a time, holding all other variables constant (with the exception of coil capacity/infiltration/conduction that were varied together to depict different case styles).  The values displayed in Table 10 are the savings values obtained from subtracting the DOE-2.2R whole building energy use in the measure case from the DOE-2.2R whole building energy use in the base case.  For base case variable sensitivity, the measure energy use is from the expected typical measure value and for measure variable sensitivity the base case energy use is from the typical value.

Table 10 Sensitivity Results

| Variable | Electric Savings (kWh/ft-yr) | Change from typical (%) | Gas Savings (therm/ft-year) | Total Energy Savings (kBTU/ft-yr) | Change from typical (%) |
| --- | --- | --- | --- | --- | --- |
| Typical | 476 |  | 56.3 | 7,257 |  |
| min case supply temp (28 F) | 500 | -5% | 57.9 | 7,496 | -3% |
| max case supply temp (37 F) | 441 | 7% | 54.0 | 6,905 | 5% |
| min lights, base (1 row T8) | 416 | 13% | 57.6 | 7,174 | 1% |
| max lights, base (6 rows T8) | 732 | -54% | 53.6 | 7,859 | -8% |
| LED vertical lights, post | 515 | -8% | 55.9 | 7,351 | -1% |
| T8 vertical lights, post | 367 | 23% | 57.5 | 7,002 | 4% |
| min fan (5 watts/ft) | 477 | 0% | 56.6 | 7,287 | 0% |
| max fan (15 watts/ft) | 476 | 0% | 56.2 | 7,243 | 0% |
| night covers, base | 432 | 9% | 50.9 | 6,560 | 10% |
| increase SST, post (+4 F) | 504 | -6% | 58.9 | 7,611 | -5% |
| add ASH to frame, post | 304 | 36% | 58.8 | 6,917 | 5% |
| max lights base = max light post | 480 | -1% | 56.3 | 7,268 | 0% |
| min lights base=min lights post | 479 | -1% | 56.9 | 7,323 | -1% |
| min coil capacity (1100 BTU/hr-ft) | 499 | -5% | 58.7 | 7,570 | -4% |
| max coil capacity (2000 BTU/hr-ft) | 473 | 1% | 56.1 | 7,225 | 0% |
| nightcovers base, ASH post | 259 | 45% | 53.4 | 6,220 | 14% |

Based on the sensitivity analysis results, lighting power in the base and measure cases, the presence of night covers and the presence of anti-sweat heat in the measure case were identified as key measure variables.

Several manufacturers stated that most retrofits include a switch to more efficient LED case lighting but not an overall increase in lighting power density, so the Terms and Conditions state that the post-case lighting power cannot exceed the pre-case lighting power.  Additionally, two of the three manufacturers interviewed stated that their products did not contain anti-sweat heat in the door or mullion. It was decided to specifically prohibit door and frame heat in the measure terms and conditions as it does not appear necessary in medium temperature applications and negatively impacts energy savings. The limitations on lighting power and anti-sweat heat are outlined in the program terms and conditions.

Night covers are present in a large number of existing open refrigerated display cases. In order to encourage the market to achieve the deeper savings available through retrofitting doors to such cases while accounting for the more efficient base case, two measures were created for each climate zone. The first iteration is based on the energy savings compared to a base case without night covers in place. The second iteration is based on the energy savings compared to a base case where night covers are in place.  The model for night covers assumes that they are deployed for 6 hours a night.

Table 11 displays the final input value and source for each of the values that were changed between the base case and post-implementation versions of the model. The changes were made to 80 ft of display case attached to a multiplex system and 40 ft of display case attached to a single compressor system in a condensing unit as identified in Attachment 3.

Table 11 Model Changes

|  | Base Case |  | Measure Case |  |
| --- | --- | --- | --- | --- |
| Input | Input Value | Source | Input Value | Source |
| Night covers (base case #2) | Multiply infiltration by 0.6 for 6 hrs | SCE report [446] and assumption that store is open 16 hrs/day and stocked for 2 hrs/day [455]. | N/A | N/A |
| Case Infiltration Load (Btu/hr-ft) | 1,331 | Calculation: = coil capacity - light load- motor load - conduction and radiation load. | 324 | Calculation: = 30% base case load - light load- motor load - conduction and radiation load. ASHRAE research and SCE report both measured 70% reduction in load. |
| Case Conduction and Radiation Load (Btu/hr-ft) | 208 | SCE report [446] and ASHRAE refrigeration handbook show 13% of load. | 67 | SCE report shows 14% of load for cases with doors. Load is 30% * base case load. |
| Evaporator Coil to Air dT (F) | 8 | Manufacturer Specification, typical | 4 | Reduction dT because now coil is oversized. SCE measured 6oF reduction. |
| Discharge Air Temperature (F) | 32 | Manufacturer Specification, typical for dairy, deli and beverage open multideck cases | 28 | Reduction in air temperature because now coil is oversized. Assume same coil temperature. |
| Defrost frequency (#/day) | 4 | Manufacturer Specification | 2 | Engineering assumption. Reduction of moist air requires less defrost. |

The base case and post-implementation models for each climate zone are identical with the exception of the changes detailed above.

## 2.1.4 Final Electrical Energy Savings Calculation

The energy savings value was calculated as the difference between the annual whole building electrical consumption output values in the base case and the post-implementation models. The difference was divided by the number of units of measure implementation that were modeled.

Electric Savings kWhUnit=Base Case Usage-Measure Case UsageUnit Count

Electric Savings kWhUnit=1,551,985 kWh-1,494,631 kWh120 ft of case=478kWhft of case

## 2.2. Demand Reduction Estimation Methodologies

The demand savings were derived from the same models that were used to develop the energy savings values. They were calculated as the difference between the peak power demand in the base case and the post-implementation model during the CPUC defined peak demand period for each climate zone. These peak demand periods have been adjusted for the weather data that was used for modeling. The total difference was divided by the number of units of measure implementation that were modeled.

Demand Reduction kWUnit=Base Case Peak kW-Measure Case Peak kWUnit Count

Demand Reduction kWUnit=216.67 kW-209.87 kW120 ft of case=0.05667kWft of case

## 2.3. Gas Energy Savings Estimation Methodologies

Gas savings were determined using the methodology detailed in Section 2.1.

This work paper applies to display cases located within a space with heating, cooling, and humidity controls. The building simulation models were generated for a grocery store. Since the heat gain to a display case mainly depends on the temperature maintained for the display case and the surrounding space temperature, it is assumed that the building types would not have significant impact on the energy savings. Thus, the resulting savings of the grocery store model is applied to all other building types considered in this work paper.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the Refrigeration load shape.  See Table 12 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 12 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Assembly | Assembly | Refrigeration |
| Grocery | Grocery_Store | Refrigeration |
| Food Store | Food_Store | Refrigeration |
| Restaurant - Fast-Food | Fast_Food_Restaurant | Refrigeration |
| Restaurant - Sit-Down | Sit_Down_Restaurant | Refrigeration |
| Retail - Multistory Large | Retail - Multistory Large | Refrigeration |
| Retail - Single-Story Large | Retail - Single-Story Large | Refrigeration |
| Retail – Small | Retail - Small | Refrigeration |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

For an REA measure, the base case cost is zero.

## 4.2 Measure Case Cost

Measure costs were estimated by averaging costs from five medium temperature case door projects representative of the measures in this work paper; these are confidential customer information and available upon request. Since the costs of labor and materials were not shown as individual line items in the project bids, a separate estimation of labor hours and costs was developed. The cost of materials is calculated as the full project cost less the estimated labor cost.

The measure material costs include: doors, door frames, LED lighting, shelving, a new expansion valve, and some additional new piping. The doors, door frames, lighting and shelving is generally sold as a package by the vendor. Based on three quotes from two vendors, these materials average $350.55/ft of case. If required, the expansion valve and piping will generally be installed by a refrigeration contractor working in coordination with the door supplier/installer. The assumptions used to generate the costs for these refrigeration components is that each 8ft refrigerated case will require a new expansion valve and 50 feet of new copper piping.  These assumptions are consistent with PECI’s discussions with a major refrigeration services contractor. The refrigeration components add $139.16/foot of case that it retrofitted. The total materials cost is $456.31/ft of case.

The labor includes time to scope the project, install the doors, alter the refrigeration system, and commission the refrigeration system controls to ensure proper system performance. The installation of the doors and lighting is generally included in the bid from the door vendor. The labor for these activities is estimated to cost $35.24/ft of case. Additionally a refrigeration contractor must often retrofit several system components and commission the applicable controls to maintain performance. Assuming a billable rate of $90/hr and 40 total labor hours for a store with 120 feet of case being retrofitted, this labor amounts to $30/ft of case. The total labor for the implementation of the measure is $65.24/ft of case.

The total measure cost, including all labor and materials required to retrofit the doors and ensure that the refrigeration system is in good functioning order, is $521.55/ft of case. This value does not change when night covers are in place in the base case.

Table 13 Measure Case Costs

| Measure | Equipment Cost | Labor Cost | Full Measure Case Cost |
| --- | --- | --- | --- |
| Add Door to Open Vertical Refrigerated Display Case, Medium Temperature | $456.31 | $65.24 | $521.55 |
| Add Door to Open Vertical Refrigerated Display Case with Night Covers, Medium Temperature | $456.31 | $65.24 | $521.55 |

All costs are per foot of case.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For REA measures, the customer is replacing equipment that is still functional and has remaining useful life. Therefore the gross measure cost is the full measure cost as shown in Table 13: $521.55.

### 4.3.2 Incremental Measure Cost

For REA measures, the incremental measure cost is the same as the gross measure cost: $521.55.
Attachments

# References

| [31] | Load Shape Update Initiative - KEMA / JJ Hirsch and Assoc. / Itron Inc. - November 17, 2006 |
| --- | --- |
| [351] | Energy Efficiency Policy Manual-Version 5 |
| [393] | Code of Federal Regulations Title 10 - Energy |
| [435] | ANSI/AHRI Standard 210/240: 2008 Standard for Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment |
| [436] | 2014 DEER EUL Table - Update |
| [446] | Performance and Energy Impact of Installing Glass Doors on an Open Vertical Deli/Dairy Display Case |
| [447] | Vertical Display Case Cabinets without and with Doors |
| [448] | Supermarkets, indoor climate and energy efficiency – field measurements before and after installation of doors on refrigerated cases |
| [449] | Glass covers on refrigerated display cabinets: Field measurement of energy savings |
| [450] | Comparison of Vertical Display Cases: Energy and Productivity Impacts of Glass Doors Versus Open Vertical Display Cases |
| [451] | Inventory of Direct and Indirect GHG Emissions from Stationary Air Conditioning and Refrigeration Sources, with Special Emphasis on Retail Food Refrigeration and Unitary Air Conditioning |
| [452] | Development of the Advanced Energy Design Guide for Grocery Stores |
| [453] | Commercial Facilities Contract Group, 2006-2008 Direct Impact Evaluation |
| [454] | Developing Building Energy Use Intensity Benchmarks for Standard 100 Energy Targets |
| [455] | Effects of the Low Emissivity Shields on Performance and Power Use of a Refrigerated Display Case |

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |