Work Paper SCE13WP001

Revision 2

Southern California Edison Company

Residential Variable Speed Swimming Pool Pump

# At-a-Glance Summary

| Applicable Measure Codes: | PM-69234: Commissioned Variable Speed Drive on Pool Pump Controls replacing Single Speed Pool Pump PM-78394: Commissioned Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump PM-79353: Programmable Variable Speed Drive on Pool Pump Control replacing Single Speed Pool Pump PM-80567: Variable Speed Drive on Pool Pump Control replacing Manually Controlled Two Speed Pool Pump PM-98422: Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump |
| --- | --- |
| Measure Description: | Variable speed pool pump. |
| Base Case Description: | Customer existing single speed pool pumps and code required two speed pool pumps. |
| Energy Impact Common Units: | Per pump. |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | 10 years (OutD-PoolPump) |
| Measure Application Type: | Early Retirement (RET), & Replace on Burnout (ROB). |
| Net-to-Gross Ratios: | 0.55 (Res-Default>2) 0.85 (Res-Default-HTG-di) |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13WP001.0 | No | 05/30/2012 | Ricardo Sfeir/BASE Energy, Inc. | Original work paper template for 2013 based on the work paper from the previous cycle. |
| SCE13WP001.1 | No | 8/29/2012 | Alfredo Gutierrez/SCE | Updated the work paper with a SDG&E study on multi-family pool pump retrofits. The multi-family values have been updated per the study. |
| SCE13WP001.2 | Yes | 6/9/2014 | Alfredo Gutierrez/SCE | -Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. -Updated work paper to the latest template. -Updated 2nd baseline costs for all RET measures. |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper describes Southern California Edison (SCE) calculations and methodologies related to energy savings and demand reduction values for variable-speed pool pumps for single family and multifamily homes.

The following five measures are evaluated in this work paper (designated as Measure A, Measure B, Measure C, Measure D, and Measure E for clarity):

- Measure A (PM-78394):

Commissioned Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump.

The measure case is variable speed swimming pool pumps that are programmed to operate outside peak hours (noon to 6 P.M.) as part of a contractor driven offer.

- Measure B (PM-98422):

Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump.

The measure case is variable speed swimming pool pumps that are not explicitly programmed.

- Measure C (PM-69234):

Commissioned Variable Speed Drive on Pool Pump Controls replacing Single Speed Pool Pump.

The measure case is variable speed swimming pool pumps that are programmed to operate outside peak hours (noon to 6 P.M.) as part of a contractor driven offer.

- Measure D (PM-79353):

Programmable Variable Speed Drive on Pool Pump Control replacing Single Speed Pool Pump in Multifamily Buildings. The measure case is operating the variable-speed pump to meet the minimum required health code requirements of one turn over every 6 hours.

- Measure E (PM-80567):

Variable Speed Drive on Pool Pump Control replacing Manually Controlled Two Speed Pool Pump in Multifamily Buildings. The measure case is installing a variable-speed pump in place of a manually controlled two-speed pump when an existing pump burns out.

The base case for this work paper is single-speed and/or two-speed swimming pool pumps as indicated below.

For Measure A, 95% of savings is assumed to be from single-speed pumps as the base case. The remaining 5% of savings is with two-speed pumps as the base case. These percentages are conservative estimates from SCE based upon likely market penetration of two speed pumps after roughly one and one half years.

For Measure B, 100% of the savings is with the base case of two-speed pumps.

For Measure C, 100% of the savings is with the base case of single-speed pumps.

For Measure D, 100% of the savings is with the base case of single-speed pumps.

For Measure E, 100% of the savings is with the base case of a manually controlled two-speed pump continuously operating at full speed.

Variable-speed pool pumps can lower daily electricity usage and can be programmed with explicit timing and flow rates to both minimize kWh and shift the 1-hour or 2-hour, high-speed cycle to an off-peak period to reduce demand.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| PM-69234 | Commissioned Variable Speed Drive on Pool Pump Controls replacing Single Speed Pool Pump |
| PM-78394 | Commissioned Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump |
| PM-79353 | Programmable Variable Speed Drive on Pool Pump Control replacing Single Speed Pool Pump |
| PM-80567 | Variable Speed Drive on Pool Pump Control replacing Manually Controlled Two Speed Pool Pump |
| PM-98422 | Variable Speed Drive on Pool Pump Controls replacing Two Speed Pool Pump |

Measures A, B, C, D, and E require replacing an existing pool pump with a qualified energy efficient variable speed pool pump. For a list of qualified variable speed pool pumps please refer to the SCE Qualified Variable Speed Pool Pump and Motor - Products List. For models that require an automatic control system capable of controlling both high and low speeds, a controller must be installed.

Measures A, B and C are applicable only for single family homes in the Southern California Edison service territory. Measures D, and E are only applicable for multifamily homes in the Southern California Edison service territory. In order to qualify for the downstream deemed portion of Measure D, a contractor is required to be onsite in order to verify that the base case pool pump is single speed, as well as to ensure that the programming of the variable speed pump is done correctly. The downstream – deemed portion of Measure D is contractor driven.

Home Energy Efficiency Rebate Program

- Variable-speed pool pump and motor must be a new qualifying product installed in a pre-existing or new in-ground pool. Note: Pool pumps installed in a spa or jacuzzi do not qualify for a rebate.

- Pool pump must be installed at a single family residence.

- For those pool pumps that require a qualifying controller, the controller must be from the list of qualifying controllers found on www.sce.com/rebates.

- Proof of purchase must be provided with your application.

- Only one Variable-speed pool pump and motor rebate per residence.

## 1.2 Technical Description

Variable speed pool pumps allow the reduction of power consumption by running the motor at slower speeds than actually needed to perform a task. The speed is able to modulate based on schedule, or load based on the type of feedback control tied into the variable speed pool pump. This is in contrast to single or multi-speed pool pumps which run at either a constant speed or have stepped speed levels, typically two-speeds.

## 1.3 Measure Application Type

Note: See Appendix A for a comparison of the application types used by and incorporated into SCE systems versus the application types available in the newest revision of DEER 2014. Appendix A will serve as a translation between the outputs of this workpaper and application types used by READi.

For Measure A and Measure C, the measure install type is Retrofit (Ret) and the delivery method is Financial Support – Direct Install. For this delivery method, the pumps are delivered as early retirement measures. Contractors are required to follow prescribed approaches to program the pump controller to avoid all on peak usage and to ensure that the turnover ratio is reduced to be one turnover per day, or the minimum required by applicable local codes.

For Measure B, the measure install type is Replace on Burnout (ROB) and the delivery method is Financial Support – Downstream Incentive – Deemed.

For Measure D, the measure install type is Retrofit (RET) and the delivery method is Financial Support – Direct Install and Financial Support – Downstream Incentive – Deemed.

The downstream – deemed portion of this measure for multi-family is contractor driven, where the baseline pump will be verified to be a single speed pump. The contractor will be trained and will commission the pump as directed by SCE.

For Measure E, the measure install type is Replace on Burnout (ROB) and the delivery method is Financial Support – Downstream Incentive – Deemed.

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

These measures are not contained within the DEER 2014 READI tool. However, the DEER 2005 [49] database for non-weather sensitive residential measures provides the following values for two-speed pool pumps, 1.5 hp, compared to the base case of single-speed pool pumps, based on an average 25,000 gallon residential single-family swimming pool:

- Electricity savings of 1,400 kWh per pool pump per year

- Peak electric demand impact of 540 watts per pool pump per year

- Measure life of 10 years

The DEER 2005 does not have a variable-speed pool pump measure. Like the DEER, this work paper uses a single-speed pool pump as the existing base case for Measure C, Measure D, and part of Measure A’s savings estimates. Unlike the DEER, savings estimates for two-speed pumps and variable-speed pumps are taken from a variety of sources including data from 491 Pentair IntelliFlo variable-speed pump installations from the InDEE Program and pump test results from the CEC Appliances Database.

This work paper provides savings estimates using single-speed and/or two-speed pool pumps as a base case. The savings estimates for variable-speed pumps are from InDEE Pentair data and the EC&C database.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | No |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER 2014 does not contain a variable speed pool pump measure |
| DEER Version | N/A |
| DEER Run ID and Measure Name (Sample) | N/A |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | Any | 0.55 |
| Res-Default-HTG-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis. This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the residential defaulted NTG value, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID* | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Spillage Rate

Spillage rate will also be applied to measures however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measures in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Values included in this workpaper |
| --- | --- |
| Measure Case UseCategory | Recreation |
| Measure Case UseSubCats | Pool |
| Measure Case TechGroups | Non-DEER |
| Measure Case TechTypes | Non-DEER |
| Base Case TechGroups | Non-DEER |
| Base Case TechTypes | Non-DEER |

### 1.4.2 Codes and Standards Analysis

There are no federal regulations governing the energy efficiency of residential swimming pool pumps. However, 2014 Title 20, Section 1605.3 of California’s Appliance Efficiency Regulations [422] requires that, effective January 1, 2008, all 1-horsepower or greater residential pool pumps sold in California shall have the capability of operating at two or more speeds, with a low speed rotation rate of no more than one-half of the motor’s maximum rotation rate. Title 20 [422] further requires that pool pump motor controls shall have the capability of operating the pump at a minimum of two speeds, and that the default circulation speed shall be the lowest speed, with a high speed override capability being for a temporary period not to exceed one normal cycle.

In other words, effective January 1, 2008, California’s minimum requirement for residential pool pumps will be two speeds, with two-speed controls. The sale of single-speed pool pumps will be prohibited, except for 0.5 hp or 0.75 hp models, which together comprised approximately ten percent of the residential pool pumps in the SCE service territory in 2001, per Section 3.1 of the Evaluation of Year 2001 Summer Initiatives Pool Pump Program report [A]. Upon burnout, these small pool pumps may be replaced by single-speed models. One notable exception to the Title 20 regulation is that single-speed pumps manufactured prior to January 1, 2008; meet the minimum requirement for residential pool pumps. Although the exact number of such pumps on the market is unknown, informal interviews with 20 pool pump vendors, in early summer of 2008, indicate that these pumps may presently have up to 60% of market share.

The 2013 Title 24 Building Energy Efficiency Standards [355] does require that any residential pool system or equipment installed shall comply with the applicable requirements of Section 110.4 as well as the following:

- Pump sizing and flow rate.

  - All pumps and pump motors installed shall be listed in the Commission’s directory of certified equipment and shall comply with the Appliance Efficiency Regulations.

  - All pump flow rates shall be calculated using the following system equation:

H= C x F2

WHERE:

H is the total system head in feet of water.

F is the flow rate in gallons per minute (gpm).

C is a coefficient based on the volume of the pool:

0.0167 for pools less than or equal to 17,000 gallons.

0.0082 for pools greater than 17,000 gallons.

  - Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater; and

  - Pump motors used for filtration with a capacity of 1 hp or more shall be multi-speed; and

  - Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multi-speed pump; and

EXCEPTION to Section 150.0(p)1E: Pumps less than 1 hp may be single speed.

  - Multi-speed pumps shall have controls which default to the filtration flow rate when no auxiliary pool loads are operating; and

  - For multi-speed pumps, the controls shall default to the filtration flow rate setting within 24 hours and shall have an override capability for servicing.

The Center for Disease Control requires a 6 hour turnover rate for swimming pools according to their Healthy Housing Reference Manual [B]. Most health codes impose the same requirement for commercial applications, including multi-family housing.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 20 (2014) | Section 1605.3 | January 2008 |
| Title 24 (2013) | Section 150.0(p)1 | July 2014 |

### 1.4.3 Non-DEER Study Review

This work paper uses data gathered by SCE’s Measurement and Evaluation team specific to residential homes within climate zone 15. Over 600 sites were selected where data was collected by site visits and metering of the existing pool pumps. A few of the variables measured for both existing and measure pool pumps were as follows:

- Pool pump size (hp)

- Pool size (gallons)

- Flow rate (gpm)

Savings for the residential pool pump measures utilizes the data collected [attachment 2] as part of this effort.

Specific to the multi-family sector, a 2012 study by SDG&E [attachment 7] looked at the savings associated with replacing single speed pool pumps with variable speed pool pumps at two sites. The first site had two (2) single speed pool pumps with 1 hp motors while the second site had one 2 hp pool pump and one ¾ hp spa pump. Savings for multifamily pool pump measures are based on this study [attachment 6].

### 1.4.4  Measure and Base Case Effective Useful Life

DEER14 update documentation provides EUL and RUL information to be used for the 2013-14 program cycle on www.deeresources.com. The DEER documentation “DEER2014-EUL-table-update_2014-02-05.xlsx” provides the RUL value as a flat 1/3 of the EUL value. The RUL value will only be applied to the first baseline period for retrofit measures that have applicable code that will affect the energy savings. In all other installation types and retrofit with no applicable code that affects the energy savings, the RUL is not applicable to either the first or second baseline period.

To obtain the EUL value the DEER14 update documentation, “DEER2014-EUL-table-update_2014-02-05.xlsx” [436], was consulted. Table 7 below identifies the value/methodology used for the measures in this work paper.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| OutD-PoolPump | Res | Recreation | High Efficiency Pool Pump | 10 | 3.3 |

# Section 2. Energy Savings & Demand Reduction Calculations

The energy savings data contained in the SCE Emerging Technologies assessment report [C] indicates that variable-speed pool pumps, particularly those with flow-based programming capabilities, such as Pentair IntelliFlo pumps [D], will provide more consistent and predictable energy savings than two-speed pool pumps. For Measure B, variable-speed pool pumps may also provide more reliable peak demand reduction than two-speed pumps. For Measure A and Measure C, demand reduction is realized from programming the variable-speed pumps to not operate during peak hours (noon to 6 P.M.).

For Measures D and E the energy savings are utilize an SDG&E study [E] which examined the retrofit of single speed pool pumps with variable speed pool pumps.

Approximately 500 records of Pentair IntelliFlo pump installations, in the 2006-2008 InDEE Program, were thorough enough to enable a comprehensive energy and demand analysis of the variable-speed pumps. In addition to recording data regarding pool size and piping type and diameter, the pump installation contractors recorded the flow-rate in gallons per minute (gpm) and the instantaneous power in kW for the pool pumps. Some relevant findings of the analysis are:

- The average flow rate during filtering is 28 gpm at a motor speed of 1,609 rpm. The average duration of daily filtering is 12 hours.

- The energy usage per volume of water filtered is only slightly less at 15 gpm than at 28 gpm. The energy usage per volume of water filtered actually increases as flows decrease below 13 gpm.

- Although the pump power at 15 gpm is about half of that at 28 gpm, the total peak coincident demand for a large sample of pumps is about the same at 15 gpm and at 28 gpm. The reason for this is that the coincidence factor is expected to climb from a measured 0.51 at 28 gpm to 1.0 at 15 gpm.

- A power vs. flow curve has been constructed from data representing 424 Pentair IntelliFlo pumps installed in SCE service territory. This curve differs significantly from the two curves used by the CEC to rate the efficiencies, or Energy Factors, of swimming pool pumps. Due to the nearly constant efficiency of the Pentair pump motors (~92%) at all RPM, this curve can be used to estimate the power required to achieve a certain flow rate for the pool stock in SCE service territory for any pump, so long as the motor efficiency is known.

To supplement the Pentair IntelliFlo pump installation data above, 20 pool pump installers were contacted and interviewed regarding pump sales, service factors, and operating hours in early summer of 2008. The installers reported the following information:

- The overwhelming majority of installers do not consider service factor, and tend to match one-speed and two-speed pool pumps on a nameplate horsepower basis. Due to the lack of attention paid to service factor and also because the variation in service factor across many market-available pumps is not dominatingly large, service factor is treated as a nuisance variable in the analysis herein. Note that the CEC Appliance Database [F] reports an average service factor of 1.24 and a standard deviation of 0.24 for one-speed pumps.

- About 63% of all pump sales were attributable to single-speed pumps. Two-speed pumps comprise just 16% of sales, while variable-speed pumps reportedly account for 22% of sales. A small minority of vendors (1/5) attribute 75% or more of their sales to multi-speed pumps.

- The average run times reported for single-speed, two-speed, and variable-speed pumps are 6.0, 11.3, and 14.6 hours. These numbers are slightly higher than those reported by EM&V studies and monitored data.[F],[A]

EC&C installation Data [Attachment 2] in CZ 15 indicates that there are greater energy savings when the variable speed pool pumps were programmed per the specifications listed in Table 8 below. Data were collected by site visits and metering. The following chart was used to determine program settings for the programmed variable speed pool pump. (See Attachment 3 for more detail). The controller was programmed to run the pump outside of the noon to 6 PM timeframe to achieve greater kW reduction.

The measures in this work paper apply for “Any” vintage and for “Any” HVAC system types.

Table 8  Programmed Specifications for Climate Zone 15

| Pool Size | High Speed |  | Low Speed |  |
| --- | --- | --- | --- | --- |
|  | Variable-Speed Pump | Number of hours | Variable-Speed Pump | Number of hours |
| (gallons) | (gpm) |  | (gpm) |  |
| 10,000 | 50 | 2 | 20 | 3.3 |
| 15,000 | 50 | 2 | 20 | 7.5 |
| 20,000 | 50 | 2 | 20 | 11.7 |
| 25,000 | 50 | 2 | 20 | 15.8 |
| 30,000 | 50 | 2 | 25 | 16.0 |
| 35,000 | 50 | 2 | 30 | 16.1 |

## 2.1 Energy Savings Estimation Methodologies

The calculation procedure for the energy savings estimation is outlined below:

- Obtain the average pool size in SCE territory

- Obtain average single, two, and variable-speed pump size and efficiency

- Obtain the average number of pool water turnovers per day

- The calculation for annual energy usage is shown in Equation 1.

Equation 1

EU	=	V × T × D / EFF × C

Where,

EU	=	annual energy usage, kWh/year

V	=	pool size, 20,341 gallons

T	=	number of turnovers per day, no units

D	=	average number of days in a year (including leap year for Measure B),

365 day/yr (Measure A and C, from EC&C database Attachment No.2), 365.25 day/yr (Measure B)

EFF	=	Energy Factor, gallons/W-hr

C	=	conversion factor, 1,000 W/kW

The determination of the work performed by the pump depends on the amount of water pumped and on the overall hydraulic performance of the pool-pump system. The pool pump Energy Factor accounts for the hydraulic performance of a typical swimming pool as discussed in the next section.

## 2.1.1 Pool Hydraulic Performance

Swimming pool hydraulic performance is characterized by system curves that show the resistance presented to the flow of water as a function of flow rate. This resistance is comprised of static head pressure, which does not change as flow changes, and dynamic head pressure, which increases in proportion to the square of flow rate.

The hydraulic performance of a typical swimming pool (i.e., a pool with 2-inch PVC plumbing and a diatomaceous earth filter) is represented by the California Energy Commission’s Curve A [G]. Curve A is defined by a mathematical relationship between the flow rate and system head. Curve A is symbolically written as:

#### CEC Curve A

H	=	0.0167 × F2

Where,

H	= 	total system head, ft of water

F	=	flow rate, gpm

The CEC also specifies a Curve B. This curve shows a higher dynamic head pressure and is suited for older pools (e.g., 1.5” copper piping). Curve B is symbolically written as:

#### CEC Curve B

H	=	0.05 × F2

Where,

H	= 	total system head, ft of water

F	=	flow rate, gpm

Figure 1 shows the CEC system curves A and B. Note that the resistance for these curves tend to zero at very low flows. These theoretical curves correspond to zero static head pressure at low flows. Curve A is chosen by PG&E in their pool pump work papers because “it has been shown to be representative of the swimming pool market” [H]. Indeed, 94% of the 975 swimming pools encountered in SCE’s InDEE Pentair installation program had PVC piping, and the majority of the pools pipe diameters were 2 inches or larger.

Figure 1 CEC System Curves Representing Typical Residential Pools.

#### InDEE Curve

Figure 2 shows power, in watts, versus flow rate in gpm for Pentair IntelliFlo 3-hp variable-speed pool pumps installed as part of the SCE 2006-2008 InDEE program. Note that the CEC power versus flow curves A and B correspond to the pump operation of the CEC pressure vs. flow curves A and B, respectively, and are recreated from the SCE Emerging Technology assessment report [I]. Although the InDEE Program data comes from the LCD displays on the pump controllers, and not from direct monitoring, the LCD display information was shown to be in good agreement with monitoring equipment [D]. In this plot, test data from Pentair for Curves A and B are shown in green triangles and red squares, respectively. The InDEE Pentair installation data are represented by the blue diamonds. Each point represents the average power for at least ten pool pumps configured to run at the given flow rate. The first data point in particular, at 15 gpm and 193 W, represents 53 swimming pools. The average pump speed for this sample of 53 pools is 1,228 RPM. About 90% of these pools have 2-inch PVC suction and discharge pipes, and the remaining 10% have 1.5-inch copper pipes. This suggests that this sample of 53 pools is a good candidate to be represented by Curve A. However, CEC Curve A predicts 100 W at 15 gpm, and according to the appliance database, 130 W at 22 gpm and 1,000 RPM.

Figure 2 Pump power vs. flow rate measured for a single pump. In this profile, each data point represents at least 10 swimming pool pumps.

The curve that represents the InDEE Pentair installations is adequately represented by the quadratic equation, Equation 2:

Equation 2

P	=	0.1430 F2 + 8.4780 F + 32.8173

Where,

P	=	power, Watts

F	=	flow rate, gpm

Equation 2 is derived from data that best represent the market segment targeted by this measure. The curve represented by this equation is in good agreement with a recent SCE ET assessment on variable-speed pool pumps [D]. Note that the curve represented by Equation 2 (for simplicity, called the InDEE Curve hereafter) is not altogether dissimilar to Curve A, but seems to have a substantial offset. This offset may be due to the static head pressure associated with the pool/pump setup (e.g., intake, pump, and discharge locations are at varying heights). Both CEC Curve A and CEC Curve B are simply related to the square of the flow rate, and tend to zero as the flow decreases to zero. As such, they do not account for static head pressure. The InDEE Curve can be understood as a modified version of Curve A that accounts for the average dynamic and static head pressures for pools in SCE service territory.

## 2.1.2 Pool Pump Energy Factor

The parameter that describes pump energy efficiency performance is the Energy Factor, which is defined as flow rate divided by power and symbolically written as in Equation 3.

Equation 3

EFF	=	F × C2 / P

Where,

EFF	=	Energy Factor, gallons/W-hr

F	=	flow rate, gpm

C2	=	conversion constant, 60 min/hr

P	=	power, Watts

The energy usage can be obtained by dividing the volume of pumped water by the Energy Factor as shown in Equation 1. Energy Factor and energy consumption are inversely related and thus a higher Energy Factor is preferred from an energy efficiency perspective. This figure of merit is posted on the CEC web site for over 200 single-speed, two-speed, and variable speed pumps [A]. Note, however, that, because these Energy Factors are based on the CEC curves that do not account for static head pressure, they are likely to underestimate power usage at low flow rates. According to Figure 2, the power/flow ratios for the InDEE Curve and CEC Curve A are quite different at low flows, but should be in good agreement for high flow rates (50-60 gpm).

#### Energy Factors for Variable-Speed Pumps

The Energy Factors for variable-speed pool pumps are obtained directly from Equation 3.

For example, the Energy Factor for a variable-speed pump at 15 gpm and 192.2 Watts (using Equation 2) is 4.68 gallons per watt-hour, as shown in the calculation below. The flow and power are obtained from the InDEE Curve, essentially by substituting Equation 2 for power in Equation 3.

EFF	=	(15)(60)/(192.2)

EFF	=	 4.68 gal/W-hr

The power and Energy Factors of variable-speed pumps are listed for a variety of flow rates in Table 9. Note that the Energy Factor peaks at approximately 15 gpm. From a pure energy efficiency perspective, there seems to be no advantage to operate below 15 gpm. This phenomenon is also demonstrated in a plot the Pentair IntelliFlo Owner’s Manual [J]. For example, at 690 rpm, one may increase the flow at no apparent cost in power. At very low flows, then, the Energy Factor increases with flow rate.

Table 9 Flow, Power, and Energy Factors 
for Pentair 3-hp Variable-Speed Pumps

| Flow (gpm) | Power (W) | Energy Factor (Gallons/W-h) |
| --- | --- | --- |
| 5 | 78.8 | 3.81 |
| 10 | 131.9 | 4.55 |
| 15 | 192.2 | 4.68 |
| 20 | 259.6 | 4.62 |
| 25 | 334.1 | 4.49 |
| 30 | 415.9 | 4.33 |
| 35 | 504.7 | 4.16 |
| 40 | 600.7 | 4.00 |
| 45 | 703.9 | 3.84 |
| 50 | 814.2 | 3.68 |
| 55 | 931.7 | 3.54 |
| 60 | 1056.3 | 3.41 |

#### Energy Factors for Two-Speed Pumps

The Energy Factors for 66 two-speed pool pumps are listed in the CEC Appliance Database. The average nameplate horsepower for all two-speed pumps is 1.73 hp. An informal survey of 20 pool installers in SCE territory indicated that, when replacing a single-speed pool pump with a two-speed, the installers tend to match nameplate horsepower. Therefore, the 1.73 hp average two-speed pool pump listed in the CEC database is well-matched to the average 1.75 hp baseline single-speed pump encountered in the SCE InDEE Program [F]. As mentioned, the Curve A values are appropriate for high flow rates, but not at lower flow rates. However, according to field data (Figure 2), CEC Curve B intersects the InDEE Curve at approximately 22 gpm. The Energy Factors for the two-speed pumps at low speed are listed in the CEC database for an average flow of 20.7 gpm. The InDEE Program data shows that Curve B and the InDEE Curve are in good agreement at flow rates near 20.7 gpm. Due to the proximity of Curve B and the InDEE Curve at this flow rate, the Energy Factors listed under Curve B in the CEC Appliance Database are used for two-speed pumps at low speed.

- The average Energy Factor for all two-speed pumps over 1 hp at low speed (21 gpm) on Curve B is 3.39 Gallons/Watt-hour.

- The average Energy Factor for all two-speed pumps over 1 hp at high speed (65 gpm) on Curve A is 2.06 Gallons/Watt-hour.

Note that the above Energy Factors are significantly lower than those of the Pentair IntelliFlo pumps at equivalent flows. The main reason is that the IntelliFlo pumps have more efficient motors than the typical two-speed pool pumps.

#### Energy Factors for Single-Speed Pumps

The energy factor equation for single-speed pumps, Equation 4, was developed from a plot of Energy Factors against nameplate horsepower for 108 single-speed pool pumps listed in the CEC Appliance Database [A].

Equation 4

EFF	=	0.0838 × HP2 – 0.8188 × HP + 3.3477

Where,

HP	=	horsepower, hp

The average rated horsepower for pool pumps in SCE territory is estimated from the 2006-2008 InDEE Program Pentair install records.

The InDEE Program data is favored over other available data for two reasons:

- The data contains records on 975 installations, making it one of the largest datasets on VSD pool pumps. The large size enables strict quality control – after removal of all incomplete or suspect records, 491 records remain. The next largest dataset [K] contains 146 measurements on single-speed pumps rated at or above 1 hp in SCE territory.

- The InDEE Program is specifically designed for VSD retrofits. As such, the program records comprise perhaps the most pertinent dataset available for this measure. The great advantage is that any correlations between the likelihood to install VSD pumps and pool sizes, baseline pump capacities and efficiencies, are likely to be captured by this data.

According to the InDEE Program data, the average horsepower rating of the replaced single-speed pump is 1.73 with a standard deviation of 0.46. The Energy Factor for the average pool pump in SCE territory can be obtained from Equation 4 with the average hp:

EFF	=	(0.0838)(1.73)2 – (0.8188)(1.73)+(3.3477)	=	2.18 gal/W-hr

This Energy Factor is comparable to an Energy Factor of 2.02 that is calculated from a sample of seven 1.5-hp pumps in a recent SCE Emerging Technology assessment of pool pumps [D].

#### Annual Work Load

The annual work load is the total gallons of water that is circulated yearly by the pump. The 491 InDEE records show an average of 0.993 turnovers per day. In this work paper it is assumed that single-speed, two-speed, and variable-speed pumps perform the same amount of work per year – equivalent to 1.00 turnovers per day on a 20,341-gallon pool. Although the energy savings scale with the amount of turnovers, demand reductions are not directly dependent on the number of turnovers per day.

#### Variable Speed Operation

Filtration pumps may provide pressure for pool sweeps or for backwashing diatomaceous earth filters. In some cases, additional booster pumps are installed to provide the additional pressure. Most market-available variable speed pool pumps are rated at 3 hp and should have sufficient power to perform these tasks without the need for booster pumps [L]. The data from the InDEE Program sites fall into two distinct categories:

The pool pumps are used for filtration purposes only.

- The pumps are used for filtration and for performing pool sweeps and/or filter backwashing.

Of the 491 sites considered in the following calculations, about 94.4% (not 94.4% of sites, but 94.4% of sites weighted by pool volume) fall into the first category, and 5.6% of the sites (by pool volume) fall into the second category.

Table 10 lists the monitored data (except for Average kW column, which is calculated with Equation No.3) from the InDEE Program installations for the various operational modes. The first usage mode consists of 12.19 hours of pumping at 28.6 gpm. The second usage mode pumps 13.21 hours at 20.7 gpm and an additional 2.79 hours at 45.4 gpm. The Energy Factors for usage modes 1 and 2A are taken from the fit to InDEE Program data (Table 9), while the Energy Factor for mode 2B (pool sweeps) is taken directly from the data, because the InDEE Curve describes the power vs. flow relationship during filtering, not during pool sweeps. Note that the Energy Factor of 3.0 at 45.4 gpm is lower than the corresponding value (3.81) listed in Table 9. This is expected, and indicative of the excess loads that the pump experiences while assisting in pool sweeps. The fact that the InDEE data captures this phenomenon suggests that a significant proportion of the participating pool technicians properly recorded the power associated with this mode (instantaneous power usage can be read from the LCD display).

Table 10  Data from InDEE sites Using Variable-Speed Pumps for Pool Sweeps 
and Filter Backwashing

| Mode | Average RPM | Average kW | Average Hours | Average gpm | Average Energy Factor | Average Pool Turnovers |
| --- | --- | --- | --- | --- | --- | --- |
| Mode 1: Filtering Only | 1,615 | 0.393 | 12.19 | 28.6 | 4.37 | 0.98 |
| Mode 2A: Filtering | 1,361 | 0.269 | 13.21 | 20.7 | 4.61 | 0.86 |
| Mode 2B: Pool Sweeps | 2,317 | 0.908 | 2.79 | 45.4 | 3.00 | 0.37 |

The sites that ran the variable speed pumps at a constant low speed averaged 0.98 turnovers per day. The sites that used the variable speed pumps to perform pool sweeps averaged 1.23 turnovers per day. The weighted average across all sites is 0.994 turnovers per day, which is rounded to unity for simplicity.

Please be aware that Table 10 considers non-programmed variable-speed pumps, which is the measure case for Measure B. The measure case for Measure A and C in this work paper includes variable-speed pool pumps that will be programmed to operate outside the noon – 6 P.M. time frame. The measure case electrical energy consumption for Measure A and C is based on the analyses provided in the EC&C database (Attachment No.2), which includes measured data for one 18,000 gallon pool with a 1 hp variable-speed pool pump located in Climate Zone 15. The electrical energy savings for Measure A and Measure C is extrapolated for the rest of the climate zones (6, 8, 9, 10, 13, 14, and 16) using the methodology in Attachment No.4, One Stop Shop Beyond CZ 15 Analysis.

Before calculating the annual energy savings, the calculation inputs per measure have been summarized below:

Measure A

- Pool size is 18,000 gallons

- The average pool experiences 1.00 turnover per day

- For two-speed, 94.4% of sites (by pool volume) filter 0.98 turnovers per day.  The remaining 5.6% of sites (by pool volume), filter 0.86 turnovers at low speeds, and perform pool sweeps for an additional 0.37 turnovers per day.

- The average Energy Factor for single-speed pumps is 2.18.

- The average Energy Factor for two-speed pumps is 3.39 at 21 gpm (low speed, from CEC Appliance Database), and 2.06 at 65 gpm (high speed, from CEC Appliance Database).

- The electrical energy consumption for programmable variable-speed pumps is 1,257 kWh/yr in Climate Zone 15 (EC&C database, Attachment No.2).

- Electrical demand reduction factor is 0.692 (Attachment No.4).  Energy and Demand reduction factors are used to adjust for all other SCE climate zones (6, 8, 9, 10, 13, 14, and 16).

- Since this measure is a Retrofit (RET) measure, it is subject to dual baselines. Baseline 1 considers single speed pumps operating at full speed and two speed pumps operating at full and reduced speed. Baseline 2 considers 2-speed pumps operating at both reduced speed and full speed as needed since new code requires 2-speed pumps.

Measure B

- The average pool size is 20,341 gallons

- The average pool experiences 1.00 turnover per day

- For two-speed and variable-speed pumps, 94.4% of sites (by pool volume) filter 0.98 turnovers per day. The remaining 5.6% of sites (by pool volume), filter 0.86 turnovers at low speeds, and perform pool sweeps for an additional 0.37 turnovers per day.

- The average Energy Factor for two-speed pumps is 3.39 at 21 gpm (low speed, from CEC Appliance Database), and 2.06 at 65 gpm (high speed, from CEC Appliance Database).

- The average Energy Factor for non-programmed variable-speed pumps is 4.37 at 28.6 gpm for sites that perform steady-state filtering only.

- For sites that perform both filtering and pool sweeps, the average Energy Factors for non-programmed variable-speed pumps are 4.61 and 3.00 for filtering and pool sweeps, respectively.

Measure C

- Pool size is 18,000 gallons

- The average pool experiences 1.00 turnover per day

- The average Energy Factor for single-speed pumps is 2.18.

- The electrical energy consumption for programmable variable-speed pumps is 1,257 kWh/yr in Climate Zone 15 (EC&C database, Attachment No.2).

- Electrical demand reduction factor is 0.692 (Attachment No.4).  Energy and Demand reduction factors are used to adjust for all other SCE climate zones (6, 8, 9, 10, 13, 14, and 16).

- Since this measure is a Retrofit (RET) measure, it is subject to dual baselines. Baseline 1 considers single speed pumps operating at full speed. Baseline 2 considers 2-speed pumps operating at both reduced speed and full speed since new code requires it.

Measure D

The savings for this measure are based on the 2012 Multi-Family Residential Variable Speed Swimming Pool/Spa Pump Retrofit study prepared by Information & Energy Services, Inc. for SDG&E [E]. This study looked at the savings associated with replacing single speed pool pumps with variable speed pool pumps at two sites. The first site had two (2) single speed pool pumps with 1 hp motors while the second site had one 2 hp pool pump and one ¾ hp spa pump. Please note that the savings for the spa pump were not taken into account for this work paper.

The assumptions shown below were used in the previous revision of this work paper to calculate the energy savings for running the pool pumps at reduced flow during nighttime operation. The SDG&E study [E] investigates pool pump savings throughout the entire day, not only at night as was assumed in the previous revision, so there will be some demand savings associated with this measure. The assumptions have been left in the work paper to compare the calculated energy savings (based on the EC&C database and general assumptions) with the savings given in the SDG&E study [E].

- Average pump size in the EC&C database (Attachment No. 2), 1.49 hp

- Average pump input power in the EC&C database (Attachment No.2), 2.155 kW

- Average Pump size in the multifamily building pool pump survey (Attachment No. 5), 1.77 hp

- Number of hours pool is expected to be closed (12 h/day, 365 days/yr), 4,380 h/yr

- Expected pump load factor at 20% speed, 0.142 [M] no units

- Since this measure is a Retrofit (RET) measure, it is subject to dual baselines. Baseline 1 considers single speed pumps operating at full speed. Baseline 2 considers pumps operating at both reduced speed (50% speed) and full speed since new code requires installing two speed pool pumps.

Measure E

The savings for this measure are based on the 2012 Multi-Family Residential Variable Speed Swimming Pool/Spa Pump Retrofit study prepared by Information & Energy Services, Inc. for SDG&E. This study looked at the savings associated with replacing single speed pool pumps with variable speed pool pumps at two sites. The first site had two (2) single speed pool pumps with 1 hp motors while the second site had one 2 hp pool pump and one ¾ hp spa pump. Please note that the savings for the spa pump were not taken into account for this work paper.

The assumptions shown below were used in the previous revision of this work paper to calculate the energy savings for running the pool pumps at reduced flow during nighttime operation. The SDG&E study [E] investigates pool pump savings throughout the entire day, not only at night as was assumed in the previous revision, so there will be some demand savings associated with this measure. The assumptions have been left in the work paper to compare the calculated energy savings (based on the EC&C database and general assumptions) with the savings given in the SDG&E study [E].

- Average pump size in the EC&C database (Attachment No. 2), 1.49 hp

- Average pump input power in the EC&C database (Attachment No.2), 2.155 kW

- Average Pump size in the multifamily building pool pump survey (Attachment No. 5), 1.77 hp

- Number of hours pool is expected to be closed (12 h/day, 365 days/yr), 4,380 h/yr

- Expected pump load factor at 20% speed, 0.142 [N] no units

The total energy usage is the total annual water flow, in gallons, divided by the Energy Factor as shown in Equation 1.

For pools that pump in two distinct modes, the total energy usage is the weighted average of the energy usages associated with each mode.

#### Measure A

#### Measure A:	Base Case Single-Speed Pump Energy Usage

The annual energy usage for the Measure A single-speed base case (EUA1-spd) is calculated as follows:

EUA1-spd	=	V × T × D / EFF × C

EUA1-spd 	=	(18,000 gallons)(1 turnover)(365 day/yr)

/(2.18 gallons/W-hr)(1,000 W/kW)

EUA1-spd 	=	3,013.76 kWh/yr

The electrical energy usage is somewhat higher than the 2,772 kWh annual average energy usages for single-speed pumps in the state as reported by RASS [O], because the 1.73 hp average encountered in the InDEE program is larger than the statewide average. The horsepower spectrum of the base case pump is obtained from the InDEE Program data, and thus provides the best representation of the base case equipment.

#### Measure A:	Base Case Two-Speed Pump Energy Usage

The annual energy usage for Measure A two-speed base case (EUA2-spd) is calculated as follows:

EUA2-spd 	=	(W94.4% × EUA2-spd:M-1) + (W5.6% × EUA2-spd:M-2)

Where,

W94.4%		=	percentage of sites (by pool volume) that filter 0.98 turnovers per

day, 94.4% (0.944), no units

EUA2-spd:M-1	=	annual energy usage for the two-speed base case first mode of

operation, kWh/yr

W5.6%		=	percentage of sites (by pool volume) that filter 0.86 turnovers per

day at low speeds and perform pool sweeps for an additional 0.37

turnovers per day at high speeds, 5.6% (0.056), no units

EUA2-spd:M-2	=	annual energy usage for the two-speed base case second mode of

operation, kWh/yr

The annual energy usage for the first mode (mode-1) of operation for the two-speed base case (EUA2-spd:M-1) is as follows:

EUA2-spd:M-1	=	V × T × D / EFF × C

EUA2-spd:M-1	=	(18,000 gallons)(0.98 turnover)(365 day/yr)

/(3.39 gallons/W-hr)(1,000 W/kW)

EUA2-spd:M-1	=	1,899.29 kWh/yr

The annual energy usage for the second mode (mode-2) of operation for the two-speed base case (EUA2-spd:M-2) is calculated as follows:

EUA2-spd:M-2	=	EUA2-spd:M-2A + EUA2-spd:M-2B

Where,

EUA2-spd:M-2A 	=	annual energy usage for the two-speed base case second mode of

filtering operation (mode-2A), kWh/yr

EUA2-spd:M-2B 	=	annual energy usage for the two-speed base case second mode of

pool sweep operation (mode-2B), kWh/yr

The annual energy usage for the second mode of filtering operation (mode-2A) for the two-speed base case (EUA2-spd:M-2A) is as follows:

EUA2-spd:M-2A 	=	V × T × D / EFF × C

EUA2-spd:M-2A 	=	(18,000 gallons)(0.86 turnover)(365 day/yr)

/ (3.39 gallons/W-hr)(1,000 W/kW)

EUA2-spd:M-2A 	=	1,666.73 kWh/yr

The annual energy usage for the second mode of pool sweep operation (mode-2B) for the two-speed base case (EUA2-spd:M-2B) is as follows:

EUA2-spd:M-2B 	=	V × T × D / EFF × C

EUA2-spd:M-2B 	=	(18,000 gallons)(0.37 turnover)(365 day/yr)

/(2.06 gallons/W-hr)(1,000 W/kW)

EUA2-spd:M-2B 	=	1,180.05 kWh/yr

The annual energy usage for the second mode of operation (mode-2) for the two-speed base case (EUA2-spd:M-2) is as follows:

EUA2-spd:M-2	=	EUA2-spd:M-2A + EUA2-spd:M-2B

EUA2-spd:M-2	=	1,666.73 kWh/yr + 1,180.05 kWh/yr

EUA2-spd:M-2	=	2,846.78 kWh/yr

Therefore, the annual energy usage for the Measure A two-speed base case (EUA2-spd) is as follows:

EUA2-spd =	(W94.4% × EUA2-spd:M-1) + (W5.6% × EUA2-spd:M-2)

EUA2-spd =	[(0.944)(1,899.29 kWh/yr)]+[(0.056)(2,846.78 kWh/yr)]

EUA2-spd =	1,952.35 kWh/yr

#### Measure A:	Measure Case Programmed Variable-Speed Pump Energy Usage

The annual energy usage for programmed variable-speed pool pumps in Climate Zone 15 is 1,257 kWh/yr (EC&C database, Attachment No.2).

#### Measure A:	Electrical Energy Savings

The estimated annual electrical energy consumptions for Measure A, measure and base cases (presented above) are for Climate Zone 15. The resulting estimated annual electrical energy savings for Climate Zone 15 is the difference between the weighted average base case energy consumption (where it is assumed that 95% of the usage is from single-speed pumps and 5% is from two speed pumps) and the measure case energy consumption, which is 1,704 kWh/yr. For the second baseline, only the savings from two-speed motors are considered. Therefore the second baseline energy savings are 695 kWh/yr.

The methodology in Attachment No.4, One Stop Shop Beyond CZ 15 Analysis is used to extrapolate the estimated electrical energy and demand savings from Climate Zone 15 for the rest of the SCE climate zones (6, 8, 9, 10, 13, 14, and 16). The resulting estimated electrical energy savings for Measure A is 1,686 kWh/yr. The corresponding second baseline energy savings are 677 kWh/yr. Please refer to Attachment No.4 for energy savings calculation.

#### Measure B

#### Measure B:	Base Case Two-Speed Pump Energy Usage

The annual energy usage for the two-speed base case (EUB2-spd) is calculated as follows:

EUB2-spd 	=	(W94.4% × EUB2-spd:M-1) + (W5.6% × EUB2-spd:M-2)

Where,

W94.4%		=	percentage of sites (by pool volume) that filter 0.98 turnovers per

day, 94.4% (0.944), no units

EUB2-spd:M-1	=	annual energy usage for the two-speed base case first mode of

operation, kWh/yr

W5.6%		=	percentage of sites (by pool volume) that filter 0.86 turnovers per

day at low speeds and perform pool sweeps for an additional 0.37

turnovers per day at high speeds, 5.6% (0.056), no units

EUB2-spd:M-2	=	annual energy usage for the two-speed base case second mode of

operation, kWh/yr

The annual energy usage for the first mode (mode-1) of operation for the two-speed base case (EUB2-spd:M-1) is as follows:

EUB2-spd:M-1	=	V × T × D / EFF × C

EUB2-spd:M-1	=	(20,341 gallons)(0.98 turnover)(365.25 day/yr)

/(3.39 gallons/W-hr)(1,000 W/kW)

EUB2-spd:M-1	=	2,147.78 kWh/yr

The annual energy usage for the second mode (mode-2) of operation for the two-speed base case (EUB2-spd:M-2) is calculated as follows:

EUB2-spd:M-2	=	EUB2-spd:M-2A + EUB2-spd:M-2B

Where,

EUB2-spd:M-2A	 =	annual energy usage for the two-speed base case second mode of

filtering operation (mode-2A), kWh/yr

EUB2-spd:M-2B 	=	annual energy usage for the two-speed base case second mode of

pool sweep operation (mode-2B), kWh/yr

The annual energy usage for the second mode of filtering operation (mode-2A) for the two-speed base case (EUB2-spd:M-2A) is as follows:

EUB2-spd:M-2A 	=	V × T × D / EFF × C

EUB2-spd:M-2A 	=	(20,341 gallons)(0.86 turnover)(365.25 day/yr)

/ (3.39 gallons/W-hr)(1,000 W/kW)

EUB2-spd:M-2A 	=	1,884.78 kWh/yr

The annual energy usage for the second mode of pool sweep operation (mode-2B) for the two-speed base case (EUB2-spd:M-2B) is as follows:

EUB2-spd:M-2B 	=	V × T × D / EFF × C

EUB2-spd:M-2B	=	(20,341 gallons)(0.37 turnover)(365.25 day/yr)

/(2.06 gallons/W-hr)(1,000 W/kW)

EUB2-spd:M-2B 	=	1,334.43 kWh/yr

The annual energy usage for the second mode of operation (mode-2) for the two-speed base case (EUB2-spd:M-2) is as follows:

EUB2-spd:M-2	=	EUB2-spd:M-2A + EUB2-spd:M-2B

EUB2-spd:M-2	=	1,884.78 kWh/yr + 1,334.43 kWh/yr

EUB2-spd:M-2	=	3,219.21 kWh/yr

Therefore, the annual energy usage for the two-speed base case (EUB2-spd) is as follows:

EUB2-spd 	=	(W94.4% × EUB2-spd:M-1) + (W5.6% × EUB2-spd:M-2)

EUB2-spd 	=	[(0.944)(2,147.78 kWh/yr)]+[(0.056)(3,219.21 kWh/yr)]

EUB2-spd 	=	2,207.78 kWh/yr

#### Measure B:	Measure Case Variable-Speed Pump Energy Usage (Not Programmed)

The annual energy usage for Measure B variable-speed case (EUBV-spd) is calculated as follows:

EUBV-spd 	=	(W94.4% × EUBV-spd:M-1) + (W5.6% × EUB V-spd:M-2)

Where,

W94.4%		=	percentage of sites (by pool volume) that filter 0.98 turnovers per

day, 94.4% (0.944), no units

EUBV-spd:M-1	=	Measure B annual energy usage for the variable-speed measure case

first mode of operation, kWh/yr

W5.6%		=	percentage of sites (by pool volume) that filter 0.86 turnovers per

day at low speeds and perform pool sweeps for an additional 0.37

turnovers per day at high speeds, 5.6% (0.056), no units

EUB V-spd:M-2	=	Measure B annual energy usage for the variable-speed measure case

second mode of operation, kWh/yr

The annual energy usage for the first mode (mode-1) of operation for Measure B variable-speed case (EUBV-spd:M-1) is as follows:

EUBV-spd:M-1	=	V × T × D / EFF × C

EUBV-spd:M-1	=	(20,341 gallons)(0.98 turnover)(365.25 day/yr)

/(4.37 gallons/W-hr)(1,000 W/kW)

EUBV-spd:M-1	=	1,666.12 kWh/yr

The annual energy usage for the second mode (mode-2) of operation for Measure B variable-speed case (EUBV-spd:M-2) is calculated as follows:

EUBV-spd:M-2	=	EUBV-spd:M-2A + EUBV-spd:M-2B

Where,

EUBV-spd:M-2A 	=	Measure B annual energy usage for the second mode of filtering

operation (mode-2A), kWh/yr

EUBV-spd:M-2A 	=	Measure B annual energy usage for the second mode of pool sweep

operation (mode-2B), kWh/yr

The annual energy usage for the second mode of filtering operation (mode-2A) for Measure B variable-speed case (EUBV-spd:M-2A) is as follows:

EUBV-spd:M-2A 	=	V × T × D / EFF × C

EUBV-spd:M-2A 	=	(20,341 gallons)(0.86 turnover)(365.25 day/yr)

/ (4.61 gallons/W-hr)(1,000 W/kW)

EUBV-spd:M-2A 	=	1,385.99 kWh/yr

The annual energy usage for the second mode of pool sweep operation (mode-2B) for Measure B variable-speed case (EUBV-spd:M-2B) is as follows:

EUBV-spd:M-2B 	=	V × T × D / EFF × C

EUBV-spd:M-2B	=	(20,341 gallons)(0.37 turnover)(365.25 day/yr)

/ (3.00 gallons/W-hr)(1,000 W/kW)

EUBV-spd:M-2B 	=	916.32 kWh/yr

The annual energy usage for the second mode (mode-2) of operation for Measure B variable-speed case (EUBV-spd:M-2) is as follows:

EUBV-spd:M-2	=	EUBV-spd:M-2A + EUBV-spd:M-2B

EUBV-spd:M-2	=	1,385.99 kWh/yr + 916.32 kWh/yr

EUBV-spd:M-2	=	2,302.31 kWh/yr

Therefore, the annual energy usage for Measure B variable-speed case (EUBV-spd) is as follows:

EUBV-spd 	=	(W94.4% × EUBV-spd:M-1) + (W5.6% × EUBV-spd:M-2)

EUBV-spd 	=	[(0.944)(1,666.12 kWh/yr)]+[(0.056)(2,302.31 kWh/yr)]

EUBV-spd 	=	1,701.75 kWh/yr

#### Measure B:	Electrical Energy Savings

The annual electrical energy savings for Measure B (EESB) is calculated as follows:

EESB		=	EUB2-spd – EUBV-spd

EESB		=	2,208 kWh/yr – 1,702 kWh/yr

EESB		=	506 kWh/yr

#### Measure C

#### Measure C:	Base Case Single-Speed Pump Energy Usage

The annual estimated electrical energy usage for the Measure C single-speed base case is the same as the Measure A single-speed base case estimated electrical energy usage of 3,013.76 kWh/yr.

#### Measure C:	Measure Case Programmed Variable-Speed Pump Energy Usage

The annual energy usage for programmed variable-speed pool pumps in Climate Zone 15 is 1,257 kWh/yr (EC&C database, Attachment No.2).

#### Measure C:	Electrical Energy Savings

The estimated annual electrical energy consumptions for Measure C, measure and base cases are for Climate Zone 15. The resulting estimated annual electrical energy savings for Climate Zone 15 is the difference between the base case energy consumption and the measure case energy consumption, which is 1,757 kWh/yr. The corresponding second baseline energy savings is 695 kWh/yr.

The methodology in Attachment No.4, One Stop Shop Beyond CZ 15 Analysis is used to calculate the estimated electrical energy and demand savings from Climate Zone 15 and extrapolate the savings for the rest of the SCE climate zones (6, 8, 9, 10, 13, 14, and 16). The estimated electrical energy savings for Measure C is 1,742 kWh/yr. The corresponding second baseline energy savings is 677 kWh/yr. Please refer to Attachment No.4 for energy savings calculation.

#### Measure D

Table 1 from the study shows the kWh savings as 13,593 kWh/year for site one and 5,195 kWh/year for site two. The study also uses an 80% weighting factor for the smaller single pump pool which is installed in site two. Using an 80/20 percentage weighting, the savings for retrofitting a single speed pool pump with a variable speed pool pump would be 6,874.6 kWh/year.

The assumptions from revision zero of this work paper have been left in to compare with the values from the SDG&E study [E].

The energy savings, EES, for Measure D were previously estimated as follows (please note these are not the savings claimed for this measure):

EES	=	kW x HPF x H x (1 – LFclose)

Where,

kW	=	Average input pump power in the EC&C Excel File (see attachment), 					2.155 kW

HPF	=	Pump horse power rating factor, the ratio between the multifamily survey 				(see attached Excel File) (1.77 hp) average pump size and the EC&C 					Excel File average pump size (1.49 hp), equivalent to 1.18 no units

H	=	number of hours the pump is expected to operate at reduced speed, 4,380 				h/yr

LFclose	=	pump controlled load factor at 20% speed while the pool is closed, 0.142 				no units

Therefore the energy savings is estimated as follows:

EES	=	(2.155)(1.18)(4,380)(1 – 0.143)

EES	=	9,545 kWh/yr

Pump load factors at various speeds were obtained from a tool developed by the Bonneville Power Administration [N]. The figured used to determine the VFD controlled load factor at 20% speed is reproduced below.

Figure 3 ASD Pump Flow Control Chart

For the 2nd baseline, the assumptions from the previous revision were kept as the SDG&E study [E] did not address two speed pool pumps as the base case. Code requires two speed pumps to be installed, and as the 2nd baseline would coincide with what code requires, the best available data was used. This data is found from the EC&C database (attachment 2), where the only assumption changed was the operating hours. The SDG&E study documented the operating hours for the two sites, where site one operated 24 hours a day and site two operated 15 hours a day. Using the 80/20 percentage weighting, the hours of operation were found to be 6,132 hr/year. The savings for multi-family operation differ from the savings for single family based on the difference in operating hours as mentioned above.

The second baseline energy savings can be estimated as follows:

EES2	=	kW x HPF x H x (LF2 – LFclose)

Where all variables are the same as in EES except,

LF2	=	two speed pump load factor at 50% speed, 0.2 from Figure 3

Therefore the energy savings is estimated as follows:

EES	=	(2.155)(1.18)(6,132)(0.2 – 0.143)

EES	=	888.8 kWh/yr

#### Measure E

The savings for this measure are based on the customer replacing a burned out pool pump with a new variable speed pool pump. Code would be invoked and would require that a customer has to at least install a two speed pool pump. Similar to the 2nd baseline of measure D, the savings for this measure would be as follows:

EES2	=	kW x HPF x H x (LF2 – LFclose)

Where all variables are the same as in EES except,

LF2	=	two speed pump load factor at 50% speed, 0.2 from Figure 3

Therefore the energy savings is estimated as follows:

EES	=	(2.155)(1.18)(6,132)(0.2 – 0.143)

EES	=	888.8 kWh/yr

The original savings have been left in this work paper to compared the savings from the original calculations and the SDG&E study [E]. The savings can be estimated as follows (please note these are not the savings claimed for this measure):

EES	=	kW x HPF x H x (1 – LFclose)

Where,

kW	=	Average input pump power in the EC&C Excel File (see attachment), 					2.155 kW

HPF	=	Pump horse power rating factor, the ratio between the multifamily survey 				(see attached Excel File) (1.77 hp) average pump size and the EC&C 					Excel File average pump size (1.49 hp), equivalent to 1.18 no units

H	=	number of hours the pump is expected to operate at reduced speed, 4,380 				h/yr

LFclose	=	pump controlled load factor at 20% speed while the pool is closed, 0.142 				no units

Therefore the energy savings is estimated as follows:

EES	=	(2.155)(1.18)(4,380)(1 – 0.143)

EES	=	9,545 kWh/yr

Table 11 lists the calculated estimated electrical energy savings for each measure.

Table 11 Energy Usages and Savings for Programmed Variable Speed Pool Pumps

| Measure Type | Base Case | Measure Case | Annual Electrical Energy Savings |  |
| --- | --- | --- | --- | --- |
| Measure A | 95% single-speed pumps 5% two-speed pumps | Programmed variable-speed pumps | Climate zone 15 | 1,704 kWh/yr. |
|  |  |  | All Other Climate Zones | 1,686 kWh/yr. |
| Measure B | 100% two-speed pumps | Variable-speed pumps (not programmed) | 506 kWh/yr. |  |
| Measure C | 100% single-speed pumps | Programmed variable-speed pumps | Climate zone 15 | 1,757 kWh/yr. |
|  |  |  | All Other Climate Zones | 1,742 kWh/yr. |
| Measure D | 100% single speed pumps | Variable-speed pumps | 6,874.6 kWh/yr |  |
| Measure E | two-speed pumps at 100% flow | Variable-speed pumps | 888.8 kWh/yr |  |

## 2.3 Demand Reduction Estimation Methodologies

The coincident peak demand savings takes into account the degree to which the demand savings coincides with the DEER peak demand, defined as average demand between 2:00 P.M. and 5:00 P.M. during a three-day summer heat wave. The demand savings are equal to the difference in electric demand, times a peak coincidence factor. In this section, the non-coincident electric demands for single-speed, two-speed, and variable-speed pumps are established. The hourly coincidence factors for the three technologies are derived next, enabling the calculation of demand reductions.

#### Electric Demand: Single-Speed Pumps

The average demand for single-speed pool pumps is taken from two sources. The first source, the InDEE Program Pentair installation data, includes the nameplate horsepower distribution for the single-speed pumps that were replaced. The transition from nameplate horsepower to kW is obtained from the CEC appliance database, which lists the operational kW for 108 single-speed pumps. The SCE Emerging Technology report [D] suggests that Curve A is a good indicator of electric demand at higher flow rates. The electric demands for all pumps above 1 hp are plotted against the nameplate horsepower in Figure 4. The 491 replaced baseline single-speed pumps in the InDEE Program installation records are individually assigned electric demands according to the linear regression that results from the fit to the data shown in Figure 4. The average non-coincident electric demand for the 491 supplanted single-speed pumps is 1.772 kW. The linear regression, fitting the data in Figure 4, is symbolically written as Equation 5:

Equation 5

P	=	0.67741 × HP + 0.591356

Where,

P	=	power, kW

HP	=	horsepower, hp

Figure 4 Electric Demand (W) vs. Nameplate Horsepower for Single-Speed Pumps, 
as Listed in the CEC Appliance Database.

#### Electric Demand: Two-Speed Pumps

The electric demand for two-speed pumps is taken to be the nominal demand at low-speed for two reasons. First, according to Section 1605.3(g) of California Title 20 [422], Pool pump motor controls manufactured on or after January 1, 2008 shall have the capability of operating the pool pump at least two speeds. The default circulation speed shall be the lowest speed, with a high speed override capability being for a temporary period not to exceed one normal cycle. Thus, according to code, the two-speed pool pumps default operational mode is at low speed. Secondly, the records from the InDEE data show that the great majority of variable-speed pumps are used solely for filtering, with a secondary ‘booster’ pump used to provide additional pressure for pool sweeps. It is therefore safe to assume that the two-speed pumps will be operating at low speed during the 2:00 pm and 5:00 pm time period.

Electric demands for all models above 1 hp listed in the CEC appliance database are averaged for the low speed modes. The average electric demand for all pumps in low speed mode is 420 W at 34 gpm according to CEC Curve A, and 376 W at 21 gpm according to Curve B. The Curve B non-coincident demand of 0.376 kW is taken as the demand of two-speed pool pumps.

#### Electric Demand: Variable-Speed Pumps

Based on the 491 records in the InDEE Program data, the average non-coincident electric demand of the average VSD pool pump is 0.415 kW [F].

#### Peak Coincidence Factor and Load Shapes

The coincidence factor is the ratio of coincident demand to maximum demand. It determines the degree to which a customer’s peak demand coincides with the utility’s system peak demand. The Public Utility Commission (PUC) peak demand reduction is the average demand across the nine hours that fall between 2:00 pm and 5:00 pm during a three-day summer heat wave. Pool pumps are non-weather sensitive, and thus are expected to run, on average, during the same hours each day.

#### Single-Speed Pumps Coincidence Factor

The hourly coincidence factors for single-speed pumps are obtained from two separate sources. The 2001 Evaluation [C] lists in its Table 4-4, the percentage of 165 monitored pool pumps that are running at any given hour. In 2008, 146 pool pumps were monitored in SCE territory for a pool pump demand response potential study [K]. In this study, the electric demand was monitored for each pump, and an actual load shape in terms of hourly kW, not just in terms of the percentage of pumps that are on, was recorded. The hourly coincidence factors are quite similar, as shown in Figure 5. The coincidence factors for single-speed pool pumps are taken to be the average of the 2001 and 2008 measurements. The PUC nine-hour average peak demand coincidence factor for single-speed pumps is 0.309. The relevant hourly coincidence factors are shown in Table 12. The sum of all hourly coincidence factors for single-speed load shape curve is 5.29, which is consistent with the 5.3 hours of pumping used in Attachment No.2 (EC&C database).

Figure 5  Load Shapes for Single Speed Pumps in SCE territory 
as Measured in 2001 and 2008

Table 12  Coincidence Factors for Single-Speed Pool Pumps as Measured in 2001 and 2008

| Hour of Day | Coincidence Factor (2001 Evaluation) | Coincidence Factor (2008 Evaluation) | Average Coincidence Factor |
| --- | --- | --- | --- |
| 2PM – 3PM | 0.378 | 0.411 | 0.395 |
| 3PM – 4PM | 0.268 | 0.341 | 0.305 |
| 4PM – 5PM | 0.171 | 0.287 | 0.229 |
| Average 2PM-5PM | 0.272 | 0.347 | 0.309 |

#### Variable Speed Pumps Coincidence Factor

For variable-speed pumps, the hourly demand coincidence factors are taken directly from the InDEE Pentair installation data. For each hour, the coincidence factor is taken to be the sum of electric demands for the subset of pumps that are in operation divided by the sum of electric demands for all pumps. The PUC nine-hour average peak demand coincidence factor for variable-speed pumps is 0.390. The sum of all hourly coincidence factors for variable-speed load shape curve is 11.2, which is consistent with the 11.6 hours of pumping used in Attachment No.2 (EC&C database).

#### Two-Speed Pumps Coincidence Factor

There are no monitored data for two-speed pumps that are comparable in size to the datasets for the single-speed and variable-speed pumps. In the absence of a sizable monitored dataset on two-speed pump electric demand, the power vs. flow data from the CEC Appliance Database is used to approximate the two-speed pump electric demands. The electric demands for the two-speed pumps at low speed are listed in the CEC database for an average flow of 20.7 gpm. As mentioned, the Curve A values are appropriate for high flow rates, but not at lower flow rates. However, according to field data (Figure 2), CEC Curve B intersects the InDEE Curve at approximately 22 gpm. The InDEE data shows that Curve B and the InDEE Curve are in good agreement at flow rates near 20.7 gpm. Due to the proximity of Curve B and the InDEE Curve at this flow rate, the electric demands listed under Curve B in the CEC Appliance Database are used for two-speed pumps at low speed.

According to the CEC database’s Curve B, two-speed pumps on low speed operate at an average flow of 20.7 gpm. This is significantly lower than the 28.6 gpm associated with the variable speed pumps.

Accordingly, the number of pumping hours per day will be longer than that of the variable-speed pumps, and the demand coincidence factor should be higher. To approximate the hourly coincidence factors for two-speed pumps, only the subset of pumps from the InDEE data that ran at flows of 19 to 22 gpm (approximately 20.7 +/- 1.5 gpm) are considered.

This is an appropriate approximation as the coincidence factor depends chiefly on pump run-time, which is determined by the flow rates and pool volumes. For a given stock of pools, the demand coincidence factor depends on the flow rates of the installed pumps. The coincidence factors that are calculated for the 70 pumps that had flow rates between 19 and 22 gpm are taken as the best approximation of the coincidence factors for two-speed pumps. The PUC 9-hour average peak demand coincidence factor for variable-speed pumps is 0.522, and this is the appropriate demand coincidence factor to use for two-speed pumps at low-speed. The sum of all hourly coincidence factors for two-speed pumps is 12.9, which is somewhat less than the 16.0 hours of pumping used in Attachment No.2 (EC&C database), though not altogether inconsistent given the relatively small sample size.

Figure 6 shows the hourly coincidence factors for single-speed, two-speed, and variable-speed (not programmed) pool pumps.

Figure 6 Hourly Coincidence Factors for Single-Speed, 
Two-Speed, and Variable-Speed Pool Pumps (not programmed)

#### Electric Peak Demand Reductions

The peak coincident electric demands can be calculated by using Equation 6 symbolically written as:

Equation 6

PC	=	P × CF

Where,

PC	=	Peak Coincident Demand, kW

P	=	Power, kW

CF	=	Coincidence Factor, no units

The peak coincident electric demands for single-speed (PC1-spd), two-speed pumps (PC2-spd), and non-programmed variable-speed pumps (PCNPV-spd) are shown below:

PC1-spd		=	1.772 × 0.309		=	0.548 kW

PC2-spd		=	0.376 × 0.522		=	0.196 kW

PCNPV-spd	=	0.415 × 0.390		=	0.162 kW

The programmed variable-speed pumps are programmed to run outside the noon to 6 P.M. timeframe, therefore their peak coincident electric demand (PCPV-spd) is zero.

Measure A

#### Measure A:	Base Case Single-Speed Pump Peak Coincident Demand

The estimated peak coincident electric demand for the Measure A single-speed base case (PC1-spd) is calculated to be 0.548 kW.

#### Measure A:	Base Case Two-Speed Peak Coincident Demand

The estimated peak coincident electric demand for the Measure A two-speed base case (PC2-spd) is calculated to be 0.196 kW.

#### Measure A:	Measure Case Programmed Variable-Speed Pump Peak Coincident Demand

The variable-speed pumps are to be programmed to run outside the noon to 6 P.M. timeframe, therefore their peak coincident electric demand (PCPV-spd) is zero.

#### Measure A:	Peak Demand Reduction

The measure and base case estimated peak coincident electric demands are for all SCE climate zones. Therefore the methodology by Ricson Chude of SCE (Attachment No.4, One Stop Shop Beyond CZ 15 Analysis) for extrapolating the estimated peak demand reduction from Climate Zone 15 to all of the SCE climate zones is not used. The peak demand reduction for Measure A (PDRA) is calculated as follows:

PDRA	=	[SF × (PC1-spd – PCPV-spd)] + [TF × (PC2-spd – PCPV-spd)]

Where all variables are the same with the addition of:

SF	=	fraction of peak demand reduction with single-speed as base case

(conservative estimate from SCE), 0.95 no units

TF	=	fraction of peak demand reduction with two-speed as base case

(conservative estimate from SCE), 0.05 no units

Thus,

PDRA	=	(0.95)(0.548 kW – 0 kW) + (0.05)(0.196 kW – 0 kW)

PDRA	=	0.530 kW

Measure B

#### Measure B:	Base Case Two-Speed Peak Coincident Demand

The estimated peak coincident electric demand for the Measure B two-speed base case (PC2-spd) is calculated to be 0.196 kW.

#### Measure B:	Measure Case Variable-Speed Pump Peak Coincident Demand

The estimated peak coincident electric demand for the Measure B non-programmed variable-speed measure case (PCNPV-spd) is calculated to be 0.162 kW.

#### Measure B:	Peak Demand Reduction

The peak demand reduction calculation for Measure B (PDRB) is estimated as follows:

PDRB	=	PC2-spd – PCNPV-spd

PDRB	=	0.196 kW – 0.162 kW

PDRB	=	0.034 kW

Measure C

#### Measure C:	Base Case Single-Speed Pump Peak Coincident Demand

The estimated peak coincident electric demand for the Measure C single-speed base case (PC1-spd) is calculated to be 0.548 kW.

#### Measure C:	Measure Case Programmed Variable-Speed Pump Peak Coincident Demand

The variable-speed pumps are to be programmed to run outside the noon to 6 P.M. timeframe, therefore their peak coincident electric demand (PCPV-spd) is zero.

#### Measure C:	Peak Demand Reduction

The measure and base case estimated peak coincident electric demands are for all SCE climate zones. Therefore the methodology by Ricson Chude of SCE (Attachment No.4, One Stop Shop Beyond CZ 15 Analysis) for extrapolating the estimated peak demand reduction from Climate Zone 15 to all of the SCE climate zones is not used. The peak demand reduction calculation for Measure C (PDRC) is estimated as follows:

PDRC	=	PC1-spd – PCPV-spd

PDRC	=	0.548 kW – 0 kW

PDRC	=	0.548 kW

Measure D

Table 1 from the study shows the kW savings as 1.55 kW for site one and 0.95 kW for site two. The study also gives an 80% weighting factor for the smaller single pump pool which is installed in site two. Using an 80/20 percentage weighting, the savings for retrofitting a single speed pool pump with a variable speed pool pump would be 1.07 kW.

For measure D, the 2nd baseline kW savings are the difference in kW from the 2 speed pool pump (which is taken to be 2.155 kW from the assumptions from the kWh calculations for measure D from above) and the variable speed pool pump (which is 1.31 kW from the SDG&E study after applying the 80/20 weighting). The kW savings is 0.84 kW for the 2nd baseline.

Two speed kW usage: 	2.155 kW

Variable speed kW usage (from SDG&E Study [E]):

(2.01 x 20%) + (1.14 x 80%) = 1.31 kW

Savings:	(2.155 – 1.31) = 0.84 kW

Please note that the original kW assumptions and savings have been left in the work paper to compare the revision one savings with the savings found from the SDG&E study [E].

Since the pump will operate at reduced flow during nighttime, this measure is not expected to result in peak demand savings.

Measure E

The kW savings will match the kW savings for the 2nd baseline of measure D. As this measure is ROB, code would be invoked and require a two speed pool pump, which matches the 2nd baseline of measure D. The savings for this measure are 0.84 kW

Please note that the original kW assumptions and savings have been left in the work paper to compare the revision one savings with the savings found from the SDG&E study [E].

Since the pump will operate at reduced flow during nighttime, this measure is not expected to result in peak demand savings.

The estimated peak demand reductions are listed in Table 13.

Table 13  Peak Coincident Electric Demand and Demand Reduction for Pool Pumps

| Measure Type | Base Case | Measure Case | Peak Demand Reduction |
| --- | --- | --- | --- |
| Measure A | 95% single-speed pumps 5% two-speed pumps | Programmed variable-speed pumps | 0.530 kW |
| Measure B | 100% two-speed pumps | Variable-speed pumps (not programmed) | 0.034 kW |
| Measure C | 100% single-speed pumps | Programmed variable-speed pumps | 0.548 kW |
| Measure D | Single Speed Pump Operating at 100% flow 24 hours per day | Programmed Variable Speed Pump for multi-family | 1.07 kW |
| Measure E | Two Speed Pump Operating at 100% flow 24 hours per day | Variable Speed Pump for multi-family (not programmed) | 0.84 kW |

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available. Therefore, the closest load shape chosen for this measure is the Residential Pool Pumps load shape. See Table 14 for a list of all Building Types and Load Shapes. See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 14 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Residential Single Family | Residential | Residential Pool Pumps |
| Residential Multifamily | Residential | Residential Pool Pumps |

# Section 4. Base Case & Measure Costs

Direct Install measures (Measures A, C, and D) use program tracking systems for measure costs.

## 4.1 Base Case Cost

The SCE evaluation team solicited bids from Southern California contractors familiar with single-speed, two-speed, and variable-speed residential pool pumps to ascertain costs. All bids represent installed costs (parts and labor) because it is assumed that there is virtually no self-installation of pool pumps by residential customers. The following bids were provided:

- Replace single-speed pump with single-speed pump: $687.24

- Replace single-speed pump and mechanical timer with a two-speed pump and two-speed capable timer: $1,251.08

RET

Measures A, C, and D have the measure install type Retrofit (Ret). The base case for Measure A is both single and two-speed pumps. The base case for Measures C and D is single-speed pumps. As discussed in Section 1.3, Title 20, Section 1605.3 of California’s Appliance Efficiency Regulations [422] requires that, effective January 1, 2008, all 1-horsepower or greater residential pool pumps sold in California shall have the capability of operating at two or more speeds.

However, for this work paper, under the retrofit measure category, the 1st baseline base cost is assumed to be zero ($0). This is because these are discretionary modifications (retrofit) to the customers’ existing equipment. Their alternative is to make no changes to their existing system.  For the 2nd baseline, the base cost is expected to be the 2-speed motor/pump as required by the code. The cost of a two speed pump is expected to be $1,251.08.

ROB

Measures B and D have the measure install type Replace on Burnout (ROB). The base case for Measure B is a two-speed pump. For the ROB measure category, the base cost for purchasing and installing a two-speed pump is $1,251.08.

## 4.2 Measure Case Cost

The SCE evaluation team also solicited bids for variable-speed residential pool pumps. As above, all bids represent installed cost (parts and labor). Variable-speed pool pumps must be installed by a trained technician to ensure effective operation. The reason is that variable-speed pumps either contain an integrated, programmable controller, or require a separate, standalone controller. Both types of controllers require fairly sophisticated programming that residential customers would be unable to provide. Therefore, assuming that all variable-speed pumps require professional installation, the bid to replace a single or two-speed pump, remove mechanical timer, install, and program a variable-speed pump is $1,705.77. The bid to replace a single or two-speed pump, remove mechanical timer and install a variable-speed pump is $1,537.50.

The measure case for Measures A, C, and D is a programmed variable-speed pump.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

RET

Measures A, C, and D have the measure install type Retrofit (Ret). For the RET measure category, the gross measure cost is the measure case cost ($1,705.77) minus the base case cost ($0), which is $1,705.77 for the 1st baseline.

For the 2nd baseline, the measure cost is the difference between the programmed variable speed pump and the 2-speed pump, which is$454.69.

ROB

Measure B and Measure E has the measure install type Replace on Burnout (ROB). For the ROB measure category, the gross measure cost is the measure cost ($1,537.50) minus the base cost ($1,251.08), which is $286.42.

### 4.3.2 Incremental Measure Cost

The incremental measure cost is for deemed measures only. The delivery method for Measures A, C, and D is Financial Support – Direct Install. The delivery method for Measures B and E are Financial Support – Downstream Incentive – Deemed.

The incremental measure cost for Measure B and Measure E is the measure cost ($1,537.50) minus the base measure cost ($1,251.08), which is $286.42.

# Attachments

- Note: address/contact info removed to protect customer confidentiality

# References

[31]

[49]

[351]

[355]

[422]

[436]

[A]	Evaluation of Year 2001 Summer Initiatives Pool Pump Program, conducted by ADM Associates for Pacific Gas & Electric Company, April 2002, p. 1-2; 3-1; 3-2;  4-6; 5-1; 5-4.

[B]	Centers for Disease Control. (2006). Health Housing Reference Manual – Chapter 14: Residential Swimming Pools and Spas.

[C]	Performance and Energy Efficiency Evaluation of Residential Variable-Speed Pool Pumps, Prepared by Design & Engineering Services, Southern California Edison, March 2007, pages 2-4, 6-8, 10-11, 13, 18-27, 29, and 33-54.

[D]	Southern California Edison’s Innovative Designs For Energy Efficiency (InDEE) Program for 2006-2008 has records of 975 Pentair IntelliFlo pool pump installations.  Of these records, 491 have complete information regarding pool size, the baseline pool pump, and variable-speed pump RPM, flow, hours of operation, and kW.

[E]	Information & Energy Services, Inc. (2012). Engineering Measurement & Verification Study: Multi-Family Residential Variable Speed Swimming Pool/Spa Pump Retrofit. Attachment 7.

[F]	“CEC Appliances Database – Pool Pumps.”  California Energy Commission.  Updated Feb 2008.  Accessed March 2008. <http://www.energy.ca.gov/appliances/database/excel_based_files/Pool_Products/Pool_Pumps.zip>

[G]	Appliance Efficiency Regulations, December 2006, CEC-400-2006-002-REV2, p. 64

[H]	PG&E work paper PGECOPUM107

[I]	Performance and Energy Efficiency Evaluation of Residential Variable-Speed Pool Pumps. Prepared by Design & Engineering Services, Southern California Edison, March 2007, page 18, Figure 4.

[J]	Pentair IntelliFlo Owners Manual http://www.pentairpool.com/pdfs/IntelliFloOm.pdf, page 47.

[K]	Pool Pump Demand Response Potential, Prepared by Design & Engineering Services, Southern California Edison, June 2008.

[L]	List of SCE-rebated variable speed pool pumps: http://www.sce.com/NR/rdonlyres/E8FB5F93-6512-4E00-8D49-501A29A570F8/0/2008_VariableSpeedList.pdf

[M]	Bonneville Power Administration (BPA) - ASD Calculators for Fan & Pump Applications,  	2004

[N]	Bonneville Power Administration (BPA) - ASD Calculators for Fan & Pump Applications,  	2004

[O]	California Statewide Residential Appliance Saturation Study (RASS), Prepared for California Energy Commission by KEMA-XENERGY, Itron and Roper ASW, June 2004, p. 3-4, 26, 28

# Appendix A – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |