## Original site results (hidden)
Location | motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
Westin | EF 7 | 1.9366 | 0.32509 | 83.21% | 24 | 46.4783 | 16964.5828 | 7.8021 | 2847.7691 | 14116.8137 | 83.21% | 2117.5221 | 57%
| EF 8 | 2.2391 | 0.95633 | 57.29% | 24 | 53.7374 | 19614.1355 | 22.9519 | 8377.4279 | 11236.7076 | 57.29% | 1685.5061
| EF 9 | 2.1772 | 0.62333 | 71.37% | 24 | 52.2528 | 19072.2728 | 14.9599 | 5460.3531 | 13611.9197 | 71.37% | 2041.788
| EF 10/ MUA | 3.8128 | 3.0383 | 20.31% | 24 | 91.5074 | 33400.1923 | 72.9192 | 26615.5062 | 6784.6861 | 20.31% | 1017.7029
| SF 2 | 0.59318 | 0.13898 | 76.57% | 24 | 14.2362 | 5196.2302 | 3.3356 | 1217.4934 | 3978.7367 | 76.57% | 596.8105
| SF 3 | 1.3455 | 0.12288 | 90.87% | 24 | 32.2925 | 11786.7548 | 2.9492 | 1076.4661 | 10710.2886 | 90.87% | 1606.5433
|  | 12.1044 | 5.2049 |  |  | 290.5046 | 106034.1684 | 124.9179 | 45595.0159 | 60439.1526 | 57% | 9065.8729
| motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
Marriott | Ex 159 | 1.5007 | 0.097636 | 93.49% | 24 | 36.0157 | 13145.7266 | 2.3433 | 855.2926 | 12290.434 | 93.49% | 1843.5651 | 69.39%
| Ex 160 | 6.3888 | 3.7627 | 41.1% | 24 | 153.3306 | 55965.682 | 90.3042 | 32961.043 | 23004.639 | 41.1% | 3450.6959
| Ex 161 | 1.8586 | 0.39967 | 78.5% | 24 | 44.6069 | 16281.5061 | 9.5921 | 3501.104 | 12780.4021 | 78.5% | 1917.0603
| Ex 162 | 1.6943 | 0.40757 | 75.94% | 24 | 40.6637 | 14842.2375 | 9.7817 | 3570.3072 | 11271.9304 | 75.94% | 1690.7896
| Ex 163 | 1.9595 | 0.25864 | 86.8% | 24 | 47.0277 | 17165.1283 | 6.2073 | 2265.6603 | 14899.4681 | 86.8% | 2234.9202
| Ex 164 | 5.5292 | 0.86801 | 84.3% | 24 | 132.6996 | 48435.3619 | 20.8322 | 7603.7697 | 40831.5923 | 84.3% | 6124.7388
|  | 18.931 | 5.7942 |  |  | 454.3442 | 165835.6425 | 139.0608 | 50757.1767 | 115078.4657 |  | 17261.7699
| motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
| MUA 6 | 0.79 | 0 | 100% | 24 | 18.96 | 6920.4 | 0 | 0 | 6920.4 | 100% | 1038.06 | 45.43%
| MUA 7 | 2.12 | 2.12 | 0% | 24 | 50.88 | 18571.2 | 50.88 | 18571.2 | 0 | 0% | 0
| MUA 8 | 2.78 | 2.78 | 0% | 24 | 66.72 | 24352.8 | 66.72 | 24352.8 | 0 | 0% | 0
| MUA 9 | 1.28 | 0 | 100% | 24 | 30.72 | 11212.8 | 0 | 0 | 11212.8 | 100% | 1681.92
| MUA 10 | 1.03 | 0 | 100% | 24 | 24.72 | 9022.8 | 0 | 0 | 9022.8 | 100% | 1353.42
| MUA 11 | 0.98 | 0 | 100% | 24 | 23.52 | 8584.8 | 0 | 0 | 8584.8 | 100% | 1287.72
|  | 8.98 | 4.9 |  |  | 215.52 | 78664.8 | 117.6 | 42924 | 35740.8 |  | 5361.12
|  | 27.911 | 10.6942 |  |  | 669.8642 | 244500.4425 | 256.6608 | 93681.1767 | 150819.2657 | 61.68% | 22622.8899
| motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
El Pollo Loco | EF 1 | 2.8038 | 1.8665 | 33.43% | 15.3596 | 43.0659 | 15675.9746 | 28.6682 | 10435.2389 | 5240.7356 | 33.43% | 786.1103 | 37.51%
| EF 2 | 1.9025 | 1.0744 | 43.53% | 15.3596 | 29.2223 | 10636.9281 | 16.5031 | 6007.1124 | 4629.8157 | 43.53% | 694.4724
|  | 4.7064 | 2.9409 |  |  | 72.2882 | 26312.9027 | 45.1713 | 16442.3513 | 9870.5514 |  | 1480.5827
| motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
Panda Express | EF 1 | 1.538 | 0.76565 | 50.22% | 13.0982 | 20.1455 | 7353.1199 | 10.0286 | 3660.4544 | 3692.6656 | 50.22% | 553.8998 | 61.17%
| EF 2/MUA | 3.6116 | 1.2338 | 65.84% | 13.0982 | 47.3062 | 17266.7794 | 16.16 | 5898.3915 | 11368.3879 | 65.84% | 1705.2582
|  | 5.1497 | 1.9994 |  |  | 67.4518 | 24619.8994 | 26.1886 | 9558.8459 | 15061.0535 |  | 2259.158
| motor | Average operational kW before | Average operational kW with Melink | operational kW% savings | hours of operation per day | kWh per day before | kWh per year before | kWh per day with Melink | kWh per year with Melink | kWh savings per year | kWh% savings per year | $ savings per year
Farmer Boys | EF 1 | 0.98197 | 0.43824 | 55.37% | 15.8295 | 15.5441 | 5658.0622 | 6.9371 | 2525.1056 | 3132.9565 | 55.37% | 469.9435 | 48.79%
| EF 2 | 0.72976 | 0.13123 | 82.02% | 15.8295 | 11.5517 | 4204.8361 | 2.0772 | 756.1138 | 3448.7223 | 82.02% | 517.3084
| EF 3 | 1.0928 | 0.86677 | 20.68% | 15.8295 | 17.2979 | 6296.4201 | 13.7206 | 4994.2994 | 1302.1207 | 20.68% | 195.3181
|  | 2.8045 | 1.4362 |  |  | 44.3937 | 16159.3185 | 22.7349 | 8275.5189 | 7883.7996 |  | 1182.5699

## Study Summary
| Institutional Cafeteria | Casual Dining Restaurant | Hotel Main Kitchen | Supermarket | University Dining | University Dining | Hotel Main Kitchen | Hotel Main Kitchen | Quick Service Restaurant | Quick Service Restaurant | Quick Service Restaurant | Average
Rated Exhaust Fan Horsepower (HP) | 6 | 3 | 15 | NA | 8 | 20 | 21 | 14 | 3 | 4 | 2.5 | 9.65
Base Case Total Fan Power (kW) | 7.3 | 3.9 | 14 | 8.49 | 12.7 | 12 | 27.9 | 12.1 | 4.7 | 5.2 | 2.9 | 10.11
Measure Case Total Fan Power (kW) | 1.9 | 2.1 | 5.3 | 2.33 | 5.8 | 6.6 | 10.7 | 5.2 | 2.9 | 2 | 1.4 | 4.2
Fan Power Reduction (kW) | 5.4 | 1.8 | 8.7 | 6.16 | 6.9 | 5.4 | 17.2 | 6.9 | 1.8 | 3.2 | 1.5 | 5.91
Estimate Exhaust Fan Speed Reduction (%) | 36 | 19 | 28 | 35 | 23 | 18 | 27 | 25 | 15 | 27 | 22 | 25
Base Case Daily Fan Energy Consumption (kWh/day) | 137.9 | 58.9 | 336 | 117.9 | 216.6 | 168 | 670 | 291 | 72 | 67 | 44 | 198.12
Measure Case Daily Fan Energy Consumption (kWh/day) | 34.8 | 31.6 | 127 | 30.7 | 97.9 | 77 | 257 | 125 | 45 | 26 | 23 | 79.55
Base Case Annual Fan Energy Consumption (kWh/yr) | 49644 | 21204 | 120960 | 42444 | 77976 | 60480 | 241200 | 104760 | 25920 | 24120 | 15840 | 71323
Measure Case Annual Fan Energy Consumption (kWh/yr) | 12528 | 11376 | 45720 | 11052 | 35244 | 27720 | 92520 | 45000 | 16200 | 9360 | 8280 | 28636
Annual Fan Energy Savings (kWh/yr) | 37116 | 9828 | 75240 | 31392 | 42732 | 32760 | 148680 | 59760 | 9720 | 14760 | 7560 | 42686
Site | San Ramon | Rancho Cucamonga | Mark Hopkins | Super Market | Berkley | UCSB | Desert Springs Marriot | Westin Mission Hills | Ell Pollo Loco | Panda Express | Farmer Boys
Source | a) ASHRAE | a) ASHRAE | b) FSTC - FN | c) FSTC - FN | d) PIER | e) PIER | f) ET07 | f) ET07 | f) ET07 | f) ET07 | f) ET07
ID

## Savings Calculations
Energy Svaings |  | Therms Savings
Average Rated Exhaust Fan Power (HP) | 9.65 | Climate Zone | OAC Output (kBtu/yr) | Base Case Heating Energy (kBtu/yr) | Measure Case Heating energy (kBtu/yr) | Natural Gas Savings (therms/yr) | Natural Gas Savings (therms/yr/Exh HP) | Fan Speed Reduction | 25%
Average Base Case Total Fan Power (kW) | 10.11 | 1 | 777247 | 971558.75 | 728669.0625 | 2429 | 170 | Efficiency | 80%
Average Measure Case Total Fan Power (kW) | 4.2 | 2 | 609224 | 761530 | 571147.5 | 1904 | 133 | kBtu/Therm | 100
Average Base Case Annual Fan Energy Consumption (kWh/yr) | 71323 | 3 | 510934 | 638667.5 | 479000.625 | 1597 | 112 | Avg HP | 14.3
Average Measure Case Annual Fan Energy Consumption (kWh/yr) | 28636 | 4 | 466873 | 583591.25 | 437693.4375 | 1459 | 102 | Note: Avg of 72 Sites
Average Annual Fan Energy Savings (kWh/yr) | 42686 | 5 | 486129 | 607661.25 | 455745.9375 | 1519 | 106
Normalized Base Case Fan Energy Consumption (kWh/yr/Exh HP) | 7390.9845 | 6 | 296319 | 370398.75 | 277799.0625 | 926 | 65
Normalized Measure Case Fan Energy Consumption (kWh/yr/Exh HP) | 2967.4611 | 7 | 245283 | 306603.75 | 229952.8125 | 767 | 54
Normalized Fan Energy Savings (kWh/yr/Exh HP) | 4423.5233 | 8 | 291176 | 363970 | 272977.5 | 910 | 64
Applied Electric Rate ($/kWh) | 0.13 | 9 | 260834 | 326042.5 | 244531.875 | 815 | 57
Average Base Case Annual Fan Energy Cost ($/yr) | 9271.99 | 10 | 312989 | 391236.25 | 293427.1875 | 978 | 68
Average Measure Case Annual Fan Energy Cost ($/yr) | 3722.68 | 11 | 533354 | 666692.5 | 500019.375 | 1667 | 117
Average Annual Fan Energy Cost Savings ($/yr) | 5549.18 | 12 | 539166 | 673957.5 | 505468.125 | 1685 | 118
Normalized Fan Energy Cost Savings ($/yr/Exh HP) | 575.0446 | 13 | 427560 | 534450 | 400837.5 | 1336 | 93
|  | 14 | 505617 | 632021.25 | 474015.9375 | 1580 | 110
|  | 15 | 165481 | 206851.25 | 155138.4375 | 517 | 36
Demand Savings |  | 16 | 964179 | 1205223.75 | 903917.8125 | 3013 | 211
Average Rated Exhaust Fan Power (HP) | 9.65 | Average | 462022.8125 | 577528.5156 | 433146.3867 | 1443.875 | 101
Average Base Case Total Fan Power (kW) | 10.11
Average Measure Case Total Fan Power (kW) | 4.2
Average Demand Reduction (kW) | 5.91
Normalized Demand Reduction (kW/Exh HP) | 0.61244
Coincident Demand Reduction (kWh/Exh HP) | 0.55119

## Overall Results (hidden)
| Desert Springs Marroitt | Westin Mission Hills | El Pollo Loco | Panda Express | Farmer Boys
Measured average kW without DCV system | 27.9 | 12.1 | 4.7 | 5.2 | 2.9 |  |  | Desert Springs Marroitt | Westin Mission Hills | El Pollo Loco | Panda Express | Farmer Boys | Average
Measured average kW with DCV system | 10.7 | 5.2 | 2.9 | 2 | 1.4 |  | base | 18.931 | 12.1044 | 4.7064 | 5.1497 | 2.8045 | 8.7392
Percentage average kW reduction | 61.65% | 57.02% | 38.3% | 61.54% | 51.72% |  | measure | 7.3854 | 4.3283 | 3.6718 | 2.3944 | 1.6457 | 3.8851
Measured Peak (2-5pm) average kW with DCV system | 7.3854 | 4.3283 | 3.6718 | 2.3944 | 1.6457 |  | savings | 11.5456 | 7.776 | 1.0346 | 2.7553 | 1.1588 | 4.8541
Peak (2-5pm) kW savings with DCV system | 11.5456 | 7.776 | 1.0346 | 2.7553 | 1.1588 | 4.8541 | hp | 21 | 14 | 3 | 4 | 2.3 | 8.86
Daily Operational Hours | 24 | 24 | 15.36 | 13.1 | 15.83 |  | kw/hp Savings | 0.54979 | 0.55543 | 0.34488 | 0.68881 | 0.50384 | 0.52855
Daily energy usage without DCV system (kWh/day) | 670 | 291 | 72 | 67 | 44
Daily energy usage with DCV system (kWh/day) | 257 | 125 | 45 | 26 | 23
Annual energy usage without DCV system (kWh/yr) | 244500 | 106034.1684 | 26312.9027 | 24619.8994 | 16159.3185
Annual energy usage with DCV system (kWh/yr) | 93681 | 45595.0159 | 16442.3513 | 9558.8459 | 8275.5189
Annual energy savings with DCV system (kWh/yr) | 150819.2657 | 60439.1526 | 9870.5514 | 15061.0535 | 7883.7996
Percentage energy usage reduction (kWh/yr) | 61.68% | 57% | 37.51% | 61.17% | 48.79%
Estimated annual operational savings (@$0.15 a kWh) | 22622.8899 | 9065.8729 | 1480.5827 | 2259.158 | 1182.5699
[7 empty] | Location | Measured average kW without DCV system | Measured average kW with DCV system | Percentage average kW reduction | Daily Operational Hours | Calculated kWH per day without DCV system | Calculated kWH per day with DCV system | Calculated kWH per year without DCV system | Calculated kWH per year with DCV system | Calculated kWH savings per year with DCV system | Estimated annual opreations savings (@$0.15 a kWh)
[7 empty] | Desert Springs Marriott | 27.9 | 10.7 | 61.65% | 24 | 670 | 257 | 244500 | 93681 | 150819.2657 | 22622.8899
[7 empty] | Westin Mission Hills | 12.1 | 5.2 | 57.02% | 24 | 291 | 125 | 106034.1684 | 45595.0159 | 60439.1526 | 9065.8729
[7 empty] | El Pollo Loco | 4.7 | 2.9 | 38.3% | 15.36 | 72 | 45 | 26312.9027 | 16442.3513 | 9870.5514 | 1480.5827
[7 empty] | Panda Express | 5.2 | 2 | 61.54% | 13.1 | 67 | 26 | 24619.8994 | 9558.8459 | 15061.0535 | 2259.158
[7 empty] | Farmer Boys | 2.9 | 1.4 | 51.72% | 15.83 | 44 | 23 | 16159.3185 | 8275.5189 | 7883.7996 | 1182.5699

## Desert Springs Marriott (hidden)
Desert Springs Marriott Exhaust fan motors | Ex 159 | Ex 160 | Ex 161 | Ex 162 | Ex 163 | Ex 164 | Combined Data
Measured average kW without DCV system | 1.5007 | 6.3888 | 1.8586 | 1.6943 | 1.9595 | 5.5292 | 18.931 | 21 HP exhaust
Measured average kW with DCV system | 0.097636 | 3.7627 | 0.39967 | 0.40757 | 0.25864 | 0.86801 | 5.7942 | 11.5 MUA
Percentage average kW reduction | 93.49% | 41.1% | 78.5% | 75.94% | 86.8% | 84.3% | 69.39%
Daily Operational Hours | 24 | 24 | 24 | 24 | 24 | 24 | 24
Daily energy usage without DCV system (kWh/day) | 36.0157 | 153.3306 | 44.6069 | 40.6637 | 47.0277 | 132.6996 | 454.3442
Daily energy usage with DCV system (kWh/day) | 2.3433 | 90.3042 | 9.5921 | 9.7817 | 6.2073 | 20.8322 | 139.0608
Annual energy usage without DCV system (kWh/yr) | 13145.7266 | 55965.682 | 16281.5061 | 14842.2375 | 17165.1283 | 48435.3619 | 165835.6425
Annual energy usage with DCV system (kWh/yr) | 855.2926 | 32961.043 | 3501.104 | 3570.3072 | 2265.6603 | 7603.7697 | 50757.1767
Annual energy savings with DCV system (kWh/yr) | 12290.434 | 23004.639 | 12780.4021 | 11271.9304 | 14899.4681 | 40831.5923 | 115078.4657
Percentage energy usage reduction (kWh/yr) | 93.49% | 41.1% | 78.5% | 75.94% | 86.8% | 84.3% | 69.39%
Estimated annual operational savings (@$0.15 a kWh) | 1843.5651 | 3450.6959 | 1917.0603 | 1690.7896 | 2234.9202 | 6124.7388 | 17261.7699
Desert Springs Marriott MUA | MUA 10 | MUA 11 | MUA 6 | MUA 7 | MUA 8 | MUA 9 | Combined Data
Measured average kW without DCV system | 1.03 | 0.98 | 0.79 | 2.12 | 2.78 | 1.28 | 8.98
Measured average kW with DCV system | 0 | 0 | 0 | 2.12 | 2.78 | 0 | 4.9
Percentage average kW reduction | 100% | 100% | 100% | 0% | 0% | 100% | 45.43%
Daily Operational Hours | 24 | 24 | 24 | 24 | 24 | 24 | 24
Daily energy usage without DCV system (kWh/day) | 24.72 | 23.52 | 18.96 | 50.88 | 66.72 | 30.72 | 215.52
Daily energy usage with DCV system (kWh/day) | 0 | 0 | 0 | 50.88 | 66.72 | 0 | 117.6
Annual energy usage without DCV system (kWh/yr) | 9022.8 | 8584.8 | 6920.4 | 18571.2 | 24352.8 | 11212.8 | 78664.8
Annual energy usage with DCV system (kWh/yr) | 0 | 0 | 0 | 18571.2 | 24352.8 | 0 | 42924
Annual energy savings with DCV system (kWh/yr) | 9022.8 | 8584.8 | 6920.4 | 0 | 0 | 11212.8 | 35740.8
Percentage energy usage reduction (kWh/yr) | 100% | 100% | 100% | 0% | 0% | 100% | 45.43%
Estimated annual operational savings (@$0.15 a kWh) | 1353.42 | 1287.72 | 1038.06 | 0 | 0 | 1681.92 | 5361.12

## Westin (hidden)
Westin Mission Hills | EF 10/ MUA | EF 7 | EF 8 | EF 9 | SF 2 | SF 3 | Combined Data
Measured average kW without DCV system | 3.8128 | 1.9366 | 2.2391 | 2.1772 | 0.59318 | 1.3455 | 12.1044 | 14 HP exhaust
Measured average kW with DCV system | 3.0383 | 0.32509 | 0.95633 | 0.62333 | 0.13898 | 0.12288 | 5.2049 | 8 HP MUA
Percentage average kW reduction | 20.31% | 83.21% | 57.29% | 71.37% | 76.57% | 90.87% | 57%
Daily Operational Hours | 24 | 24 | 24 | 24 | 24 | 24 | 24
Daily energy usage without DCV system (kWh/day) | 91.5074 | 46.4783 | 53.7374 | 52.2528 | 14.2362 | 32.2925 | 290.5046
Daily energy usage with DCV system (kWh/day) | 72.9192 | 7.8021 | 22.9519 | 14.9599 | 3.3356 | 2.9492 | 124.9179
Annual energy usage without DCV system (kWh/yr) | 33400.1923 | 16964.5828 | 19614.1355 | 19072.2728 | 5196.2302 | 11786.7548 | 106034.1684
Annual energy usage with DCV system (kWh/yr) | 6784.6861 | 14116.8137 | 11236.7076 | 13611.9197 | 3978.7367 | 10710.2886 | 60439.1526
Annual energy savings with DCV system (kWh/yr) | 26615.5062 | 2847.7691 | 8377.4279 | 5460.3531 | 1217.4934 | 1076.4661 | 45595.0159
Percentage energy usage reduction (kWh/yr) | 20.31% | 83.21% | 57.29% | 71.37% | 76.57% | 90.87% | 57%
Estimated annual operational savings (@$0.15 a kWh) | 1017.7029 | 2117.5221 | 1685.5061 | 2041.788 | 596.8105 | 1606.5433 | 9065.8729

## El Pollo Loco (hidden)
El Pollo Loco | EF 1 | EF 2 | Combined Data
Measured average kW without DCV system | 2.8038 | 1.9025 | 4.7064
Measured average kW with DCV system | 1.8665 | 1.0744 | 2.9409
Percentage average kW reduction | 33.43% | 43.53% | 37.51%
Daily Operational Hours | 15.3596 | 15.3596 | 15.3596
Daily energy usage without DCV system (kWh/day) | 43.0659 | 29.2223 | 72.2882
Daily energy usage with DCV system (kWh/day) | 28.6682 | 16.5031 | 45.1713
Annual energy usage without DCV system (kWh/yr) | 15675.9746 | 10636.9281 | 26312.9027
Annual energy usage with DCV system (kWh/yr) | 10435.2389 | 6007.1124 | 16442.3513
Annual energy savings with DCV system (kWh/yr) | 5240.7356 | 4629.8157 | 9870.5514
Percentage energy usage reduction (kWh/yr) | 33.43% | 43.53% | 37.51%
Estimated annual operational savings (@$0.15 a kWh) | 786.1103 | 694.4724 | 1480.5827

## Panda Express (hidden)
Panda Express | EF 1 | EF 2/MUA | Combined Data
Measured average kW without DCV system | 1.538 | 3.6116 | 5.1497
Measured average kW with DCV system | 0.76565 | 1.2338 | 1.9994
Percentage average kW reduction | 50.22% | 65.84% | 61.17%
Daily Operational Hours | 13.0982 | 13.0982 | 13.0982
Daily energy usage without DCV system (kWh/day) | 20.1455 | 47.3062 | 67.4518
Daily energy usage with DCV system (kWh/day) | 10.0286 | 16.16 | 26.1886
Annual energy usage without DCV system (kWh/yr) | 7353.1199 | 17266.7794 | 24619.8994
Annual energy usage with DCV system (kWh/yr) | 3660.4544 | 5898.3915 | 9558.8459
Annual energy savings with DCV system (kWh/yr) | 3692.6656 | 11368.3879 | 15061.0535
Percentage energy usage reduction (kWh/yr) | 50.22% | 65.84% | 61.17%
Estimated annual operational savings (@$0.15 a kWh) | 553.8998 | 1705.2582 | 2259.158

## Farmer Boys (hidden)
Farmer Boys | EF 1 | EF 2 | EF 3 | Combined Data
Measured average kW without DCV system | 0.98197 | 0.72976 | 1.0928 | 2.8045
Measured average kW with DCV system | 0.43824 | 0.13123 | 0.86677 | 1.4362
Percentage average kW reduction | 55.37% | 82.02% | 20.68% | 48.79%
Daily Operational Hours | 15.8295 | 15.8295 | 15.8295 | 15.8295
Daily energy usage without DCV system (kWh/day) | 15.5441 | 11.5517 | 17.2979 | 44.3937
Daily energy usage with DCV system (kWh/day) | 6.9371 | 2.0772 | 13.7206 | 22.7349
Annual energy usage without DCV system (kWh/yr) | 5658.0622 | 4204.8361 | 6296.4201 | 16159.3185
Annual energy usage with DCV system (kWh/yr) | 2525.1056 | 756.1138 | 4994.2994 | 8275.5189
Annual energy savings with DCV system (kWh/yr) | 3132.9565 | 3448.7223 | 1302.1207 | 7883.7996
Percentage energy usage reduction (kWh/yr) | 55.37% | 82.02% | 20.68% | 48.79%
Estimated annual operational savings (@$0.15 a kWh) | 469.9435 | 517.3084 | 195.3181 | 1182.5699