## Summary COP
| Base |  | Measure
48 kbtuh models (4 tons) | COP | HIR | COP | HIR | Flow Number | CFM | Gross Capacity Indoor Fan Heat Not Included (kBtuh) | Net Capacity Base Including Indoor Fan Heat (kBtuh) | Net Capacity Measure Including Indoor Fan Heat (kBtuh) | CFM/Ton Base | CFM/Ton Measure | Power Base Outdoor Unit Only (kW) | Total Power Base (kW) | Total Power Measure (kW) | Base Fan Power (kW) | Measure Fan Power (kW) | Base COP (kBtuh/kW) | Measure COP (kBtuh/kW) | Measure CFM/Ton | Measure COP kBtuh/kW % Increase | AHRI Reference
8.7 HSPF/15 SEER | 3.68 | 0.27174 | 3.8909 | 0.25701 | 1 | 1440 | 42.9 | 45.7006 | 45.3077 | 378.1134 | 381.3918 | 3.32 | 4.1408 | 4.0256 | 0.8208 | 0.7056 | 3.2347 | 3.2986 | 426.0078 | 2.6% | 3894845
[5 empty] | 2 | 1575 | 43.4 | 46.4631 | 46.0335 | 406.7742 | 410.5709 | 3.22 | 4.1178 | 3.9918 | 0.89775 | 0.77175 | 3.307 | 3.3799
[5 empty] | 3 | 1740 | 43.9 | 47.284 | 46.8093 | 441.5868 | 446.0647 | 3.32 | 4.3118 | 4.1726 | 0.9918 | 0.8526 | 3.214 | 3.2879
[5 empty] | 1 | 1415 | 43.4 | 46.1519 | 45.7659 | 367.9151 | 371.0183 | 3.21 | 4.0165 | 3.9033 | 0.80655 | 0.69335 | 3.3677 | 3.4653 | 414.5177 | 4.032% | 7045132
[5 empty] | 2 | 1610 | 44.2 | 47.3312 | 46.892 | 408.1875 | 412.0107 | 3.1 | 4.0177 | 3.8889 | 0.9177 | 0.7889 | 3.4527 | 3.5671
[5 empty] | 3 | 1815 | 45.1 | 48.6299 | 48.1348 | 447.8727 | 452.4797 | 3.21 | 4.2446 | 4.0994 | 1.0345 | 0.88935 | 3.3579 | 3.4768
[5 empty] | 1 | 1400 |  | 45.9261 | 45.5442 | 365.8051 | 368.8726 |  | 3.5739 | 3.4619 | 0.798 | 0.686 | 3.7662 | 3.8881 | 412.1404 | 6.291% | 4616532
[5 empty] | 2 | 1600 |  | 46.53 | 46.0935 | 412.637 | 416.5445 |  | 3.5244 | 3.3964 | 0.912 | 0.784 | 3.8694 | 4.0152
[5 empty] | 3 | 1800 |  | 47.1636 | 46.6726 | 457.9803 | 462.7987 |  | 3.4848 | 3.3408 | 1.026 | 0.882 | 3.9666 | 4.1376
[5 empty] | 1 | 1400 |  | 48.412 | 48.0301 | 347.0214 | 349.7808 |  | 3.9456 | 3.8336 | 0.798 | 0.686 | 3.5961 | 3.7012 | 390.9774 | 9.999% | 5934001
[5 empty] | 2 | 1600 |  | 49.098 | 48.6615 | 391.0546 | 394.5623 |  | 3.744 | 3.616 | 0.912 | 0.784 | 3.8434 | 3.9795
[5 empty] | 3 | 1800 |  | 49.784 | 49.293 | 433.8743 | 438.1964 |  | 3.5808 | 3.4368 | 1.026 | 0.882 | 4.0747 | 4.2455
9.0 HSPF/16 SEER | 3.57 | 0.28011 | 3.794 | 0.26358 | 1 | 1005 | 39.2 | 41.1546 | 40.8804 | 293.0416 | 295.0069 | 2.89 | 3.4628 | 3.3824 | 0.57285 | 0.49245 | 3.4832 | 3.566 | 330.1602 | 3.362% | 7785946
[5 empty] | 2 | 1100 | 39.7 | 41.8393 | 41.5392 | 315.4927 | 317.7718 | 2.81 | 3.437 | 3.349 | 0.627 | 0.539 | 3.5678 | 3.6615
[5 empty] | 3 | 1275 | 40.4 | 42.8797 | 42.5319 | 356.8124 | 359.7304 | 2.89 | 3.6168 | 3.5148 | 0.72675 | 0.62475 | 3.4748 | 3.5756
[5 empty] | 1 | 1200 |  | 47 | 46.6726 | 306.383 | 308.5319 |  | 4.0392 | 3.9432 | 0.684 | 0.588 | 3.4103 | 3.4933 | 345.1915 | 5.292% | 4640349
[5 empty] | 2 | 1300 |  | 47.42 | 47.0654 | 328.9751 | 331.454 |  | 3.9984 | 3.8944 | 0.741 | 0.637 | 3.4759 | 3.5687
[5 empty] | 3 | 1400 |  | 47.8 | 47.4181 | 351.4644 | 354.2952 |  | 3.9678 | 3.8558 | 0.798 | 0.686 | 3.5308 | 3.6333
[5 empty] | 4 | 1600 |  | 48.44 | 48.0035 | 396.3666 | 399.9707 |  | 3.9678 | 3.8398 | 0.912 | 0.784 | 3.578 | 3.6973
[5 empty] | 1 | 1400 |  | 48.412 | 48.0301 | 347.0214 | 349.7808 |  | 3.7812 | 3.6692 | 0.798 | 0.686 | 3.7524 | 3.867 | 390.9774 | 10.17% | 5934017
[5 empty] | 2 | 1600 |  | 49.098 | 48.6615 | 391.0546 | 394.5623 |  | 3.588 | 3.46 | 0.912 | 0.784 | 4.0105 | 4.1589
[5 empty] | 3 | 1800 |  | 49.784 | 49.293 | 433.8743 | 438.1964 |  | 3.4316 | 3.2876 | 1.026 | 0.882 | 4.2519 | 4.4381
9.4 HSPF/17 SEER | 3.74 | 0.26738 | 3.9308 | 0.2544 | 1 | 1440 | 42.3 | 45.1006 | 44.7077 | 383.1437 | 386.5103 | 3.14 | 3.9608 | 3.8456 | 0.8208 | 0.7056 | 3.3373 | 3.4372 | 431.6753 | 4.126% | 8329185
[5 empty] | 2 | 1575 | 42.9 | 45.9631 | 45.5335 | 411.1992 | 415.0793 | 3.02 | 3.9177 | 3.7917 | 0.89775 | 0.77175 | 3.4385 | 3.5527
[5 empty] | 3 | 1740 | 43.8 | 47.184 | 46.7093 | 442.5227 | 447.0197 | 3.17 | 4.1618 | 4.0226 | 0.9918 | 0.8526 | 3.3228 | 3.4378
[5 empty] | 1 | 1200 |  | 47.51 | 47.1826 | 303.0941 | 305.197 |  | 3.65 | 3.554 | 0.684 | 0.588 | 3.8149 | 3.9179 | 341.486 | 6.079% | 4643185
[5 empty] | 2 | 1300 |  | 47.93 | 47.5754 | 325.4747 | 327.9008 |  | 3.61 | 3.506 | 0.741 | 0.637 | 3.8913 | 4.0067
[5 empty] | 3 | 1400 |  | 48.3 | 47.9181 | 347.8261 | 350.5984 |  | 3.57 | 3.458 | 0.798 | 0.686 | 3.9652 | 4.0937
[5 empty] | 4 | 1600 |  | 48.91 | 48.4735 | 392.5578 | 396.0925 |  | 3.53 | 3.402 | 0.912 | 0.784 | 4.0608 | 4.2136

## Summary EER
| Base | Measure
48 kbtuh models (4 tons) | EER (kBtuh/kW) | EER (kBtuh/kW) | EIR (kW/kW) | Flow Number | CFM | Gross Capacity Indoor Fan Heat Not Included (kBtuh) | Net Capacity Base Including Indoor Fan Heat (kBtuh) | Net Capacity Measure Including Indoor Fan Heat (kBtuh) | CFM/Ton Base | CFM/Ton Measure | Power Base Outdoor Unit Only (kW) | Total Power Base (kW) | Total Power Measure (kW) | Base kW/CFM | Base Fan Power (kW) | Measure kW/CFM | Measure Fan Power (kW) | Base EER (kBtuh/kW) | Measure EER (kBtuh/kW) | Measure Flow | Measure EER kBtuh/kW % Increase | AHRI Reference
15 SEER Unit | 12.78 | 13.3185 | 0.25619 | 1 | 1395 | 46.5 | 43.7869 | 44.1677 | 382.3057 | 379.0098 | 3.11 | 3.9051 | 3.7935 | 0.00057 | 0.79515 | 0.00049 | 0.68355 | 11.2126 | 11.6428 | 430.7311 | 2.242% | 6685265
|  |  |  | 2 | 1565 | 47.5 | 44.4563 | 44.8835 | 422.4371 | 418.4165 | 3.13 | 4.0221 | 3.8968 | 0.00057 | 0.89205 | 0.00049 | 0.76685 | 11.0532 | 11.5179
|  |  |  | 3 | 1810 | 48.5 | 44.9798 | 45.4739 | 482.883 | 477.6367 | 3.14 | 4.1717 | 4.0269 | 0.00057 | 1.0317 | 0.00049 | 0.8869 | 10.7821 | 11.2925
|  |  |  | 1 | 1400 | 48 | 45.2772 | 45.6594 | 371.0475 | 367.942 | 3.14 | 3.938 | 3.826 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.4975 | 11.934 | 418.0468 | 2.64% | 5290616
|  |  |  | 2 | 1565 | 49 | 45.9563 | 46.3835 | 408.6489 | 404.8853 | 3.14 | 4.032 | 3.9068 | 0.00057 | 0.89205 | 0.00049 | 0.76685 | 11.3978 | 11.8724
|  |  |  | 3 | 1715 | 49.5 | 46.1646 | 46.6327 | 445.7961 | 441.321 | 3.14 | 4.1175 | 3.9803 | 0.00057 | 0.97755 | 0.00049 | 0.84035 | 11.2117 | 11.7157
|  |  |  | 1 | 1410 | 48 | 45.2578 | 45.6426 | 373.8584 | 370.7059 | 3.07 | 3.8737 | 3.7609 | 0.00057 | 0.8037 | 0.00049 | 0.6909 | 11.6833 | 12.1361 | 421.2138 | 2.869% | 8110211
|  |  |  | 2 | 1565 | 49 | 45.9563 | 46.3835 | 408.6489 | 404.8853 | 3.08 | 3.9721 | 3.8468 | 0.00057 | 0.89205 | 0.00049 | 0.76685 | 11.5699 | 12.0575
|  |  |  | 3 | 1770 | 50 | 46.5576 | 47.0408 | 456.2088 | 451.5232 | 3.07 | 4.0789 | 3.9373 | 0.00057 | 1.0089 | 0.00049 | 0.8673 | 11.4143 | 11.9475
|  |  |  | 1 | 1400 | 44.0089 | 41.2861 | 41.6683 | 406.9164 | 403.1845 |  | 3.5017 | 3.3897 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.7903 | 12.2926 | 458.4591 | 3.145% | 3916504
|  |  |  | 2 | 1600 | 44.62 | 41.5083 | 41.945 | 462.5586 | 457.7424 |  | 3.5696 | 3.4416 | 0.00057 | 0.912 | 0.00049 | 0.784 | 11.6283 | 12.1876
|  |  |  | 3 | 1800 | 45.0662 | 41.5655 | 42.0568 | 519.6619 | 513.5909 |  | 3.6472 | 3.5032 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.3965 | 12.0053
|  |  |  | 1 | 1400 | 41.211 | 38.4882 | 38.8704 | 436.4971 | 432.2058 |  | 3.294 | 3.182 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.6843 | 12.2157 | 491.7868 | 3.972% | 4765138
|  |  |  | 2 | 1600 | 41.85 | 38.7383 | 39.175 | 495.6341 | 490.1086 |  | 3.348 | 3.22 | 0.00057 | 0.912 | 0.00049 | 0.784 | 11.5706 | 12.1661
|  |  |  | 3 | 1800 | 42.327 | 38.8263 | 39.3176 | 556.3241 | 549.3721 |  | 3.402 | 3.258 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.4128 | 12.068
|  |  |  | 1 | 1400 | 40.3008 | 37.578 | 37.9602 | 447.0698 | 442.5692 |  | 3.4944 | 3.3824 | 0.00057 | 0.798 | 0.00049 | 0.686 | 10.7538 | 11.2229 | 503.6987 | 7.043% | 4611463
|  |  |  | 2 | 1600 | 41.8656 | 38.7539 | 39.1906 | 495.4346 | 489.9135 |  | 3.5424 | 3.4144 | 0.00057 | 0.912 | 0.00049 | 0.784 | 10.94 | 11.478
|  |  |  | 3 | 1800 | 43.1616 | 39.6609 | 40.1522 | 544.6172 | 537.9529 |  | 3.5904 | 3.4464 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.0464 | 11.6505
|  |  |  | 1 | 1400 |  | 45 | 45.3821 | 373.3333 | 370.1896 |  | 3.82 | 3.708 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.7801 | 12.239 | 420.6222 | 5.953% | 7541180
|  |  |  | 2 | 1550 |  | 45.5 | 45.9231 | 408.7912 | 405.025 |  | 3.83 | 3.706 | 0.00057 | 0.8835 | 0.00049 | 0.7595 | 11.8799 | 12.3916
|  |  |  | 3 | 1800 |  | 46.5 | 46.9913 | 464.5161 | 459.6593 |  | 3.85 | 3.706 | 0.00057 | 1.026 | 0.00049 | 0.882 | 12.0779 | 12.6798
|  |  |  | 1 | 1400 |  | 47.874 | 48.2561 | 350.9212 | 348.1422 |  | 3.7323 | 3.6203 | 0.00057 | 0.798 | 0.00049 | 0.686 | 12.8269 | 13.3293 | 395.3712 | 6.161% | 5561827
|  |  |  | 2 | 1600 |  | 48.48 | 48.9167 | 396.0396 | 392.5037 |  | 3.7224 | 3.5944 | 0.00057 | 0.912 | 0.00049 | 0.784 | 13.0239 | 13.6092
|  |  |  | 3 | 1800 |  | 49.086 | 49.5773 | 440.044 | 435.683 |  | 3.7224 | 3.5784 | 0.00057 | 1.026 | 0.00049 | 0.882 | 13.1867 | 13.8546
|  |  |  | 1 | 1400 |  | 46.431 | 46.8131 | 361.8272 | 358.8736 |  | 3.6921 | 3.5801 | 0.00057 | 0.798 | 0.00049 | 0.686 | 12.5758 | 13.0759 | 407.6587 | 3.895% | 8439429
|  |  |  | 2 | 1600 |  | 47.025 | 47.4617 | 408.2935 | 404.5364 |  | 3.7572 | 3.6292 | 0.00057 | 0.912 | 0.00049 | 0.784 | 12.516 | 13.0777
|  |  |  | 3 | 1800 |  | 47.619 | 48.1103 | 453.6005 | 448.968 |  | 3.8316 | 3.6876 | 0.00057 | 1.026 | 0.00049 | 0.882 | 12.428 | 13.0465
16 SEER Unit | 12.48 | 12.966 | 0.26315 | 1 | 1440 | 48 | 45.1994 | 45.5925 | 382.3057 | 379.0098 | 3.13 | 3.9508 | 3.8356 | 0.00057 | 0.8208 | 0.00049 | 0.7056 | 11.4406 | 11.8867 | 430.7311 | 3.149% | 6685288
|  |  |  | 2 | 1610 | 49.5 | 46.3688 | 46.8083 | 416.6594 | 412.7475 | 3.15 | 4.0677 | 3.9389 | 0.00057 | 0.9177 | 0.00049 | 0.7889 | 11.3993 | 11.8836
|  |  |  | 3 | 1815 | 50.5 | 46.9701 | 47.4655 | 463.6991 | 458.8592 | 3.16 | 4.1945 | 4.0493 | 0.00057 | 1.0345 | 0.00049 | 0.88935 | 11.1979 | 11.7218
|  |  |  | 1 | 1395 | 48 | 45.2869 | 45.6677 | 369.6429 | 366.5608 | 3.13 | 3.9251 | 3.8135 | 0.00057 | 0.79515 | 0.00049 | 0.68355 | 11.5376 | 11.9751 | 416.4644 | 2.631% | 6685290
|  |  |  | 2 | 1565 | 49 | 45.9563 | 46.3835 | 408.6489 | 404.8853 | 3.14 | 4.032 | 3.9068 | 0.00057 | 0.89205 | 0.00049 | 0.76685 | 11.3978 | 11.8724
|  |  |  | 3 | 1810 | 50.5 | 46.9798 | 47.4739 | 462.326 | 457.5146 | 3.16 | 4.1917 | 4.0469 | 0.00057 | 1.0317 | 0.00049 | 0.8869 | 11.2078 | 11.7309
|  |  |  | 1 | 1440 | 50 | 47.1994 | 47.5925 | 366.1061 | 363.0825 | 3.15 | 3.9708 | 3.8556 | 0.00057 | 0.8208 | 0.00049 | 0.7056 | 11.8866 | 12.3437 | 412.4796 | 2.461% | 5290603
|  |  |  | 2 | 1575 | 50.5 | 47.4369 | 47.8668 | 398.4242 | 394.8458 | 3.15 | 4.0477 | 3.9217 | 0.00057 | 0.89775 | 0.00049 | 0.77175 | 11.7193 | 12.2055
|  |  |  | 3 | 1740 | 51.5 | 48.116 | 48.5909 | 433.9515 | 429.7098 | 3.15 | 4.1418 | 4.0026 | 0.00057 | 0.9918 | 0.00049 | 0.8526 | 11.6172 | 12.1398
|  |  |  | 1 | 1440 | 50.5 | 47.6994 | 48.0925 | 362.2685 | 359.3076 | 3.07 | 3.8908 | 3.7756 | 0.00057 | 0.8208 | 0.00049 | 0.7056 | 12.2595 | 12.7377 | 408.1558 | 3.092% | 8110296
|  |  |  | 2 | 1575 | 51.5 | 48.4369 | 48.8668 | 390.1986 | 386.7657 | 3.08 | 3.9777 | 3.8518 | 0.00057 | 0.89775 | 0.00049 | 0.77175 | 12.177 | 12.6869
|  |  |  | 3 | 1740 | 52.5 | 49.116 | 49.5909 | 425.1162 | 421.0447 | 3.08 | 4.0718 | 3.9326 | 0.00057 | 0.9918 | 0.00049 | 0.8526 | 12.0625 | 12.6102
|  |  |  | 1 | 1400 | 41.5602 | 38.8374 | 39.2196 | 432.5725 | 428.3576 |  | 3.458 | 3.346 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.2312 | 11.7213 | 487.365 | 7.078% | 4611476
|  |  |  | 2 | 1600 | 43.1739 | 40.0622 | 40.4989 | 479.2553 | 474.087 |  | 3.5055 | 3.3775 | 0.00057 | 0.912 | 0.00049 | 0.784 | 11.4284 | 11.9908
|  |  |  | 3 | 1800 | 44.5104 | 41.0097 | 41.501 | 526.7048 | 520.4692 |  | 3.553 | 3.409 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.5423 | 12.174
|  |  |  | 1 | 1400 | 44.8742 | 42.1514 | 42.5336 | 398.563 | 394.9821 |  | 3.4404 | 3.3284 | 0.00057 | 0.798 | 0.00049 | 0.686 | 12.2519 | 12.779 | 449.0477 | 3.778% | 3656148
|  |  |  | 2 | 1600 | 45.57 | 42.4583 | 42.895 | 452.2089 | 447.6047 |  | 3.4968 | 3.3688 | 0.00057 | 0.912 | 0.00049 | 0.784 | 12.142 | 12.733
|  |  |  | 3 | 1800 | 46.0894 | 42.5887 | 43.08 | 507.1769 | 501.3926 |  | 3.5532 | 3.4092 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.986 | 12.6364
|  |  |  | 1 | 1400 |  | 44.8 | 45.1821 | 375 | 371.8283 |  | 3.74 | 3.628 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.9786 | 12.4537 | 422.5 | 5.876% | 5983782
|  |  |  | 2 | 1500 |  | 45.5 | 45.9094 | 395.6044 | 392.0762 |  | 3.79 | 3.67 | 0.00057 | 0.855 | 0.00049 | 0.735 | 12.0053 | 12.5094
|  |  |  | 3 | 1800 |  | 47.1 | 47.5913 | 458.5987 | 453.8642 |  | 3.85 | 3.706 | 0.00057 | 1.026 | 0.00049 | 0.882 | 12.2338 | 12.8417
|  |  |  | 1 | 1600 |  | 44.736 | 45.1727 | 429.1845 | 425.0351 |  | 3.869 | 3.741 | 0.00057 | 0.912 | 0.00049 | 0.784 | 11.5627 | 11.9583 | 483.5479 | 3.258% | 7021248
|  |  |  | 2 | 1700 |  | 45.12 | 45.584 | 452.1277 | 447.5251 |  | 3.9114 | 3.7754 | 0.00057 | 0.969 | 0.00049 | 0.833 | 11.5355 | 11.9511
|  |  |  | 3 | 1800 |  | 45.504 | 45.9953 | 474.6835 | 469.6129 |  | 3.9538 | 3.8098 | 0.00057 | 1.026 | 0.00049 | 0.882 | 11.5089 | 11.9439
|  |  |  | 1 | 1400 |  | 47.369 | 47.7511 | 354.6623 | 351.824 |  | 3.8509 | 3.7389 | 0.00057 | 0.798 | 0.00049 | 0.686 | 12.3008 | 12.7714 | 399.5862 | 3.724% | 8439809
|  |  |  | 2 | 1600 |  | 47.975 | 48.4117 | 400.2084 | 396.598 |  | 3.9188 | 3.7908 | 0.00057 | 0.912 | 0.00049 | 0.784 | 12.2423 | 12.7708
|  |  |  | 3 | 1800 |  | 48.581 | 49.0723 | 444.6183 | 440.1666 |  | 3.9964 | 3.8524 | 0.00057 | 1.026 | 0.00049 | 0.882 | 12.1562 | 12.7381
17 SEER Unit | 13.26 | 13.8062 | 0.24714 | 1 | 1200 | 47.04 | 44.7062 | 45.0337 | 322.103 | 319.7602 |  | 3.65 | 3.554 | 0.00057 | 0.684 | 0.00049 | 0.588 | 12.2483 | 12.6713 | 362.9027 | 4.06% | 6406597
|  |  |  | 2 | 1300 | 47.69 | 45.1617 | 45.5166 | 345.4254 | 342.7324 |  | 3.68 | 3.576 | 0.00057 | 0.741 | 0.00049 | 0.637 | 12.2722 | 12.7283
|  |  |  | 3 | 1355 | 48 | 45.3647 | 45.7346 | 358.4281 | 355.5295 |  | 3.69 | 3.5816 | 0.00057 | 0.77235 | 0.00049 | 0.66395 | 12.294 | 12.7693
|  |  |  | 4 | 1500 | 48.71 | 45.7927 | 46.2022 | 393.0754 | 389.592 |  | 3.73 | 3.61 | 0.00057 | 0.855 | 0.00049 | 0.735 | 12.2769 | 12.7984
|  |  |  | 5 | 1600 | 49.12 | 46.0083 | 46.445 | 417.3164 | 413.3923 |  | 3.76 | 3.632 | 0.00057 | 0.912 | 0.00049 | 0.784 | 12.2362 | 12.7877
|  |  |  | 6 | 1700 | 49.47 | 46.1638 | 46.6278 | 441.905 | 437.5072 |  | 3.78 | 3.644 | 0.00057 | 0.969 | 0.00049 | 0.833 | 12.2126 | 12.7958
|  |  |  | 1 | 1200 | 45.3766 | 43.0428 | 43.3703 | 334.5508 | 332.0241 |  | 3.605 | 3.509 | 0.00057 | 0.684 | 0.00049 | 0.588 | 11.9397 | 12.3597 | 376.9272 | 4.122% | 4647058
|  |  |  | 2 | 1300 | 46.0071 | 43.4788 | 43.8337 | 358.7955 | 355.8909 |  | 3.6359 | 3.5319 | 0.00057 | 0.741 | 0.00049 | 0.637 | 11.9582 | 12.4108
|  |  |  | 3 | 1400 | 46.56 | 43.8372 | 44.2194 | 383.2359 | 379.924 |  | 3.6668 | 3.5548 | 0.00057 | 0.798 | 0.00049 | 0.686 | 11.9552 | 12.4393
|  |  |  | 4 | 1600 | 47.433 | 44.3213 | 44.758 | 433.2007 | 428.9737 |  | 3.708 | 3.58 | 0.00057 | 0.912 | 0.00049 | 0.784 | 11.9529 | 12.5022
|  |  |  | 1 | 1400 |  | 46.6 | 46.9821 | 360.515 | 357.5827 |  | 3.796 | 3.684 | 0.00057 | 0.798 | 0.00049 | 0.686 | 12.2761 | 12.753 | 406.1803 | 4.176% | 8874198
|  |  |  | 2 | 1600 |  | 47 | 47.4367 | 408.5106 | 404.7496 |  | 3.8376 | 3.7096 | 0.00057 | 0.912 | 0.00049 | 0.784 | 12.2472 | 12.7876
|  |  |  | 3 | 1800 |  | 47.4 | 47.8913 | 455.6962 | 451.0211 |  | 3.8792 | 3.7352 | 0.00057 | 1.026 | 0.00049 | 0.882 | 12.219 | 12.8216

## DEER DX SEER to EER
DEER 2015 Values - per 2015 DEER-PackagedAndSplitDXUpdate-24Nov2014) |  |  |  |  | delete data and adjust EER |  |  |  |  | vs.
[5 empty] | 1/eer |  |  |  |  | Prototype | Prototype EIR
Residential SEER-rated split Air Conditioners | Version |  | SEER | EER | EIR w/ fan Power | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | T1 | T2 | T3 | T4 | T5 | .inp | Model File Extracted
dxAC-Res-Split-lt45kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 12.17 | 0.28036 | 18 | 45 | Air | 0.754 | 0.239 | 0.2393 | 0.2393 | 0.2393 | 0.2393 | 0.2393 | cC13-mRE-HV-ResAC-lt45kBtuh.inp | SFM-w01-v14-hAC-t1-cC13-mRE-HV-ResAC-lt45kBtuh.inp
|  | Customer Average | [8 empty] | 0.25823 | 0.25823 | 0.25823 | 0.25823 | 0.25823 | cCAv-mRE-HV-ResAC-lt45kBtuh.inp | SFM-w01-v14-hAC-t1-cCAv-mRE-HV-ResAC-lt45kBtuh.inp
dxAC-Res-Split-SEER-15.0 | DEER2015 | Measure | 15 | 12.78 | 0.26698 | 18 | 65 | Air | 0.744 | 0.232 | 0.23218 | 0.23218 | 0.23218 | 0.23218 | 0.23218 | cMsr-mRE-HV-ResAC-lt45kBtuh-15S.inp | SFM-w01-v14-hAC-t1-cMsr-mRE-HV-ResAC-lt45kBtuh-15S.inp
dxAC-Res-Split-SEER-16.0 | DEER2015 | Measure | 16 | 12.48 | 0.2734 | 18 | 65 | Air | 0.724 | 0.238 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | cMsr-mRE-HV-ResAC-lt45kBtuh-16S.inp | SFM-w01-v14-hAC-t1-cMsr-mRE-HV-ResAC-lt45kBtuh-16S.inp
dxAC-Res-Split-SEER-17.0 | DEER2015 | Measure | 17 | 13.26 | 0.25732 | 18 | 65 | Air | 0.724 | 0.223 | 0.2225 | 0.2225 | 0.2225 | 0.2225 | 0.2225 | cMsr-mRE-HV-ResAC-lt45kBtuh-17S.inp | SFM-w01-v14-hAC-t1-cMsr-mRE-HV-ResAC-lt45kBtuh-17S.inp
dxAC-Res-Split-SEER-18.0 | DEER2015 | Measure | 18 | 14.04 |  | 18 | 65 | Air | 0.724 | 0.209 | Not Part of Workpaper
dxAC-Res-Split-SEER-19.0 | DEER2015 | Measure | 19 | 14.82 |  | 18 | 65 | Air | 0.724 | 0.201
dxAC-Res-Split-SEER-20.0 | DEER2015 | Measure | 20 | 15.6 |  | 18 | 65 | Air | 0.724 | 0.19
dxAC-Res-Split-SEER-21.0 | DEER2015 | Measure | 21 | 16.38 |  | 18 | 65 | Air | 0.724 | 0.18
dxAC-Res-Split-45to65kBTUh-SEER-14.0 | DEER2015 | Code/Standard | 14 | 11.82 |  | 45 | 65 | Air | 0.759 | 0.247
dxAC-Res-Split-SEER-10.0 | DEER2015 | pre-2001 | 10 | 8.52 |  | 18 | 65 | Air | 0.744 | 0.345
dxAC-Res-Split-SEER-13.0 | DEER2015 | post-2001 | 13 | 11.08 |  | 18 | 65 | Air | 0.744 | 0.258
dxAC-Res-EvapAC-SEER-17.4 | DEER2015 | Measure | 17.4 |  |  | 18 | 45 | Evap
Standard Conditions from ANSI/AHRI Standard 210/240
Air Entering Indoor Unit | Dry Bulb | 80 | oF
Air Entering Indoor Unit | Wet Bulb | 67 | oF
Air Entering Outdoor Unit | Dry Bulb | 95 | oF
Air Entering Outdoor Unit | Wet Bulb | 75 | oF

## DEER HP COP to HIR
[12 empty] | HVAC ID | SEER | EER | W/CFM | Spd | HSPF | HVAC Performance Curve Class
[12 empty] | 21405 | 14 | 11.9296 | 0.294 | 1 | 8.2 | HP one-speed, SEER 10 - 15
Split DX Selected Performance Maps | [11 empty] | 21501 | 15 | 12.7817 | 0.251 | 1 | 8.7 | HP one-speed, SEER 10 - 15
[12 empty] | 21604 | 16 | 12.48 | 0.271 | 2 | 9 | HP two-speed, SEER 16 - 18
This table lists the complete performance data sets used for the split DX measures for the DEER2015 update. | [11 empty] | 21704 | 17 | 13.26 | 0.271 | 2 | 9.4 | HP two-speed, SEER 16 - 18
[12 empty] | 21802 | 18 | 14.04 | 0.271 | 2 | 9.7 | HP two-speed, SEER 16 - 18
Indep. | Dependents
1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78
Equip ID | SEER | EER | Tot Cap | Sen/Total | EIR | cfm/Btuh | Fan W/cfm | Coil-BF | Crnk/Tot kW | Crnk Off | Total Capacity Curve Fit Coefficients | [5 empty] | Sensible Capacity Curve Fit Coefficients | [5 empty] | EIR Curve Fit Coefficients | [5 empty] | Coil-BF Curve Fit Coefficients | [5 empty] | Temperate EIR_PLR Curve Fit Coefficients |  |  |  | Moderate EIR_PLR Curve Fit Coefficients |  |  |  | Hot EIR_PLR Curve Fit Coefficients |  |  |  | Temp C-Loss Curve Fit Coefficients |  |  | Mod C-Loss Curve Fit Coefficients |  |  | Hot C-Loss Curve Fit Coefficients |  |  | Cmp Spd | Low Speed Ratios |  | HSPF | COP47 | Heat Cap | H-EIR | Total Capacity Curve Fit Coefficients | [5 empty] | HIR Curve Fit Coefficients | [5 empty] | BF-FFLOW Curve Coeffients
21405 | 14 | 11.9296 | 34895 | 0.744 | 0.24467 | 0.0321 | 0.294 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.2 | 3.48 | 33754 | 0.28764 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1
21501 | 15 | 12.7817 | 34895 | 0.744 | 0.23218 | 0.0321 | 0.251 | 0.12 | 0.0109 | 100 | 0.33897 | 0.00041807 | 0.00021371 | 0.0089003 | -2.5963e-05 | -0.0001473 | 4.678 | -0.073712 | 0.00028931 | 0.0064477 | -2.7952e-05 | -6.2571e-05 | 0.9275 | -0.00046154 | 3.96e-05 | -0.0068688 | 0.0002048 | -0.00019954 | 25.5462 | -0.65922 | 0.0051164 | -0.027638 | 0.00033263 | -0.00058485 | -7e-05 | 1.1695 | -0.21321 | 0.04377 | 0.00012 | 1.2018 | -0.26145 | 0.05955 | 7e-05 | 1.2314 | -0.30703 | 0.07557 | 0.85187 | 0.17007 | -0.02194 | 0.82723 | 0.20273 | -0.02996 | 0.8053 | 0.2327 | -0.038 | 1 | 1 | 1 | 8.7 | 3.68 | 33754 | 0.27157 | 0.48334 | -0.0018833 | 5.4506e-06 | 0.017815 | -1.6965e-06 | -6.4368e-05 | 1.3857 | 0.0056717 | 5.247e-05 | -0.028076 | 0.00026023 | -8.9704e-05 | 1 | 0 | 0 | 1
21604 | 16 | 12.48 | 58805 | 0.724 | 0.23814 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9 | 3.57 | 31641 | 0.2799 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21704 | 17 | 13.26 | 58805 | 0.724 | 0.2225 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9.4 | 3.74 | 31641 | 0.26765 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
21802 | 18 | 14.04 | 58805 | 0.724 | 0.2086 | 0.03 | 0.271 | 0.102 | 0.01 | 100 | 3.4462 | -0.09133 | 0.000924 | 0.0070176 | -2.0119e-05 | -0.00015082 | 0.25994 | 0.074843 | -0.00091895 | -0.0096756 | -3.0969e-05 | 0.00016487 | -3.0223 | 0.13455 | -0.0010034 | -0.015978 | 0.00023792 | -0.00017556 | 66.8974 | -2.0132 | 0.01588 | 0.10092 | 0.00035451 | -0.0023705 | -0.0072625 | 1.1134 | -0.13234 | 0.026242 | -0.00144 | 1.1191 | -0.13966 | 0.021968 | 0.0063475 | 1.1162 | -0.13862 | 0.016045 | 0.9595 | 0.093423 | -0.006875 | 0.94032 | 0.12407 | -0.010928 | 0.92296 | 0.15259 | -0.015618 | 2 | 0.739 | 0.686 | 9.7 | 3.86 | 31641 | 0.25912 | 0.42851 | -0.00097813 | 5.0142e-15 | 0.015309 | 3.9018e-05 | -5.0381e-05 | 1.366 | 0.0034688 | 6.2209e-05 | -0.02346 | 0.00022502 | -9.3635e-05 | 1.745 | -0.745 | 1 | 1.189
Data Key:
Dep Col(s) | Usage
1 | SEER
2 | Unit's rated EER.
3 | Actual unit total capacity. Value is for reference only and not used in simulations.
Data used as DOE-2 simulation inputs. Fields are used as follows:
4 | Ratio of sensible to total capacity (sensible heat ratio) is used to establish COOL-SH-CAP from design cooling load.
COOL-SH-CAP = COOLING-CAPACITY * Sen/Total
5 | Value is DOE-2 keyword COOLING-EIR
6 | cfm/Btuh is used to calculate design air flow as SUPPLY-CFM = cfm/Btuh * unit design capacity.
7 | Fan W/cfm is used to set the fan power input and fan Delta T via the following keywords:
SUPPLY-KW = (Fan W/cfm)/1,000
SUPPLY-DELTA-T = (Fan W/cfm)* 3.160
8 | Coil-BF is the design coil by-pass factor. The DOE-2 keyword COIL-BF = Coil-BF
9 | Crkn/Tot kW is used to set the keyword CRANKCASE-HEAT, and is the ratio of crankcase load heat to the design compressor load.
10 | Crnk Off is the temperature above which crankcase heat is deactivated and is the value used for the keyword CRANKCASE-MAX-T.
11 - 16 | The coefficients for the bi-quadratic total capacity off-design curve set by the keyword COOL-CAP-FT
17 - 22 | The coefficients for the bi-quadratic sensible capacity off-design curve set by the keyword COOL-SH-FT
23 - 28 | The coefficients for the bi-quadratic EIR off-design curve set by the keyword COOL-EIR-FT
29 - 34 | The coefficients for the bi-quadratic coil by-pass factor off-design curve set by the keyword COIL-BF-FT
For this curve set, the following should be set: OUTPUT-MAX = 0.4/CoilBF, where the Coil-BF is specified in column 8.
35 - 38 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in temperate climate zones
39 - 42 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in moderate climate zones
43 - 46 | The coefficients for the qubic equation that determines the EIR as a function of the part-load ratio for houses in hot climate zones
47 - 49 | The coefficients for the quadratic equation of the C-LOSS curve for houses in temperate climate zones
50 - 52 | The coefficients for the quadratic equation of the C-LOSS curve for houses in moderate climate zones
53 - 55 | The coefficients for the quadratic equation of the C-LOSS curve for houses in hot climate zones
56 | Number of compressor speeds (1 or 2). This is used as a flag to notify simulation when 2-speed equipment is to be simulated
57 | Low speed cfm ratio for 2-speed units (ratio of low speed to high speed cfm) used by keyword MIN-FLOW-RATIO
58 | Low speed capacity ratio for 2-speed units (ratio of lowspeed to high speed cooling capacity) used by keyword COOL-STAGES
Columns for heat pumps only. Colums BL and BN are descriptive only and not used in simulations
59 | For heat pumps only - rated HSPF
60 | For heat pumps only - rated COP at 47 outdoor temperature. Keyword HEATING-EIR = 1/(COP at 47 ODB)
61 | For heat pumps only - Actual unit rated heating capacity. Value is for reference only and not used in simulations.
62 | Heating EIR from manufacturers expanded ratings chart. Used only as a check with the rated COP at 47 ODB.
63 - 68 | For heat pumps only - the coefficients of the bi-quadratic heating capacity off-design curve set by keyword HEAT-CAP-FT
69 - 74 | For heat pumps only - the coefficients of the bi-quadratic heating EIR off-design curve set by keyword HEAT-EIR-FT
75 - 78 | The coefficients C0 & C1 and the Min and Max values of the linear curve-fit command assigned to keyword COIL-BF-FFLOW