## Data Collection
Data Collection Methodology
· Baseline and measure costs were determined by surveying manufacturers for cost information (information was collected directly from the market and not from Program data).
· Cost documentation for both base and measure case was collected from two manufacturers. Data was a combination of data from 2017 and 2016.
· Distributors provided costs for tier 1 and tier 2 equipment for both units under 150 tons and those greater than or equal to 150 tons.
· In some cases, only incremental costs were provided and actual prices were not provided. Therefore, baseline costs were determined by subtracting IMCs from Tier 2 cost data.
· Data collection is summarized in the SCE Measure Summary tab. The raw data is provided in the <150 tons Data and >150 tons Data tabs.

## <150 tons Data
Actual Tonnage | EER | IPLV | $/ton | IMC/ton | EER Tier | IEER Tier | Tier
145.3 | 11.4 | 18.3 |  | 196.7655 | 1 | 2 | 1 | Size | Title 24 Path A
147.3 | 11.5 | 18.4 |  | 206.2211 | 1 | 2 | 1 | <150 | 10.1 | 14
145 | 11.1 | 17 | 616.6276 | 139.0483 | 1 | 2 | 1
145 | 12.1 | 18.2 | 803.6552 | 326.0759 | 2 | 2 | 2 | Tier | DEER EER | DEER Min IPLV | Tier
[8 empty] | 1 | 11.1 | 15.1 | 1
[8 empty] | 2 | 12.1 | 16.6 | 2
[8 empty] | Size | Tier | Avg. Cost/ton | Avg IMC/ton | Units
[8 empty] | <150 | 0 | 477.5793 | 0
[9 empty] | 1 | 658.2576 | 180.6783 | 3 | 29.6889
[9 empty] | 2 | 803.6552 | 326.0759 | 1

## >150 tons Data
Actual Tonnage | EER | IPLV | $/ton | IMC/ton | EER Tier | IEER Tier | Tier
176.2 | 11.4 | 18.4 |  | 172.6627 | 1 | 2 | 1 | Size | Title 24 Path A
178.6 | 11.6 | 18.5 |  | 180.3428 | 1 | 2 | 1 | ≥150 | 10.1 | 14
196.5 | 11.6 | 18.8 |  | 146.5033 | 1 | 2 | 1
199.2 | 11.6 | 18.9 |  | 166.1221 | 1 | 2 | 1 | Tier | DEER EER | DEER Min IPLV | Tier
221.5 | 12.1 | 19.5 |  | 195.6233 | 2 | 2 | 2 | 1 | 11.1 | 15.4 | 1
224.5 | 12.1 | 19.6 |  | 148.6699 | 2 | 2 | 2 | 2 | 12.1 | 16.9 | 2
248.4 | 11.6 | 19.3 |  | 131.0105 | 1 | 2 | 1
251.7 | 11.6 | 19.4 |  | 141.2749 | 1 | 2 | 1 | Size | Tier | Avg. Cost/ton | Avg IMC/ton | Units
271.5 | 11.8 | 19.7 |  | 142.9781 | 1 | 2 | 1 | ≥150 | 0 | 450.0919 | 0
275.2 | 11.8 | 19.8 |  | 100.4108 | 1 | 2 | 1 |  | 1 | 589.3206 | 139.2287 | 11 | 30.9243
299.9 | 11.7 | 20 |  | 116.3531 | 1 | 2 | 1 |  | 2 | 639.1467 | 189.0548 | 3 | 40.801
304 | 11.8 | 20.1 |  | 73.199 | 1 | 2 | 1
225 | 11.1 | 17.6 | 576.9333 | 160.6578 | 1 | 2 | 1
225 | 12.1 | 18.6 | 639.1467 | 222.8711 | 2 | 2 | 2

## SCE Measure Summary
SCE 2018 Air-Cooled Chiller Measure Summary
Measure | Size | Tier | EER | IPLV | Percent over Title 24 | Tier kW/ton Demand Reduction | Tier kWh/ton Energy Savings | IMC | Baseline Cost | GMC | Proposed Incentive | Estimated Annual Participation | kW | kWh
Air-Cooled Chiller | < 150 tons | 1 | 11.1 | 15.1 | 10% | 0.0631 | 102 | 180.6783 | 477.5793 | 658.2576 | 100 | 793.7139 | 50.0834 | 80958.8227
|  | 2 | 12.1 | 16.6 | 20% | 0.116 | 187 | 326.0759 | 477.5793 | 803.6552 | 175 | 95.3828 | 11.0644 | 17836.5794
| ≥ 150 tons | 1 | 11.1 | 15.4 | 10% | 0.0631 | 102 | 139.2287 | 450.0919 | 589.3206 | 100 | 906.0477 | 57.1716 | 92416.8673
|  | 2 | 12.1 | 16.9 | 20% | 0.116 | 187 | 189.0548 | 450.0919 | 639.1467 | 175 | 204.8556 | 23.7632 | 38307.9889
[11 empty] | Total | 2000 | 142.0826 | 229520.2583
[11 empty] | Estimated TRC w P4P | 0.75