## Sheet1
Cooling Tower fan control scaling for NEW
File | OfL-w09-v11-hSVAV-cC13-mNE-HVAC-Chlr-Cent-gte300tons-0p461kwpton-ConstSpd_CTParametric.pd2
Keyword | CAPACITY-CTRL
(PV-A) Fan Power Design | 23.34 | kW |  | 31.2869 | hp | 100 ton | 1.2 Mbtu
Cooling capacity (CHW loop) | 7.736 | kBtu/hr |  | 644.6667 | tons
Vintage 2011
|  | kWh/year |  |  |  |  | kW Peak
CZ |  | Heat Reject | 2SPDover1SPD | VFDover1SPD | VFDover2SPD | kWh Scaling | Heat Reject | 2SPDover1SPD | VFDover1SPD | VFDover2SPD | kW Scaling
CZ06 | 0+2psdFan | 7480 | 62.25% |  | 25.85% | 8.022% | 6.91 | 57.63% |  | 6.622% | 2.055%
| VFD | 2359 |  | 88.09% |  |  | 5.83 |  | 64.26%
| 1spd | 19812 |  |  |  |  | 16.31
CZ08 | 0+2psdFan | 8159 | 62.16% |  | 25.22% | 9.51% | 7.25 | 58.36% |  | -0.05744% | -0.02166%
| VFD | 2722 |  | 87.38% |  |  | 7.26 |  | 58.3%
| 1spd | 21562 |  |  |  |  | 17.41
CZ09 | 0+2psdFan | 8646 | 60.48% |  | 23.13% | 5.254% | 17.21 | 18.55% |  | 9.229% | 2.096%
| VFD | 3585 |  | 83.61% |  |  | 15.26 |  | 27.78%
| 1spd | 21876 |  |  |  |  | 21.13
CZ10 | 0+2psdFan | 8530 | 61.65% |  | 23.98% | 2.047% | 10.24 | 44.8% |  | 5.067% | 0.4327%
| VFD | 3197 |  | 85.63% |  |  | 9.3 |  | 49.87%
| 1spd | 22243 |  |  |  |  | 18.55
Weighted average scaling | [5 empty] | 24.83% |  |  |  |  | 4.562%
DEER2014-EnergyImpact-Weights-Tables-v2.xlsx | [8 empty] | Adjusted Weighting
OfL | Ex | Multiple | Any |  | OfLExSCECZ01 | OfLExSCE | CZ01 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ02 | OfLExSCE | CZ02 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ03 | OfLExSCE | CZ03 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ04 | OfLExSCE | CZ04 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ05 | OfLExSCE | CZ05 | 1.3083
OfL | Ex | Multiple | Any |  | OfLExSCECZ06 | OfLExSCE | CZ06 | 117.1113 | 0.31036
OfL | Ex | Multiple | Any |  | OfLExSCECZ07 | OfLExSCE | CZ07 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ08 | OfLExSCE | CZ08 | 142.3205 | 0.37716
OfL | Ex | Multiple | Any |  | OfLExSCECZ09 | OfLExSCE | CZ09 | 85.6962 | 0.2271
OfL | Ex | Multiple | Any |  | OfLExSCECZ10 | OfLExSCE | CZ10 | 32.2181 | 0.085381
OfL | Ex | Multiple | Any |  | OfLExSCECZ11 | OfLExSCE | CZ11 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ12 | OfLExSCE | CZ12 | 0
OfL | Ex | Multiple | Any |  | OfLExSCECZ13 | OfLExSCE | CZ13 | 3.6548
OfL | Ex | Multiple | Any |  | OfLExSCECZ14 | OfLExSCE | CZ14 | 7.4876
OfL | Ex | Multiple | Any |  | OfLExSCECZ15 | OfLExSCE | CZ15 | 8.8041
OfL | Ex | Multiple | Any |  | OfLExSCECZ16 | OfLExSCE | CZ16 | 3.4486
[8 empty] | 402.0495 | 377.3461
0.93856