## Regression Results
Baseline For Undersized
All |  | 20.2037 |  | Climate Zone | Yearly Avg Temp. (°F)
Baseline For Properly-Sized |  |  |  | 6 | 61.5
Site Size Category | Regression Coefficients |  |  | 8 | 63.4
| Intercept | Temp. |  | 9 | 63.5
1 | 105.9085 | -1.1784 |  | 10 | 63.9
2 | 88.9213 | -0.7006 |  | 13 | 63.8
3 | 139.8546 | -0.9318 |  | 14 | 62.4
|  |  |  | 15 | 75.2
|  |  |  | 16 | 51.5
Treatment
Site Size Category | Regression Coefficients
| Intercept | Heater Size | Heater Size * Temp. | Annual Oper. Days: | 334
1 | 3.7032 | 13.1354 | -0.13649
2 | 5.8599 | 13.1949 | -0.13339 | Size Category | Proper-Sized Threshold
3 | 10.2591 | 16.6877 | -0.17943 | 1 | 2
4 | 229.5194 | 0 | -2.5769 | 2 | 2
|  |  |  | 3 | 6

## Sample Savings Estimate
Table 6: Sample Savings - Climate Zone 8
| Baseline Heater Size | New Heater Size | Baseline Heater Designation | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings
1 | 1 | 1 | Undersized | 20.2037 | 8.1851 | 4014.2086
| 3 | 3 | Proper-Sized | 31.2007 | 17.1489 | 4693.2878
2 | 1 | 1 | Undersized | 20.2037 | 10.5977 | 3208.4117
| 6 | 6 | Proper-Sized | 44.5033 | 34.2865 | 3412.3991
3 | 2 | 2 | Undersized | 40.4074 | 20.8828 | 6521.2125
| 6 | 6 | Proper-Sized | 80.7784 | 42.1303 | 12908.4472
4 | 10 | 10 | Undersized | 202.037 | 66.1428 | 45388.668

## SAVINGS CALCULATOR
Savings Estimate Calculator
Select these Parameter |  |  |  | Auto-Calculated Savings Estimates
Climate Zone | Site Size Category | Baseline Heater Size (kW) | New Heater Size (kW) | Baseline Heater Designation | Avg. Temp (F) | Baseline Daily kWh | Treatment Daily kWh | Annual kWh Savings | Annual kW Savings
6 | 1 | 1 | 1 | Undersized | 61.5 | 20.2037 | 8.4444 | 3927.5914 | 0.48997

## CBH Baseline Data w Heater Size
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 52 | 21.12 | 1 | 52
COCFD | 2 | 1 | 46 | 21.12 | 1 | 46
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 39 | 21.12 | 1 | 39
COCFD | 2 | 1 | 38 | 21.12 | 1 | 38
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 45 | 21.12 | 1 | 45
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 33 | 21.12 | 1 | 33
COCFD | 2 | 1 | 38 | 20.67 | 1 | 38
COCFD | 2 | 1 | 35 | 19.87 | 1 | 35
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 44 | 19.66 | 1 | 44
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 37 | 21.12 | 1 | 37
COCFD | 2 | 1 | 33 | 21.12 | 1 | 33
COCFD | 2 | 1 | 28 | 21.12 | 1 | 28
COCFD | 2 | 1 | 31 | 21.12 | 1 | 31
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 34 | 21.12 | 1 | 34
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 27 | 21.12 | 1 | 27
COCFD | 2 | 1 | 28 | 21.12 | 1 | 28
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 30 | 21.12 | 1 | 30
COCFD | 2 | 1 | 32 | 21.12 | 1 | 32
COCFD | 2 | 1 | 38 | 21.12 | 1 | 38
COCFD | 2 | 1 | 35 | 21.12 | 1 | 35
COCFD | 2 | 1 | 36 | 21.12 | 1 | 36
COCFD | 2 | 1 | 35 | 19.85 | 1 | 35
COCFD | 2 | 1 | 33 | 19.94 | 1 | 33
COCFD | 2 | 1 | 30 | 19.84 | 1 | 30
COCFD | 2 | 1 | 35 | 20.07 | 1 | 35
COCFD | 2 | 1 | 48 | 21.12 | 1 | 48
KE ECAM | 2 | 1 | 36 | 22.32 | 1 | 36
KE ECAM | 2 | 1 | 46 | 21.82 | 1 | 46
KE ECAM | 2 | 1 | 41 | 22.32 | 1 | 41
KE ECAM | 2 | 1 | 38 | 22.32 | 1 | 38
KE ECAM | 2 | 1 | 30 | 22.32 | 1 | 30
KE ECAM | 2 | 1 | 30 | 22.32 | 1 | 30
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 42 | 21.69 | 1 | 42
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 39 | 22.32 | 1 | 39
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 28 | 22.32 | 1 | 28
KE ECAM | 2 | 1 | 24 | 22.32 | 1 | 24
KE ECAM | 2 | 1 | 25 | 22.32 | 1 | 25
KE ECAM | 2 | 1 | 26 | 22.06 | 1 | 26
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 41 | 22.32 | 1 | 41
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 24 | 22.32 | 1 | 24
KE ECAM | 2 | 1 | 29 | 22.32 | 1 | 29
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 25 | 22.32 | 1 | 25
KE ECAM | 2 | 1 | 31 | 22.32 | 1 | 31
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 29 | 21.92 | 1 | 29
KE ECAM | 2 | 1 | 18 | 22.32 | 1 | 18
KE ECAM | 2 | 1 | 22 | 22.12 | 1 | 22
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 34 | 22.32 | 1 | 34
KE ECAM | 2 | 1 | 32 | 22.32 | 1 | 32
KE ECAM | 2 | 1 | 26 | 22.32 | 1 | 26
KRMC | 3 | 0 | 33 | 83 | 6 | 198
KRMC | 3 | 0 | 14 | 98.93 | 6 | 84
KRMC | 3 | 0 | 20 | 85.7 | 6 | 120
KRMC | 3 | 0 | 21 | 86.8 | 6 | 126
KRMC | 3 | 0 | 18 | 89.06 | 6 | 108
KRMC | 3 | 0 | 16 | 93.15 | 6 | 96
KRMC | 3 | 0 | 14 | 106.25 | 6 | 84
KRMC | 3 | 0 | 20 | 101.37 | 6 | 120
KRMC | 3 | 0 | 30 | 80.93 | 6 | 180
KRMC | 3 | 0 | 35 | 83.64 | 6 | 210
KRMC | 3 | 0 | 30 | 92.52 | 6 | 180
KRMC | 3 | 0 | 25 | 89.17 | 6 | 150
KRMC | 3 | 0 | 19 | 82.92 | 6 | 114
KRMC | 3 | 0 | 20 | 96.73 | 6 | 120
KRMC | 3 | 0 | 38 | 63.45 | 6 | 228
KRMC | 3 | 0 | 32 | 80.41 | 6 | 192
KRMC | 3 | 0 | 24 | 84.01 | 6 | 144
KRMC | 3 | 0 | 19 | 90.2 | 6 | 114
KRMC | 3 | 0 | 29 | 98.03 | 6 | 174
KRMC | 3 | 0 | 39 | 70.46 | 6 | 234
KRMC | 3 | 0 | 38 | 72.97 | 6 | 228
KRMC | 3 | 0 | 31 | 99.6 | 6 | 186
KRMC | 3 | 0 | 23 | 103.96 | 6 | 138
KRMC | 3 | 0 | 30 | 86.62 | 6 | 180
KRMC | 3 | 0 | 35 | 69.46 | 6 | 210
KRMC | 3 | 0 | 32 | 78.05 | 6 | 192
KRMC | 3 | 0 | 33 | 69.65 | 6 | 198
KRMC | 3 | 0 | 27 | 92.92 | 6 | 162
KRMC | 3 | 0 | 16 | 101.64 | 6 | 96
KRMC | 3 | 0 | 20 | 99.81 | 6 | 120
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 24 | 21.12 | 1 | 24
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 20 | 21.12 | 1 | 20
COCTV | 2 | 1 | 16 | 21.12 | 1 | 16
COCTV | 2 | 1 | 13 | 21.12 | 1 | 13
COCTV | 2 | 1 | 21 | 21.12 | 1 | 21
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 24 | 21.12 | 1 | 24
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 18 | 21.12 | 1 | 18
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 17 | 21.12 | 1 | 17
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 21 | 21.12 | 1 | 21
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 25 | 21.12 | 1 | 25
COCTV | 2 | 1 | 23 | 21.12 | 1 | 23
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 22 | 21.12 | 1 | 22
COCTV | 2 | 1 | 52 | 20.26 | 1 | 52
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 26 | 20.04 | 1 | 26
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 38 | 21.12 | 1 | 38
COCTV | 2 | 1 | 46 | 21.12 | 1 | 46
COCTV | 2 | 1 | 45 | 21.12 | 1 | 45
COCTV | 2 | 1 | 23 | 21.12 | 1 | 23
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 39 | 21.12 | 1 | 39
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 38 | 21.12 | 1 | 38
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 33 | 19.87 | 1 | 33
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 30 | 19.97 | 1 | 30
COCTV | 2 | 1 | 23 | 20.05 | 1 | 23
COCTV | 2 | 1 | 38 | 19.88 | 1 | 38
COCTV | 2 | 1 | 20 | 20.23 | 1 | 20
COCTV | 2 | 1 | 27 | 20.08 | 1 | 27
COCTV | 2 | 1 | 34 | 20.12 | 1 | 34
COCTV | 2 | 1 | 35 | 20.12 | 1 | 35
COCTV | 2 | 1 | 36 | 20.06 | 1 | 36
COCTV | 2 | 1 | 31 | 20.04 | 1 | 31
COCTV | 2 | 1 | 35 | 20.01 | 1 | 35
COCTV | 2 | 1 | 38 | 19.8 | 1 | 38
COCTV | 2 | 1 | 48 | 19.07 | 1 | 48
COCTV | 2 | 1 | 44 | 21.12 | 1 | 44
COCTV | 2 | 1 | 37 | 21.12 | 1 | 37
COCTV | 2 | 1 | 17 | 21.12 | 1 | 17
COCTV | 2 | 1 | 14 | 21.12 | 1 | 14
COCTV | 2 | 1 | 15 | 21.12 | 1 | 15
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 29 | 21.12 | 1 | 29
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 34 | 21.12 | 1 | 34
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 31 | 21.12 | 1 | 31
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 36 | 21.12 | 1 | 36
COCTV | 2 | 1 | 33 | 21.12 | 1 | 33
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 34 | 21.12 | 1 | 34
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 32 | 20.7 | 1 | 32
COCTV | 2 | 1 | 35 | 21.12 | 1 | 35
COCTV | 2 | 1 | 28 | 21.12 | 1 | 28
COCTV | 2 | 1 | 27 | 21.12 | 1 | 27
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
COCTV | 2 | 1 | 32 | 21.12 | 1 | 32
COCTV | 2 | 1 | 30 | 21.12 | 1 | 30
TCWWTP | 1 | 1 | 54 | 11.11 | 1 | 54
TCWWTP | 1 | 1 | 52 | 11.03 | 1 | 52
TCWWTP | 1 | 1 | 63 | 9.84 | 1 | 63
TCWWTP | 1 | 1 | 57 | 11.28 | 1 | 57
TCWWTP | 1 | 1 | 44 | 12.37 | 1 | 44
TCWWTP | 1 | 1 | 63 | 9.86 | 1 | 63
TCWWTP | 1 | 1 | 48 | 12.02 | 1 | 48
TCWWTP | 1 | 1 | 51 | 11.9 | 1 | 51
TCWWTP | 1 | 1 | 53 | 11.15 | 1 | 53
TCWWTP | 1 | 1 | 44 | 12.53 | 1 | 44
TCWWTP | 1 | 1 | 72 | 7.65 | 1 | 72
TCWWTP | 1 | 1 | 55 | 7.24 | 1 | 55
TCWWTP | 1 | 1 | 58 | 10.42 | 1 | 58
TCWWTP | 1 | 1 | 58 | 10 | 1 | 58
TCWWTP | 1 | 1 | 54 | 11.33 | 1 | 54
TCWWTP | 1 | 1 | 59 | 10.04 | 1 | 59
TCWWTP | 1 | 1 | 61 | 10.18 | 1 | 61
TCWWTP | 1 | 1 | 58 | 10.17 | 1 | 58
TCWWTP | 1 | 1 | 47 | 12.2 | 1 | 47
TCWWTP | 1 | 1 | 56 | 10.55 | 1 | 56
TCWWTP | 1 | 1 | 64 | 10 | 1 | 64
TCWWTP | 1 | 1 | 48 | 11.89 | 1 | 48
TCWWTP | 1 | 1 | 49 | 11.95 | 1 | 49
TCWWTP | 1 | 1 | 40 | 12.82 | 1 | 40
TCWWTP | 1 | 1 | 45 | 12.33 | 1 | 45
TCWWTP | 1 | 1 | 47 | 10.3 | 1 | 47
TCWWTP | 1 | 1 | 39 | 11.37 | 1 | 39
TCWWTP | 1 | 1 | 53 | 9.62 | 1 | 53
TCWWTP | 1 | 1 | 47 | 10.53 | 1 | 47
TCWWTP | 1 | 1 | 48 | 10.63 | 1 | 48
TCWWTP | 1 | 1 | 36 | 11.76 | 1 | 36
TCWWTP | 1 | 1 | 65 | 9.4 | 1 | 65
TCWWTP | 1 | 1 | 58 | 10.03 | 1 | 58
TCWWTP | 1 | 1 | 53 | 9.83 | 1 | 53
TCWWTP | 1 | 1 | 48 | 11.69 | 1 | 48
TCWWTP | 1 | 1 | 58 | 10.47 | 1 | 58
TCWWTP | 1 | 1 | 41 | 12.61 | 1 | 41
TCWWTP | 1 | 1 | 58 | 10.18 | 1 | 58
TCWWTP | 1 | 1 | 47 | 12 | 1 | 47
TCWWTP | 1 | 1 | 56 | 11.3 | 1 | 56
TCWWTP | 1 | 1 | 41 | 12.85 | 1 | 41
TCWWTP | 1 | 1 | 60 | 8.86 | 1 | 60
TCWWTP | 1 | 1 | 56 | 9.16 | 1 | 56
TCWWTP | 1 | 1 | 57 | 10.28 | 1 | 57
TCWWTP | 1 | 1 | 43 | 12.52 | 1 | 43
TCWWTP | 1 | 1 | 38 | 13.29 | 1 | 38
TCWWTP | 1 | 1 | 48 | 11.75 | 1 | 48
TCWWTP | 1 | 1 | 55 | 9.43 | 1 | 55
TCWWTP | 1 | 1 | 54 | 9.44 | 1 | 54
TCWWTP | 1 | 1 | 59 | 8.62 | 1 | 59
TCWWTP | 1 | 1 | 64 | 8 | 1 | 64
TCWWTP | 1 | 1 | 50 | 12.5 | 1 | 50
TCWWTP | 1 | 1 | 35 | 13.05 | 1 | 35
TCWWTP | 1 | 1 | 42 | 12.68 | 1 | 42
TCWWTP | 1 | 1 | 58 | 11.45 | 1 | 58
TCWWTP | 1 | 1 | 57 | 10.58 | 1 | 57
TCWWTP | 1 | 1 | 46 | 12.31 | 1 | 46
TCWWTP | 1 | 1 | 45 | 12.22 | 1 | 45
TCWWTP | 1 | 1 | 52 | 11.02 | 1 | 52
TCWWTP | 1 | 1 | 45 | 12.06 | 1 | 45
TCWWTP | 1 | 1 | 62 | 9.8 | 1 | 62
TCWWTP | 1 | 1 | 54 | 10.73 | 1 | 54
TCWWTP | 1 | 1 | 64 | 9.66 | 1 | 64
TCWWTP | 1 | 1 | 67 | 8.87 | 1 | 67
TCWWTP | 1 | 1 | 50 | 10.3 | 1 | 50
TCWWTP | 1 | 1 | 43 | 12.04 | 1 | 43
TCWWTP | 1 | 1 | 56 | 10.69 | 1 | 56
TCWWTP | 1 | 1 | 39 | 12.99 | 1 | 39
TCWWTP | 1 | 1 | 70 | 7.96 | 1 | 70
TCWWTP | 1 | 1 | 68 | 8.17 | 1 | 68
TCWWTP | 1 | 1 | 68 | 9.35 | 1 | 68
TCWWTP | 1 | 1 | 62 | 9.59 | 1 | 62
TCWWTP | 1 | 1 | 49 | 12.4 | 1 | 49
TCWWTP | 1 | 1 | 48 | 11.4 | 1 | 48
TCWWTP | 1 | 1 | 54 | 10.62 | 1 | 54
TCWWTP | 1 | 1 | 56 | 10.53 | 1 | 56
TCWWTP | 1 | 1 | 45 | 12.14 | 1 | 45
TCWWTP | 1 | 1 | 44 | 12.12 | 1 | 44
TCWWTP | 1 | 1 | 44 | 12.34 | 1 | 44
TCWWTP | 1 | 1 | 51 | 8.93 | 1 | 51
TCWWTP | 1 | 1 | 58 | 10.91 | 1 | 58
TCWWTP | 1 | 1 | 51 | 11.47 | 1 | 51
TCWWTP | 1 | 1 | 45 | 12.59 | 1 | 45
TCWWTP | 1 | 1 | 43 | 12.77 | 1 | 43
TCWWTP | 1 | 1 | 48 | 11.86 | 1 | 48
TCWWTP | 1 | 1 | 44 | 12.07 | 1 | 44
TCWWTP | 1 | 1 | 59 | 10.56 | 1 | 59
TCWWTP | 1 | 1 | 46 | 12.18 | 1 | 46
TCWWTP | 1 | 1 | 44 | 12.14 | 1 | 44
TCWP | 2 | 1 | 47 | 21.14 | 1 | 47
TCWP | 2 | 1 | 32 | 23.28 | 1 | 32
TCWP | 2 | 1 | 28 | 23.28 | 1 | 28
TCWP | 2 | 1 | 26 | 22.99 | 1 | 26
TCWP | 2 | 1 | 30 | 22.93 | 1 | 30
TCWP | 2 | 1 | 32 | 23.28 | 1 | 32
TCWP | 2 | 1 | 36 | 23.06 | 1 | 36
TCWP | 2 | 1 | 47 | 21.3 | 1 | 47
TCWP | 2 | 1 | 33 | 23.28 | 1 | 33
TCWP | 2 | 1 | 30 | 23.12 | 1 | 30
TCWP | 2 | 1 | 42 | 22.64 | 1 | 42
TCWP | 2 | 1 | 37 | 23.16 | 1 | 37
TCWP | 2 | 1 | 34 | 21.51 | 1 | 34
TCWP | 2 | 1 | 41 | 23.16 | 1 | 41
TCWP | 2 | 1 | 35 | 22.98 | 1 | 35
TCWP | 2 | 1 | 33 | 23.28 | 1 | 33
TCWP | 2 | 1 | 34 | 23.28 | 1 | 34
TCWP | 2 | 1 | 34 | 22.43 | 1 | 34
TCWP | 2 | 1 | 28 | 22.42 | 1 | 28
TCWP | 2 | 1 | 31 | 23.28 | 1 | 31
TCWP | 2 | 1 | 33 | 23.17 | 1 | 33
TCWP | 2 | 1 | 32 | 22.93 | 1 | 32
TCWP | 2 | 1 | 41 | 21.12 | 1 | 41
TCWP | 2 | 1 | 33 | 22.38 | 1 | 33
TCWP | 2 | 1 | 38 | 21 | 1 | 38
TCWP | 2 | 1 | 30 | 23.28 | 1 | 30
TCWP | 2 | 1 | 30 | 23.28 | 1 | 30
TCWP | 2 | 1 | 45 | 20.95 | 1 | 45
TCWP | 2 | 1 | 31 | 23.28 | 1 | 31
TCWP | 2 | 1 | 35 | 22.71 | 1 | 35
TCWP | 2 | 1 | 44 | 19.64 | 1 | 44
TCWP | 2 | 1 | 39 | 20.98 | 1 | 39
TCWP | 2 | 1 | 38 | 21.84 | 1 | 38
TCWP | 2 | 1 | 38 | 21.54 | 1 | 38
TCWP | 2 | 1 | 45 | 21.21 | 1 | 45
TCWP | 2 | 1 | 40 | 22.95 | 1 | 40
TCWP | 2 | 1 | 40 | 22.11 | 1 | 40
TCWP | 2 | 1 | 40 | 20.57 | 1 | 40
TCWP | 2 | 1 | 43 | 22.08 | 1 | 43
TCWP | 2 | 1 | 47 | 20.01 | 1 | 47
TCWP | 2 | 1 | 42 | 20.15 | 1 | 42
TCWP | 2 | 1 | 35 | 22.01 | 1 | 35
TCWP | 2 | 1 | 35 | 22.61 | 1 | 35
TCWP | 2 | 1 | 34 | 23.2 | 1 | 34
TCWP | 2 | 1 | 36 | 23.28 | 1 | 36
HCNW | 1 | 0 | 47 | 51.5 | 6 | 282
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 48 | 50.7 | 6 | 288
HCNW | 1 | 0 | 33 | 67.1 | 6 | 198
HCNW | 1 | 0 | 34 | 66.5 | 6 | 204
HCNW | 1 | 0 | 38 | 62.2 | 6 | 228
HCNW | 1 | 0 | 45 | 52.3 | 6 | 270
HCNW | 1 | 0 | 55 | 38.9 | 6 | 330
HCNW | 1 | 0 | 44 | 55.2 | 6 | 264
HCNW | 1 | 0 | 43 | 56.7 | 6 | 258
HCNW | 1 | 0 | 38 | 59.9 | 6 | 228
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 55 | 45.6 | 6 | 330
HCNW | 1 | 0 | 43 | 52.9 | 6 | 258
HCNW | 1 | 0 | 45 | 54.5 | 6 | 270
HCNW | 1 | 0 | 31 | 69.6 | 6 | 186
HCNW | 1 | 0 | 25 | 82.5 | 6 | 150
HCNW | 1 | 0 | 22 | 80 | 6 | 132
HCNW | 1 | 0 | 26 | 76.4 | 6 | 156
HCNW | 1 | 0 | 44 | 55.6 | 6 | 264
HCNW | 1 | 0 | 56 | 44.3 | 6 | 336
HCNW | 1 | 0 | 36 | 60.7 | 6 | 216
HCNW | 1 | 0 | 38 | 55.7 | 6 | 228
HCNW | 1 | 0 | 44 | 55.9 | 6 | 264
HCNW | 1 | 0 | 47 | 50.2 | 6 | 282
HCNW | 1 | 0 | 44 | 52.6 | 6 | 264
HCNW | 1 | 0 | 46 | 51.8 | 6 | 276
HCNW | 1 | 0 | 46 | 51.9 | 6 | 276
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 57 | 43.4 | 6 | 342
HCNW | 1 | 0 | 31 | 67.8 | 6 | 186
HCNW | 1 | 0 | 48 | 53.2 | 6 | 288
HCNW | 1 | 0 | 43 | 56.1 | 6 | 258
HCNW | 1 | 0 | 39 | 58.4 | 6 | 234
HCNW | 1 | 0 | 44 | 54.5 | 6 | 264
HCNW | 1 | 0 | 44 | 56.4 | 6 | 264
HCNW | 1 | 0 | 34 | 63.6 | 6 | 204
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 55 | 45.5 | 6 | 330
HCNW | 1 | 0 | 59 | 34.5 | 6 | 354
HCNW | 1 | 0 | 59 | 35.1 | 6 | 354
HCNW | 1 | 0 | 57 | 37.8 | 6 | 342
HCNW | 1 | 0 | 29 | 70.9 | 6 | 174
HCNW | 1 | 0 | 56 | 38.6 | 6 | 336
HCNW | 1 | 0 | 58 | 35.9 | 6 | 348
HCNW | 1 | 0 | 52 | 42.1 | 6 | 312
HCNW | 1 | 0 | 60 | 34 | 6 | 360
HCNW | 1 | 0 | 58 | 37.3 | 6 | 348
HCNW | 1 | 0 | 54 | 38.6 | 6 | 324
HCNW | 1 | 0 | 59 | 41.6 | 6 | 354
HCNW | 1 | 0 | 55 | 40.9 | 6 | 330
HCNW | 1 | 0 | 56 | 40.7 | 6 | 336
HCNW | 1 | 0 | 53 | 42.3 | 6 | 318
HCNW | 1 | 0 | 54 | 40.7 | 6 | 324
HCNW | 1 | 0 | 58 | 36.9 | 6 | 348
HCNW | 1 | 0 | 58 | 36.6 | 6 | 348
HCNW | 1 | 0 | 56 | 39.3 | 6 | 336
HCNW | 1 | 0 | 55 | 39.7 | 6 | 330
HCNW | 1 | 0 | 40 | 58.8 | 6 | 240
HCNW | 1 | 0 | 56 | 36.7 | 6 | 336
PCDC | 2 | 0 | 71 | 32 | 6 | 426
PCDC | 2 | 0 | 52 | 52.3 | 6 | 312
PCDC | 2 | 0 | 56 | 56.5 | 6 | 336
PCDC | 2 | 0 | 72 | 35.5 | 6 | 432
PCDC | 2 | 0 | 79 | 17 | 6 | 474
PCDC | 2 | 0 | 66 | 43.5 | 6 | 396
PCDC | 2 | 0 | 77 | 26.9 | 6 | 462
PCDC | 2 | 0 | 52 | 60.2 | 6 | 312
PCDC | 2 | 0 | 68 | 35.2 | 6 | 408
PCDC | 2 | 0 | 64 | 46.2 | 6 | 384
PCDC | 2 | 0 | 74 | 24.8 | 6 | 444
PCDC | 2 | 0 | 54 | 58.7 | 6 | 324
PCDC | 2 | 0 | 64 | 39.3 | 6 | 384
PCDC | 2 | 0 | 49 | 50.9 | 6 | 294
PCDC | 2 | 0 | 46 | 60.6 | 6 | 276
PCDC | 2 | 0 | 64 | 48.8 | 6 | 384
PCDC | 2 | 0 | 63 | 47.7 | 6 | 378
PCDC | 2 | 0 | 57 | 46.8 | 6 | 342
PCDC | 2 | 0 | 60 | 46.7 | 6 | 360
PCDC | 2 | 0 | 58 | 52.3 | 6 | 348
PCDC | 2 | 0 | 56 | 57.1 | 6 | 336
PCDC | 2 | 0 | 53 | 58.3 | 6 | 318
PCDC | 2 | 0 | 50 | 64.8 | 6 | 300
PCDC | 2 | 0 | 53 | 61.9 | 6 | 318
PCDC | 2 | 0 | 66 | 46.5 | 6 | 396
PCDC | 2 | 0 | 67 | 31.4 | 6 | 402
PCDC | 2 | 0 | 44 | 74.7 | 6 | 264
PCDC | 2 | 0 | 61 | 46 | 6 | 366
PCDC | 2 | 0 | 49 | 73.1 | 6 | 294
PCDC | 2 | 0 | 57 | 55.5 | 6 | 342
PCDC | 2 | 0 | 58 | 41.8 | 6 | 348
PCDC | 2 | 0 | 72 | 38.1 | 6 | 432
PCDC | 2 | 0 | 74 | 25.2 | 6 | 444
PCDC | 2 | 0 | 74 | 30.8 | 6 | 444
PCDC | 2 | 0 | 57 | 57.2 | 6 | 342
PCDC | 2 | 0 | 54 | 55.3 | 6 | 324
PCDC | 2 | 0 | 67 | 42.6 | 6 | 402
PCDC | 2 | 0 | 71 | 38.6 | 6 | 426
PCDC | 2 | 0 | 71 | 38.9 | 6 | 426
PCDC | 2 | 0 | 59 | 51.8 | 6 | 354
PCDC | 2 | 0 | 59 | 46.9 | 6 | 354
PCDC | 2 | 0 | 46 | 71.8 | 6 | 276
PCDC | 2 | 0 | 61 | 50.6 | 6 | 366
PCDC | 2 | 0 | 52 | 60.7 | 6 | 312
PCDC | 2 | 0 | 76 | 31.4 | 6 | 456
PCDC | 2 | 0 | 45 | 72.6 | 6 | 270
PCDC | 2 | 0 | 52 | 67.6 | 6 | 312
PCDC | 2 | 0 | 55 | 57.4 | 6 | 330
PCDC | 2 | 0 | 50 | 62.5 | 6 | 300
PCDC | 2 | 0 | 65 | 51.8 | 6 | 390
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 45 | 68.5 | 6 | 270
PCDC | 2 | 0 | 74 | 39.1 | 6 | 444
PCDC | 2 | 0 | 75 | 31.4 | 6 | 450
PCDC | 2 | 0 | 66 | 41.8 | 6 | 396
PCDC | 2 | 0 | 56 | 52.5 | 6 | 336
PCDC | 2 | 0 | 75 | 33.2 | 6 | 450
PCDC | 2 | 0 | 74 | 33.6 | 6 | 444
PCDC | 2 | 0 | 75 | 32.2 | 6 | 450
PCDC | 2 | 0 | 64 | 44.1 | 6 | 384
PCDC | 2 | 0 | 72 | 31.9 | 6 | 432
PCDC | 2 | 0 | 73 | 31.2 | 6 | 438
PCDC | 2 | 0 | 69 | 37.3 | 6 | 414
PCDC | 2 | 0 | 71 | 31.9 | 6 | 426
PCDC | 2 | 0 | 72 | 33.4 | 6 | 432
PCDC | 2 | 0 | 68 | 39.7 | 6 | 408
PCDC | 2 | 0 | 66 | 37.2 | 6 | 396
PCDC | 2 | 0 | 70 | 32.2 | 6 | 420
PCDC | 2 | 0 | 60 | 51.9 | 6 | 360
PCDC | 2 | 0 | 71 | 35.8 | 6 | 426
PCDC | 2 | 0 |  | 45.5 | 6
PCDC | 2 | 0 | 58 | 61.8 | 6 | 348
PCDC | 2 | 0 | 43 | 75.2 | 6 | 258
PCDC | 2 | 0 | 47 | 66.6 | 6 | 282
PCDC | 2 | 0 | 58 | 54 | 6 | 348
PCDC | 2 | 0 | 60 | 50.1 | 6 | 360
PCDC | 2 | 0 | 62 | 46.4 | 6 | 372
PCDC | 2 | 0 | 53 | 63 | 6 | 318
PCDC | 2 | 0 | 71 | 35.4 | 6 | 426
PCDC | 2 | 0 | 51 | 66.2 | 6 | 306
PCDC | 2 | 0 | 76 | 34.3 | 6 | 456
PCDC | 2 | 0 | 73 | 29.1 | 6 | 438
PCDC | 2 | 0 | 77 | 24.2 | 6 | 462
PCDC | 2 | 0 | 65 | 44.9 | 6 | 390
PCDC | 2 | 0 | 63 | 45.4 | 6 | 378
PCDC | 2 | 0 | 72 | 43.7 | 6 | 432
PCDC | 2 | 0 | 64 | 46 | 6 | 384
PCDC | 2 | 0 | 83 | 23.2 | 6 | 498
PCDC | 2 | 0 | 57 | 54.5 | 6 | 342
PCDC | 2 | 0 | 66 | 45.4 | 6 | 396
PCDC | 2 | 0 | 57 | 53.6 | 6 | 342
PCDC | 2 | 0 | 67 | 39.7 | 6 | 402
PCDC | 2 | 0 | 72 | 33.7 | 6 | 432
PCDC | 2 | 0 |  | 48.8 | 6
PCDC | 2 | 0 | 46 | 70.1 | 6 | 276
PCDC | 2 | 0 | 73 | 30.7 | 6 | 438
PCDC | 2 | 0 | 49 | 65.3 | 6 | 294
PCDC | 2 | 0 | 68 | 41.5 | 6 | 408
PCDC | 2 | 0 | 64 | 41.7 | 6 | 384
PCDC | 2 | 0 | 69 | 37.7 | 6 | 414
PCDC | 2 | 0 | 68 | 47.5 | 6 | 408
PCDC | 2 | 0 | 51 | 63.6 | 6 | 306
PCDC | 2 | 0 | 55 | 56.8 | 6 | 330
PCDC | 2 | 0 | 73 | 34.2 | 6 | 438
PCDC | 2 | 0 | 60 | 51.5 | 6 | 360
PCDC | 2 | 0 | 42 | 76.7 | 6 | 252
PCDC | 2 | 0 | 53 | 56.8 | 6 | 318
PCDC | 2 | 0 | 48 | 69.3 | 6 | 288
PCDC | 2 | 0 | 64 | 44 | 6 | 384
PCDC | 2 | 0 | 56 | 55.4 | 6 | 336
PCDC | 2 | 0 | 42 | 75.7 | 6 | 252
PCDC | 2 | 0 | 53 | 50.8 | 6 | 318
PCDC | 2 | 0 | 41 | 75.4 | 6 | 246
PCDC | 2 | 0 | 58 | 55.3 | 6 | 348
PCDC | 2 | 0 | 69 | 39.2 | 6 | 414
PCDC | 2 | 0 | 65 | 46.4 | 6 | 390
PCDC | 2 | 0 | 72 | 37 | 6 | 432
PCDC | 2 | 0 | 73 | 24.1 | 6 | 438
PCDC | 2 | 0 |  | 36.7 | 6
PCDC | 2 | 0 | 60 | 49.5 | 6 | 360
PCDC | 2 | 0 | 59 | 47.5 | 6 | 354
PCDC | 2 | 0 | 70 | 40.5 | 6 | 420
PCDC | 2 | 0 | 48 | 67.7 | 6 | 288
PCDC | 2 | 0 | 51 | 65.7 | 6 | 306
PCDC | 2 | 0 | 58 | 50.3 | 6 | 348
PCDC | 2 | 0 | 48 | 71.6 | 6 | 288
PCDC | 2 | 0 | 52 | 59.9 | 6 | 312
PCDC | 2 | 0 | 50 | 72.8 | 6 | 300
PCDC | 2 | 0 | 59 | 48.4 | 6 | 354
PCDC | 2 | 0 | 64 | 43 | 6 | 384
PCDC | 2 | 0 | 56 | 55.3 | 6 | 336
PCDC | 2 | 0 | 65 | 50 | 6 | 390
PCDC | 2 | 0 | 75 | 20.4 | 6 | 450
PCDC | 2 | 0 |  | 38.2 | 6
PCDC | 2 | 0 | 66 | 31 | 6 | 396
PCDC | 2 | 0 | 73 | 33.7 | 6 | 438
PCDC | 2 | 0 | 75 | 34.3 | 6 | 450
PCDC | 2 | 0 | 51 | 51.6 | 6 | 306
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 47 | 72.6 | 6 | 282
PCDC | 2 | 0 | 48 | 69.1 | 6 | 288
PCDC | 2 | 0 | 57 | 57.8 | 6 | 342
PCDC | 2 | 0 | 48 | 63.8 | 6 | 288
PCDC | 2 | 0 | 40 | 80.7 | 6 | 240
COMW | 2 | 1 | 45 | 22 | 1 | 45
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 28 | 22.8 | 1 | 28
COMW | 2 | 1 | 27 | 22.8 | 1 | 27
COMW | 2 | 1 | 29 | 22.8 | 1 | 29
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 39 | 22.1 | 1 | 39
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 33 | 22.8 | 1 | 33
COMW | 2 | 1 | 47 | 22.8 | 1 | 47
COMW | 2 | 1 | 47 | 21.6 | 1 | 47
COMW | 2 | 1 | 38 | 22.8 | 1 | 38
COMW | 2 | 1 | 36 | 22.8 | 1 | 36
COMW | 2 | 1 | 35 | 22.8 | 1 | 35
COMW | 2 | 1 | 32 | 22.8 | 1 | 32
COMKR | 2 | 1 | 29 | 21.9 | 1 | 29
COMKR | 2 | 1 | 33 | 19.9 | 1 | 33
COMKR | 2 | 1 | 47 | 21.6 | 1 | 47
COMKR | 2 | 1 | 33 | 20.8 | 1 | 33
COMKR | 2 | 1 | 35 | 21.2 | 1 | 35
COMKR | 2 | 1 | 36 | 20.8 | 1 | 36
COMKR | 2 | 1 | 38 | 21.7 | 1 | 38
COMKR | 2 | 1 | 38 | 20.1 | 1 | 38
COMKR | 2 | 1 | 28 | 21 | 1 | 28
COMKR | 2 | 1 | 45 | 16.8 | 1 | 45
COMKR | 2 | 1 | 27 | 20.3 | 1 | 27
COMKR | 2 | 1 | 38 | 20.4 | 1 | 38
COMKR | 2 | 1 | 35 | 22.3 | 1 | 35
COMKR | 2 | 1 | 32 | 22.3 | 1 | 32
COMKR | 2 | 1 | 33 | 20.4 | 1 | 33
COMKR | 2 | 1 | 39 | 21 | 1 | 39
COMKR | 2 | 1 | 35 | 21.3 | 1 | 35
COMKR | 2 | 1 | 47 | 17.9 | 1 | 47
COCWWTP | 3 | 0 | 30 | 111.33 | 6 | 180
COCWWTP | 3 | 0 | 25 | 115.4 | 6 | 150
COCWWTP | 3 | 0 | 24 | 112.24 | 6 | 144
COCWWTP | 3 | 0 | 13 | 126.58 | 6 | 78
COCWWTP | 3 | 0 | 23 | 117.89 | 6 | 138
COCWWTP | 3 | 0 | 23 | 121.38 | 6 | 138
COCWWTP | 3 | 0 | 22 | 124.61 | 6 | 132
COCWWTP | 3 | 0 | 22 | 120.53 | 6 | 132
COCWWTP | 3 | 0 | 27 | 114.24 | 6 | 162
COCWWTP | 3 | 0 | 35 | 101.63 | 6 | 210
COCWWTP | 3 | 0 | 30 | 103.82 | 6 | 180
COCWWTP | 3 | 0 | 33 | 110.19 | 6 | 198
COCWWTP | 3 | 0 | 35 | 104.85 | 6 | 210
COCWWTP | 3 | 0 | 36 | 108.81 | 6 | 216
COCWWTP | 3 | 0 | 27 | 114.66 | 6 | 162
COCWWTP | 3 | 0 | 29 | 121.22 | 6 | 174
COCWWTP | 3 | 0 | 22 | 122.18 | 6 | 132
COCWWTP | 3 | 0 | 32 | 107.27 | 6 | 192
COCWWTP | 3 | 0 | 38 | 97.29 | 6 | 228
COCWWTP | 3 | 0 | 36 | 111.2 | 6 | 216
COCWWTP | 3 | 0 | 32 | 104.25 | 6 | 192
COCWWTP | 3 | 0 | 38 | 101.91 | 6 | 228
COCWWTP | 3 | 0 | 35 | 104.64 | 6 | 210
COCWWTP | 3 | 0 | 33 | 108.23 | 6 | 198
COCWWTP | 3 | 0 | 29 | 112.79 | 6 | 174
COCWWTP | 3 | 0 | 32 | 103.43 | 6 | 192
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 22 | 113.54 | 6 | 132
COCWWTP | 3 | 0 | 15 | 118.41 | 6 | 90
COCWWTP | 3 | 0 | 35 | 104.75 | 6 | 210
COCWWTP | 3 | 0 | 33 | 99.61 | 6 | 198
COCWWTP | 3 | 0 | 27 | 111.06 | 6 | 162
COCWWTP | 3 | 0 | 39 | 108.75 | 6 | 234
COCWWTP | 3 | 0 | 28 | 119.15 | 6 | 168
COCWWTP | 3 | 0 | 35 | 101.97 | 6 | 210
COCWWTP | 3 | 0 | 45 | 103.31 | 6 | 270
COCWWTP | 3 | 0 | 38 | 105.3 | 6 | 228
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 35 | 121.97 | 6 | 210
COCWWTP | 3 | 0 | 31 | 108.73 | 6 | 186
COCWWTP | 3 | 0 | 34 | 107.82 | 6 | 204
COCWWTP | 3 | 0 | 31 | 112.35 | 6 | 186
COCWWTP | 3 | 0 | 35 | 107.22 | 6 | 210
COCWWTP | 3 | 0 | 29 | 114.12 | 6 | 174
COCWWTP | 3 | 0 | 28 | 109.18 | 6 | 168
COCWWTP | 3 | 0 | 31 | 112.2 | 6 | 186
COCWWTP | 3 | 0 | 32 | 124.2 | 6 | 192
COCWWTP | 3 | 0 | 31 | 115.31 | 6 | 186
COCWWTP | 3 | 0 | 30 | 107.83 | 6 | 180
COCWWTP | 3 | 0 | 35 | 101.9 | 6 | 210
COCWWTP | 3 | 0 | 30 | 118.7 | 6 | 180
COCWWTP | 3 | 0 | 18 | 122.01 | 6 | 108
COCWWTP | 3 | 0 | 32 | 122.28 | 6 | 192
COCWWTP | 3 | 0 | 36 | 99.23 | 6 | 216
COCWWTP | 3 | 0 | 28 | 117.11 | 6 | 168
COCWWTP | 3 | 0 | 27 | 115.82 | 6 | 162
COCWWTP | 3 | 0 | 14 | 127.5 | 6 | 84
COCWWTP | 3 | 0 | 17 | 117.79 | 6 | 102
COCWWTP | 3 | 0 | 30 | 115.86 | 6 | 180
COCWWTP | 3 | 0 | 21 | 121.73 | 6 | 126
COCWWTP | 3 | 0 | 20 | 121.41 | 6 | 120
COCWWTP | 3 | 0 | 21 | 128.59 | 6 | 126
COCWWTP | 3 | 0 | 17 | 128.33 | 6 | 102
COCWWTP | 3 | 0 | 16 | 128.92 | 6 | 96
COCWWTP | 3 | 0 | 20 | 115.5 | 6 | 120
COCWWTP | 3 | 0 | 44 | 93.32 | 6 | 264
COCWWTP | 3 | 0 | 28 | 114.78 | 6 | 168
COCWWTP | 3 | 0 | 23 | 117.13 | 6 | 138
COCCH | 1 | 1 | 44 | 10.89 | 0.5 | 22
COCCH | 1 | 1 | 45 | 11.04 | 0.5 | 22.5
COCCH | 1 | 1 | 38 | 10.92 | 0.5 | 19
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 48 | 11.04 | 0.5 | 24
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 52 | 11.04 | 0.5 | 26
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 39 | 11.04 | 0.5 | 19.5
COCCH | 1 | 1 | 35 | 10.9 | 0.5 | 17.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 46 | 11.04 | 0.5 | 23
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 30 | 10.91 | 0.5 | 15
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 24 | 11.04 | 0.5 | 12
COCCH | 1 | 1 | 25 | 10.92 | 0.5 | 12.5
COCCH | 1 | 1 | 35 | 10.92 | 0.5 | 17.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 25 | 11.04 | 0.5 | 12.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 36 | 10.84 | 0.5 | 18
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 29 | 11.04 | 0.5 | 14.5
COCCH | 1 | 1 | 26 | 11.04 | 0.5 | 13
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 29 | 10.92 | 0.5 | 14.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 37 | 11.04 | 0.5 | 18.5
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 29 | 11.04 | 0.5 | 14.5
COCCH | 1 | 1 | 35 | 10.91 | 0.5 | 17.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 33 | 11.04 | 0.5 | 16.5
COCCH | 1 | 1 | 38 | 11.04 | 0.5 | 19
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 25 | 11.04 | 0.5 | 12.5
COCCH | 1 | 1 | 22 | 11.04 | 0.5 | 11
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 31 | 11.04 | 0.5 | 15.5
COCCH | 1 | 1 | 33 | 10.91 | 0.5 | 16.5
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 34 | 11.04 | 0.5 | 17
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 10.91 | 0.5 | 17.5
COCCH | 1 | 1 | 28 | 11.04 | 0.5 | 14
COCCH | 1 | 1 | 27 | 11.04 | 0.5 | 13.5
COCCH | 1 | 1 | 30 | 11.04 | 0.5 | 15
COCCH | 1 | 1 | 32 | 11.04 | 0.5 | 16
COCCH | 1 | 1 | 22 | 11.04 | 0.5 | 11
COCCH | 1 | 1 | 36 | 11.04 | 0.5 | 18
COCCH | 1 | 1 | 35 | 11.04 | 0.5 | 17.5
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 38 | 19.93 | 1 | 38
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 31 | 21.11 | 1 | 31
Kid Kare | 1 | 1 | 32 | 21.36 | 1 | 32
Kid Kare | 1 | 1 | 29 | 21.36 | 1 | 29
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 34 | 21.36 | 1 | 34
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 14 | 21.36 | 1 | 14
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 16 | 21.36 | 1 | 16
Kid Kare | 1 | 1 | 24 | 21.36 | 1 | 24
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 19 | 21.36 | 1 | 19
Kid Kare | 1 | 1 | 32 | 21.12 | 1 | 32
Kid Kare | 1 | 1 | 19 | 21.36 | 1 | 19
Kid Kare | 1 | 1 | 18 | 21.36 | 1 | 18
Kid Kare | 1 | 1 | 14 | 21.36 | 1 | 14
Kid Kare | 1 | 1 | 30 | 20.91 | 1 | 30
Kid Kare | 1 | 1 | 35 | 21.36 | 1 | 35
Kid Kare | 1 | 1 | 33 | 21.36 | 1 | 33
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 25 | 21.36 | 1 | 25
Kid Kare | 1 | 1 | 20 | 21.36 | 1 | 20
Kid Kare | 1 | 1 | 34 | 20.61 | 1 | 34
Kid Kare | 1 | 1 | 21 | 21.36 | 1 | 21
Kid Kare | 1 | 1 | 26 | 21.36 | 1 | 26
Kid Kare | 1 | 1 | 32 | 21.36 | 1 | 32
Kid Kare | 1 | 1 | 40 | 20.86 | 1 | 40
Kid Kare | 1 | 1 | 16 | 21.36 | 1 | 16
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 35 | 21.11 | 1 | 35
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 32 | 20.86 | 1 | 32
Kid Kare | 1 | 1 | 31 | 21.36 | 1 | 31
Kid Kare | 1 | 1 | 37 | 20.9 | 1 | 37
Kid Kare | 1 | 1 | 36 | 20.33 | 1 | 36
Kid Kare | 1 | 1 | 31 | 21.36 | 1 | 31
Kid Kare | 1 | 1 | 27 | 21.36 | 1 | 27
Kid Kare | 1 | 1 | 34 | 21.11 | 1 | 34
Kid Kare | 1 | 1 | 39 | 20.21 | 1 | 39
Kid Kare | 1 | 1 | 30 | 21.36 | 1 | 30
Kid Kare | 1 | 1 | 23 | 21.36 | 1 | 23
Kid Kare | 1 | 1 | 38 | 20.1 | 1 | 38
Kid Kare | 1 | 1 | 39 | 20.34 | 1 | 39
Kid Kare | 1 | 1 | 32 | 20.43 | 1 | 32
Kid Kare | 1 | 1 | 29 | 20.63 | 1 | 29
BayView | 3 | 1 | 48 | 33.36 | 1.5 | 72
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 42 | 33.36 | 1.5 | 63
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 59 | 33.36 | 1.5 | 88.5
BayView | 3 | 1 | 63 | 33.36 | 1.5 | 94.5
BayView | 3 | 1 | 61 | 33.36 | 1.5 | 91.5
BayView | 3 | 1 | 50 | 33.36 | 1.5 | 75
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 46 | 33.36 | 1.5 | 69
BayView | 3 | 1 | 54 | 33.36 | 1.5 | 81
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 39 | 33.36 | 1.5 | 58.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 34 | 33.36 | 1.5 | 51
BayView | 3 | 1 | 38 | 33.36 | 1.5 | 57
BayView | 3 | 1 | 40 | 33.33 | 1.5 | 60
BayView | 3 | 1 | 52 | 33.36 | 1.5 | 78
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 60 | 33.36 | 1.5 | 90
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 38 | 33.31 | 1.5 | 57
BayView | 3 | 1 | 35 | 33.36 | 1.5 | 52.5
BayView | 3 | 1 | 34 | 33.36 | 1.5 | 51
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 33 | 33.36 | 1.5 | 49.5
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 45 | 33.36 | 1.5 | 67.5
BayView | 3 | 1 | 37 | 33.36 | 1.5 | 55.5
BayView | 3 | 1 | 44 | 33.36 | 1.5 | 66
BayView | 3 | 1 | 40 | 33.35 | 1.5 | 60
BayView | 3 | 1 | 47 | 33.36 | 1.5 | 70.5
BayView | 3 | 1 | 40 | 33.36 | 1.5 | 60
BayView | 3 | 1 | 36 | 33.36 | 1.5 | 54
BayView | 3 | 1 | 38 | 33.36 | 1.5 | 57
BayView | 3 | 1 | 35 | 33.36 | 1.5 | 52.5
BayView | 3 | 1 | 35 | 32.99 | 1.5 | 52.5
BayView | 3 | 1 | 34 | 32.26 | 1.5 | 51
BayView | 3 | 1 | 38 | 32.39 | 1.5 | 57
BayView | 3 | 1 | 43 | 33.1 | 1.5 | 64.5
BayView | 3 | 1 | 49 | 33.35 | 1.5 | 73.5
BayView | 3 | 1 | 49 | 33.36 | 1.5 | 73.5
BayView | 3 | 1 | 41 | 33.36 | 1.5 | 61.5
BayView | 3 | 1 | 42 | 33.36 | 1.5 | 63
BLDG210 | 2 | 0 | 34 | 47.95 | 2.5 | 85
BLDG210 | 2 | 0 | 46 | 38.73 | 2.5 | 115
BLDG210 | 2 | 0 | 33 | 44.7 | 2.5 | 82.5
BLDG210 | 2 | 0 | 34 | 51.14 | 2.5 | 85
BLDG210 | 2 | 0 | 35 | 48.59 | 2.5 | 87.5
BLDG210 | 2 | 0 | 44 | 43.79 | 2.5 | 110
BLDG210 | 2 | 0 | 46 | 42.09 | 2.5 | 115
BLDG210 | 2 | 0 | 34 | 46.4 | 2.5 | 85
BLDG210 | 2 | 0 | 41 | 47.68 | 2.5 | 102.5
BLDG210 | 2 | 0 | 36 | 43.68 | 2.5 | 90
BLDG210 | 2 | 0 | 35 | 49.39 | 2.5 | 87.5
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 34 | 47.36 | 2.5 | 85
BLDG210 | 2 | 0 | 32 | 49.76 | 2.5 | 80
BLDG210 | 2 | 0 | 33 | 48.43 | 2.5 | 82.5
BLDG210 | 2 | 0 | 30 | 49.71 | 2.5 | 75
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 32 | 48.43 | 2.5 | 80
BLDG210 | 2 | 0 | 29 | 50.61 | 2.5 | 72.5
BLDG210 | 2 | 0 | 35 | 48.43 | 2.5 | 87.5
BLDG210 | 2 | 0 | 42 | 45.76 | 2.5 | 105
BNS GEN | 3 | 1 | 48 | 44.4 | 4.95 | 237.59
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 34 | 44.4 | 4.95 | 168.29
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 49 | 44.4 | 4.95 | 242.54
BNS GEN | 3 | 1 | 52 | 44.4 | 4.95 | 257.39
BNS GEN | 3 | 1 | 59 | 44.4 | 4.95 | 292.04
BNS GEN | 3 | 1 | 63 | 44.4 | 4.95 | 311.84
BNS GEN | 3 | 1 | 61 | 44.4 | 4.95 | 301.94
BNS GEN | 3 | 1 | 50 | 44.4 | 4.95 | 247.49
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 46 | 44.4 | 4.95 | 227.69
BNS GEN | 3 | 1 | 34 | 43.47 | 4.95 | 168.29
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 39 | 44.4 | 4.95 | 193.04
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 38 | 43.48 | 4.95 | 188.09
BNS GEN | 3 | 1 | 52 | 43.47 | 4.95 | 257.39
BNS GEN | 3 | 1 | 44 | 43.48 | 4.95 | 217.79
BNS GEN | 3 | 1 | 60 | 43.48 | 4.95 | 297
BNS GEN | 3 | 1 | 41 | 43.48 | 4.95 | 202.94
BNS GEN | 3 | 1 | 45 | 44.4 | 4.95 | 222.74
BNS GEN | 3 | 1 | 44 | 44.4 | 4.95 | 217.79
BNS GEN | 3 | 1 | 40 | 43.48 | 4.95 | 198
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 42 | 44.4 | 4.95 | 207.89
BNS GEN | 3 | 1 | 42 | 44.4 | 4.95 | 207.89
BNS GEN | 3 | 1 | 52 | 44.4 | 4.95 | 257.39
BNS GEN | 3 | 1 | 47 | 44.4 | 4.95 | 232.64
BNS GEN | 3 | 1 | 54 | 44.4 | 4.95 | 267.29
BNS GEN | 3 | 1 | 49 | 44.4 | 4.95 | 242.54
BNS GEN | 3 | 1 | 43 | 44.4 | 4.95 | 212.84
BNS GEN | 3 | 1 | 38 | 44.4 | 4.95 | 188.09
BNS GEN | 3 | 1 | 34 | 44.4 | 4.95 | 168.29
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 37 | 44.4 | 4.95 | 183.14
BNS GEN | 3 | 1 | 33 | 44.4 | 4.95 | 163.34
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 44 | 44.4 | 4.95 | 217.79
BNS GEN | 3 | 1 | 35 | 44.4 | 4.95 | 173.25
BNS GEN | 3 | 1 | 45 | 44.4 | 4.95 | 222.74
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 40 | 44.4 | 4.95 | 198
BNS GEN | 3 | 1 | 41 | 44.4 | 4.95 | 202.94
BNS GEN | 3 | 1 | 40 | 44.4 | 4.95 | 198
BNS GEN | 3 | 1 | 36 | 44.4 | 4.95 | 178.19
BNS GEN | 3 | 1 | 38 | 44.4 | 4.95 | 188.09
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 40 | 228.96 | 10 | 400
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 43 | 226.69 | 10 | 430
NQ | 4 | 1 | 38 | 228.49 | 10 | 380
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 46 | 228.96 | 10 | 460
NQ | 4 | 1 | 52 | 228.96 | 10 | 520
NQ | 4 | 1 | 43 | 226.8 | 10 | 430
NQ | 4 | 1 | 39 | 228.96 | 10 | 390
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 33 | 228.96 | 10 | 330
NQ | 4 | 1 | 42 | 228.96 | 10 | 420
NQ | 4 | 1 | 37 | 228.96 | 10 | 370
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 40 | 224.97 | 10 | 400
NQ | 4 | 1 | 41 | 228.96 | 10 | 410
NQ | 4 | 1 | 40 | 228.96 | 10 | 400
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 43 | 228.96 | 10 | 430
NQ | 4 | 1 | 32 | 228.65 | 10 | 320
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 30 | 228.96 | 10 | 300
NQ | 4 | 1 | 30 | 228.96 | 10 | 300
NQ | 4 | 1 | 24 | 228.96 | 10 | 240
NQ | 4 | 1 | 10 | 228.96 | 10 | 100
NQ | 4 | 1 | 8 | 228.96 | 10 | 80
NQ | 4 | 1 | 9 | 228.96 | 10 | 90
NQ | 4 | 1 | 35 | 227.87 | 10 | 350
NQ | 4 | 1 | 35 | 228.96 | 10 | 350
NQ | 4 | 1 | 38 | 228.96 | 10 | 380
NQ | 4 | 1 | 35 | 228.82 | 10 | 350
NQ | 4 | 1 | 34 | 228.96 | 10 | 340
NQ | 4 | 1 | 35 | 228.69 | 10 | 350
NQ | 4 | 1 | 34 | 226.37 | 10 | 340
NQ | 4 | 1 | 33 | 227.72 | 10 | 330
NQ | 4 | 1 | 32 | 228.96 | 10 | 320
NQ | 4 | 1 | 39 | 228.23 | 10 | 390
NQ | 4 | 1 | 36 | 215.89 | 10 | 360
NQ | 4 | 1 | 36 | 228.96 | 10 | 360
NQ | 4 | 1 | 43 | 228.96 | 10 | 430
NQ | 4 | 1 | 41 | 228.96 | 10 | 410
NQ | 4 | 1 | 24 | 228.96 | 10 | 240

## BL Size1 Var
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
HCNW | 1 | 0 | 47 | 51.5 | 6 | 282 | SUMMARY OUTPUT
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 48 | 50.7 | 6 | 288 | Regression Statistics
HCNW | 1 | 0 | 33 | 67.1 | 6 | 198 | Multiple R | 0.98258
HCNW | 1 | 0 | 34 | 66.5 | 6 | 204 | R Square | 0.96547
HCNW | 1 | 0 | 38 | 62.2 | 6 | 228 | Adjusted R Square | 0.96487
HCNW | 1 | 0 | 45 | 52.3 | 6 | 270 | Standard Error | 2.3296
HCNW | 1 | 0 | 55 | 38.9 | 6 | 330 | Observations | 60
HCNW | 1 | 0 | 44 | 55.2 | 6 | 264
HCNW | 1 | 0 | 43 | 56.7 | 6 | 258 | ANOVA
HCNW | 1 | 0 | 38 | 59.9 | 6 | 228 |  | df | SS | MS | F | Significance F
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186 | Regression | 1 | 8800.089 | 8800.089 | 1621.4618 | 4.3172e-44
HCNW | 1 | 0 | 55 | 45.6 | 6 | 330 | Residual | 58 | 314.7809 | 5.4273
HCNW | 1 | 0 | 43 | 52.9 | 6 | 258 | Total | 59 | 9114.8698
HCNW | 1 | 0 | 45 | 54.5 | 6 | 270
HCNW | 1 | 0 | 31 | 69.6 | 6 | 186 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
HCNW | 1 | 0 | 25 | 82.5 | 6 | 150 | Intercept | 105.9085 | 1.3717 | 77.2104 | 3.5698e-60 | 103.1628 | 108.6542 | 103.1628 | 108.6542
HCNW | 1 | 0 | 22 | 80 | 6 | 132 | X Variable 1 | -1.1784 | 0.029263 | -40.2674 | 4.3172e-44 | -1.2369 | -1.1198 | -1.2369 | -1.1198
HCNW | 1 | 0 | 26 | 76.4 | 6 | 156
HCNW | 1 | 0 | 44 | 55.6 | 6 | 264
HCNW | 1 | 0 | 56 | 44.3 | 6 | 336
HCNW | 1 | 0 | 36 | 60.7 | 6 | 216
HCNW | 1 | 0 | 38 | 55.7 | 6 | 228
HCNW | 1 | 0 | 44 | 55.9 | 6 | 264
HCNW | 1 | 0 | 47 | 50.2 | 6 | 282
HCNW | 1 | 0 | 44 | 52.6 | 6 | 264
HCNW | 1 | 0 | 46 | 51.8 | 6 | 276
HCNW | 1 | 0 | 46 | 51.9 | 6 | 276
HCNW | 1 | 0 | 31 | 70.4 | 6 | 186
HCNW | 1 | 0 | 57 | 43.4 | 6 | 342
HCNW | 1 | 0 | 31 | 67.8 | 6 | 186
HCNW | 1 | 0 | 48 | 53.2 | 6 | 288
HCNW | 1 | 0 | 43 | 56.1 | 6 | 258
HCNW | 1 | 0 | 39 | 58.4 | 6 | 234
HCNW | 1 | 0 | 44 | 54.5 | 6 | 264
HCNW | 1 | 0 | 44 | 56.4 | 6 | 264
HCNW | 1 | 0 | 34 | 63.6 | 6 | 204
HCNW | 1 | 0 | 36 | 60.6 | 6 | 216
HCNW | 1 | 0 | 55 | 45.5 | 6 | 330
HCNW | 1 | 0 | 59 | 34.5 | 6 | 354
HCNW | 1 | 0 | 59 | 35.1 | 6 | 354
HCNW | 1 | 0 | 57 | 37.8 | 6 | 342
HCNW | 1 | 0 | 29 | 70.9 | 6 | 174
HCNW | 1 | 0 | 56 | 38.6 | 6 | 336
HCNW | 1 | 0 | 58 | 35.9 | 6 | 348
HCNW | 1 | 0 | 52 | 42.1 | 6 | 312
HCNW | 1 | 0 | 60 | 34 | 6 | 360
HCNW | 1 | 0 | 58 | 37.3 | 6 | 348
HCNW | 1 | 0 | 54 | 38.6 | 6 | 324
HCNW | 1 | 0 | 59 | 41.6 | 6 | 354
HCNW | 1 | 0 | 55 | 40.9 | 6 | 330
HCNW | 1 | 0 | 56 | 40.7 | 6 | 336
HCNW | 1 | 0 | 53 | 42.3 | 6 | 318
HCNW | 1 | 0 | 54 | 40.7 | 6 | 324
HCNW | 1 | 0 | 58 | 36.9 | 6 | 348
HCNW | 1 | 0 | 58 | 36.6 | 6 | 348
HCNW | 1 | 0 | 56 | 39.3 | 6 | 336
HCNW | 1 | 0 | 55 | 39.7 | 6 | 330
HCNW | 1 | 0 | 40 | 58.8 | 6 | 240
HCNW | 1 | 0 | 56 | 36.7 | 6 | 336

## BL Size2 Var
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
PCDC | 2 | 0 | 71 | 32 | 6 | 426 | SUMMARY OUTPUT
PCDC | 2 | 0 | 52 | 52.3 | 6 | 312
PCDC | 2 | 0 | 56 | 56.5 | 6 | 336 | Regression Statistics
PCDC | 2 | 0 | 72 | 35.5 | 6 | 432 | Multiple R | 0.67329
PCDC | 2 | 0 | 79 | 17 | 6 | 474 | R Square | 0.45332
PCDC | 2 | 0 | 66 | 43.5 | 6 | 396 | Adjusted R Square | 0.44988
PCDC | 2 | 0 | 77 | 26.9 | 6 | 462 | Standard Error | 9.8789
PCDC | 2 | 0 | 52 | 60.2 | 6 | 312 | Observations | 161
PCDC | 2 | 0 | 68 | 35.2 | 6 | 408
PCDC | 2 | 0 | 64 | 46.2 | 6 | 384 | ANOVA
PCDC | 2 | 0 | 74 | 24.8 | 6 | 444 |  | df | SS | MS | F | Significance F
PCDC | 2 | 0 | 54 | 58.7 | 6 | 324 | Regression | 1 | 12867.0371 | 12867.0371 | 131.8445 | 1.3158e-22
PCDC | 2 | 0 | 64 | 39.3 | 6 | 384 | Residual | 159 | 15517.205 | 97.5925
PCDC | 2 | 0 | 49 | 50.9 | 6 | 294 | Total | 160 | 28384.2421
PCDC | 2 | 0 | 46 | 60.6 | 6 | 276
PCDC | 2 | 0 | 64 | 48.8 | 6 | 384 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
PCDC | 2 | 0 | 63 | 47.7 | 6 | 378 | Intercept | 88.9213 | 3.6124 | 24.6155 | 4.1111e-56 | 81.7868 | 96.0557 | 81.7868 | 96.0557
PCDC | 2 | 0 | 57 | 46.8 | 6 | 342 | X Variable 1 | -0.7006 | 0.061015 | -11.4824 | 1.3158e-22 | -0.8211 | -0.58009 | -0.8211 | -0.58009
PCDC | 2 | 0 | 60 | 46.7 | 6 | 360
PCDC | 2 | 0 | 58 | 52.3 | 6 | 348
PCDC | 2 | 0 | 56 | 57.1 | 6 | 336
PCDC | 2 | 0 | 53 | 58.3 | 6 | 318
PCDC | 2 | 0 | 50 | 64.8 | 6 | 300
PCDC | 2 | 0 | 53 | 61.9 | 6 | 318
PCDC | 2 | 0 | 66 | 46.5 | 6 | 396
PCDC | 2 | 0 | 67 | 31.4 | 6 | 402
PCDC | 2 | 0 | 44 | 74.7 | 6 | 264
PCDC | 2 | 0 | 61 | 46 | 6 | 366
PCDC | 2 | 0 | 49 | 73.1 | 6 | 294
PCDC | 2 | 0 | 57 | 55.5 | 6 | 342
PCDC | 2 | 0 | 58 | 41.8 | 6 | 348
PCDC | 2 | 0 | 72 | 38.1 | 6 | 432
PCDC | 2 | 0 | 74 | 25.2 | 6 | 444
PCDC | 2 | 0 | 74 | 30.8 | 6 | 444
PCDC | 2 | 0 | 57 | 57.2 | 6 | 342
PCDC | 2 | 0 | 54 | 55.3 | 6 | 324
PCDC | 2 | 0 | 67 | 42.6 | 6 | 402
PCDC | 2 | 0 | 71 | 38.6 | 6 | 426
PCDC | 2 | 0 | 71 | 38.9 | 6 | 426
PCDC | 2 | 0 | 59 | 51.8 | 6 | 354
PCDC | 2 | 0 | 59 | 46.9 | 6 | 354
PCDC | 2 | 0 | 46 | 71.8 | 6 | 276
PCDC | 2 | 0 | 61 | 50.6 | 6 | 366
PCDC | 2 | 0 | 52 | 60.7 | 6 | 312
PCDC | 2 | 0 | 76 | 31.4 | 6 | 456
PCDC | 2 | 0 | 45 | 72.6 | 6 | 270
PCDC | 2 | 0 | 52 | 67.6 | 6 | 312
PCDC | 2 | 0 | 55 | 57.4 | 6 | 330
PCDC | 2 | 0 | 50 | 62.5 | 6 | 300
PCDC | 2 | 0 | 65 | 51.8 | 6 | 390
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 45 | 68.5 | 6 | 270
PCDC | 2 | 0 | 74 | 39.1 | 6 | 444
PCDC | 2 | 0 | 75 | 31.4 | 6 | 450
PCDC | 2 | 0 | 66 | 41.8 | 6 | 396
PCDC | 2 | 0 | 56 | 52.5 | 6 | 336
PCDC | 2 | 0 | 75 | 33.2 | 6 | 450
PCDC | 2 | 0 | 74 | 33.6 | 6 | 444
PCDC | 2 | 0 | 75 | 32.2 | 6 | 450
PCDC | 2 | 0 | 64 | 44.1 | 6 | 384
PCDC | 2 | 0 | 72 | 31.9 | 6 | 432
PCDC | 2 | 0 | 73 | 31.2 | 6 | 438
PCDC | 2 | 0 | 69 | 37.3 | 6 | 414
PCDC | 2 | 0 | 71 | 31.9 | 6 | 426
PCDC | 2 | 0 | 72 | 33.4 | 6 | 432
PCDC | 2 | 0 | 68 | 39.7 | 6 | 408
PCDC | 2 | 0 | 66 | 37.2 | 6 | 396
PCDC | 2 | 0 | 70 | 32.2 | 6 | 420
PCDC | 2 | 0 | 60 | 51.9 | 6 | 360
PCDC | 2 | 0 | 71 | 35.8 | 6 | 426
PCDC | 2 | 0 | 58 | 61.8 | 6 | 348
PCDC | 2 | 0 | 43 | 75.2 | 6 | 258
PCDC | 2 | 0 | 47 | 66.6 | 6 | 282
PCDC | 2 | 0 | 58 | 54 | 6 | 348
PCDC | 2 | 0 | 60 | 50.1 | 6 | 360
PCDC | 2 | 0 | 62 | 46.4 | 6 | 372
PCDC | 2 | 0 | 53 | 63 | 6 | 318
PCDC | 2 | 0 | 71 | 35.4 | 6 | 426
PCDC | 2 | 0 | 51 | 66.2 | 6 | 306
PCDC | 2 | 0 | 76 | 34.3 | 6 | 456
PCDC | 2 | 0 | 73 | 29.1 | 6 | 438
PCDC | 2 | 0 | 77 | 24.2 | 6 | 462
PCDC | 2 | 0 | 65 | 44.9 | 6 | 390
PCDC | 2 | 0 | 63 | 45.4 | 6 | 378
PCDC | 2 | 0 | 72 | 43.7 | 6 | 432
PCDC | 2 | 0 | 64 | 46 | 6 | 384
PCDC | 2 | 0 | 83 | 23.2 | 6 | 498
PCDC | 2 | 0 | 57 | 54.5 | 6 | 342
PCDC | 2 | 0 | 66 | 45.4 | 6 | 396
PCDC | 2 | 0 | 57 | 53.6 | 6 | 342
PCDC | 2 | 0 | 67 | 39.7 | 6 | 402
PCDC | 2 | 0 | 72 | 33.7 | 6 | 432
PCDC | 2 | 0 | 46 | 70.1 | 6 | 276
PCDC | 2 | 0 | 73 | 30.7 | 6 | 438
PCDC | 2 | 0 | 49 | 65.3 | 6 | 294
PCDC | 2 | 0 | 68 | 41.5 | 6 | 408
PCDC | 2 | 0 | 64 | 41.7 | 6 | 384
PCDC | 2 | 0 | 69 | 37.7 | 6 | 414
PCDC | 2 | 0 | 68 | 47.5 | 6 | 408
PCDC | 2 | 0 | 51 | 63.6 | 6 | 306
PCDC | 2 | 0 | 55 | 56.8 | 6 | 330
PCDC | 2 | 0 | 73 | 34.2 | 6 | 438
PCDC | 2 | 0 | 60 | 51.5 | 6 | 360
PCDC | 2 | 0 | 42 | 76.7 | 6 | 252
PCDC | 2 | 0 | 53 | 56.8 | 6 | 318
PCDC | 2 | 0 | 48 | 69.3 | 6 | 288
PCDC | 2 | 0 | 64 | 44 | 6 | 384
PCDC | 2 | 0 | 56 | 55.4 | 6 | 336
PCDC | 2 | 0 | 42 | 75.7 | 6 | 252
PCDC | 2 | 0 | 53 | 50.8 | 6 | 318
PCDC | 2 | 0 | 41 | 75.4 | 6 | 246
PCDC | 2 | 0 | 58 | 55.3 | 6 | 348
PCDC | 2 | 0 | 69 | 39.2 | 6 | 414
PCDC | 2 | 0 | 65 | 46.4 | 6 | 390
PCDC | 2 | 0 | 72 | 37 | 6 | 432
PCDC | 2 | 0 | 73 | 24.1 | 6 | 438
PCDC | 2 | 0 | 60 | 49.5 | 6 | 360
PCDC | 2 | 0 | 59 | 47.5 | 6 | 354
PCDC | 2 | 0 | 70 | 40.5 | 6 | 420
PCDC | 2 | 0 | 48 | 67.7 | 6 | 288
PCDC | 2 | 0 | 51 | 65.7 | 6 | 306
PCDC | 2 | 0 | 58 | 50.3 | 6 | 348
PCDC | 2 | 0 | 48 | 71.6 | 6 | 288
PCDC | 2 | 0 | 52 | 59.9 | 6 | 312
PCDC | 2 | 0 | 50 | 72.8 | 6 | 300
PCDC | 2 | 0 | 59 | 48.4 | 6 | 354
PCDC | 2 | 0 | 64 | 43 | 6 | 384
PCDC | 2 | 0 | 56 | 55.3 | 6 | 336
PCDC | 2 | 0 | 65 | 50 | 6 | 390
PCDC | 2 | 0 | 75 | 20.4 | 6 | 450
PCDC | 2 | 0 | 66 | 31 | 6 | 396
PCDC | 2 | 0 | 73 | 33.7 | 6 | 438
PCDC | 2 | 0 | 75 | 34.3 | 6 | 450
PCDC | 2 | 0 | 51 | 51.6 | 6 | 306
PCDC | 2 | 0 | 58 | 51.1 | 6 | 348
PCDC | 2 | 0 | 47 | 72.6 | 6 | 282
PCDC | 2 | 0 | 48 | 69.1 | 6 | 288
PCDC | 2 | 0 | 57 | 57.8 | 6 | 342
PCDC | 2 | 0 | 48 | 63.8 | 6 | 288
PCDC | 2 | 0 | 40 | 80.7 | 6 | 240
BLDG210 | 2 | 0 | 34 | 47.95 | 2.5 | 85
BLDG210 | 2 | 0 | 46 | 38.73 | 2.5 | 115
BLDG210 | 2 | 0 | 33 | 44.7 | 2.5 | 82.5
BLDG210 | 2 | 0 | 34 | 51.14 | 2.5 | 85
BLDG210 | 2 | 0 | 35 | 48.59 | 2.5 | 87.5
BLDG210 | 2 | 0 | 44 | 43.79 | 2.5 | 110
BLDG210 | 2 | 0 | 46 | 42.09 | 2.5 | 115
BLDG210 | 2 | 0 | 34 | 46.4 | 2.5 | 85
BLDG210 | 2 | 0 | 41 | 47.68 | 2.5 | 102.5
BLDG210 | 2 | 0 | 36 | 43.68 | 2.5 | 90
BLDG210 | 2 | 0 | 35 | 49.39 | 2.5 | 87.5
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 34 | 47.36 | 2.5 | 85
BLDG210 | 2 | 0 | 32 | 49.76 | 2.5 | 80
BLDG210 | 2 | 0 | 33 | 48.43 | 2.5 | 82.5
BLDG210 | 2 | 0 | 30 | 49.71 | 2.5 | 75
BLDG210 | 2 | 0 | 32 | 48.16 | 2.5 | 80
BLDG210 | 2 | 0 | 32 | 48.43 | 2.5 | 80
BLDG210 | 2 | 0 | 29 | 50.61 | 2.5 | 72.5
BLDG210 | 2 | 0 | 35 | 48.43 | 2.5 | 87.5
BLDG210 | 2 | 0 | 42 | 45.76 | 2.5 | 105

## BL Size3 Var
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | Baseline Heater Size kW | Heater Size X Temp
COCWWTP | 3 | 0 | 30 | 111.33 | 6 | 180 | SUMMARY OUTPUT
COCWWTP | 3 | 0 | 25 | 115.4 | 6 | 150
COCWWTP | 3 | 0 | 24 | 112.24 | 6 | 144 | Regression Statistics
COCWWTP | 3 | 0 | 13 | 126.58 | 6 | 78 | Multiple R | 0.79204
COCWWTP | 3 | 0 | 23 | 117.89 | 6 | 138 | R Square | 0.62732
COCWWTP | 3 | 0 | 23 | 121.38 | 6 | 138 | Adjusted R Square | 0.62167
COCWWTP | 3 | 0 | 22 | 124.61 | 6 | 132 | Standard Error | 5.1396
COCWWTP | 3 | 0 | 22 | 120.53 | 6 | 132 | Observations | 68
COCWWTP | 3 | 0 | 27 | 114.24 | 6 | 162
COCWWTP | 3 | 0 | 35 | 101.63 | 6 | 210 | ANOVA
COCWWTP | 3 | 0 | 30 | 103.82 | 6 | 180 |  | df | SS | MS | F | Significance F
COCWWTP | 3 | 0 | 33 | 110.19 | 6 | 198 | Regression | 1 | 2934.7004 | 2934.7004 | 111.0962 | 8.752e-16
COCWWTP | 3 | 0 | 35 | 104.85 | 6 | 210 | Residual | 66 | 1743.4463 | 26.4159
COCWWTP | 3 | 0 | 36 | 108.81 | 6 | 216 | Total | 67 | 4678.1466
COCWWTP | 3 | 0 | 27 | 114.66 | 6 | 162
COCWWTP | 3 | 0 | 29 | 121.22 | 6 | 174 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCWWTP | 3 | 0 | 22 | 122.18 | 6 | 132 | Intercept | 139.8546 | 2.6384 | 53.0073 | 7.9701e-56 | 134.5869 | 145.1223 | 134.5869 | 145.1223
COCWWTP | 3 | 0 | 32 | 107.27 | 6 | 192 | X Variable 1 | -0.9318 | 0.088404 | -10.5402 | 8.752e-16 | -1.1083 | -0.7553 | -1.1083 | -0.7553
COCWWTP | 3 | 0 | 38 | 97.29 | 6 | 228
COCWWTP | 3 | 0 | 36 | 111.2 | 6 | 216
COCWWTP | 3 | 0 | 32 | 104.25 | 6 | 192
COCWWTP | 3 | 0 | 38 | 101.91 | 6 | 228
COCWWTP | 3 | 0 | 35 | 104.64 | 6 | 210
COCWWTP | 3 | 0 | 33 | 108.23 | 6 | 198
COCWWTP | 3 | 0 | 29 | 112.79 | 6 | 174
COCWWTP | 3 | 0 | 32 | 103.43 | 6 | 192
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 22 | 113.54 | 6 | 132
COCWWTP | 3 | 0 | 15 | 118.41 | 6 | 90
COCWWTP | 3 | 0 | 35 | 104.75 | 6 | 210
COCWWTP | 3 | 0 | 33 | 99.61 | 6 | 198
COCWWTP | 3 | 0 | 27 | 111.06 | 6 | 162
COCWWTP | 3 | 0 | 39 | 108.75 | 6 | 234
COCWWTP | 3 | 0 | 28 | 119.15 | 6 | 168
COCWWTP | 3 | 0 | 35 | 101.97 | 6 | 210
COCWWTP | 3 | 0 | 45 | 103.31 | 6 | 270
COCWWTP | 3 | 0 | 38 | 105.3 | 6 | 228
COCWWTP | 3 | 0 | 35 | 107.67 | 6 | 210
COCWWTP | 3 | 0 | 35 | 121.97 | 6 | 210
COCWWTP | 3 | 0 | 31 | 108.73 | 6 | 186
COCWWTP | 3 | 0 | 34 | 107.82 | 6 | 204
COCWWTP | 3 | 0 | 31 | 112.35 | 6 | 186
COCWWTP | 3 | 0 | 35 | 107.22 | 6 | 210
COCWWTP | 3 | 0 | 29 | 114.12 | 6 | 174
COCWWTP | 3 | 0 | 28 | 109.18 | 6 | 168
COCWWTP | 3 | 0 | 31 | 112.2 | 6 | 186
COCWWTP | 3 | 0 | 32 | 124.2 | 6 | 192
COCWWTP | 3 | 0 | 31 | 115.31 | 6 | 186
COCWWTP | 3 | 0 | 30 | 107.83 | 6 | 180
COCWWTP | 3 | 0 | 35 | 101.9 | 6 | 210
COCWWTP | 3 | 0 | 30 | 118.7 | 6 | 180
COCWWTP | 3 | 0 | 18 | 122.01 | 6 | 108
COCWWTP | 3 | 0 | 32 | 122.28 | 6 | 192
COCWWTP | 3 | 0 | 36 | 99.23 | 6 | 216
COCWWTP | 3 | 0 | 28 | 117.11 | 6 | 168
COCWWTP | 3 | 0 | 27 | 115.82 | 6 | 162
COCWWTP | 3 | 0 | 14 | 127.5 | 6 | 84
COCWWTP | 3 | 0 | 17 | 117.79 | 6 | 102
COCWWTP | 3 | 0 | 30 | 115.86 | 6 | 180
COCWWTP | 3 | 0 | 21 | 121.73 | 6 | 126
COCWWTP | 3 | 0 | 20 | 121.41 | 6 | 120
COCWWTP | 3 | 0 | 21 | 128.59 | 6 | 126
COCWWTP | 3 | 0 | 17 | 128.33 | 6 | 102
COCWWTP | 3 | 0 | 16 | 128.92 | 6 | 96
COCWWTP | 3 | 0 | 20 | 115.5 | 6 | 120
COCWWTP | 3 | 0 | 44 | 93.32 | 6 | 264
COCWWTP | 3 | 0 | 28 | 114.78 | 6 | 168
COCWWTP | 3 | 0 | 23 | 117.13 | 6 | 138

## BL Flat
Site | Size Category | Baseline Heater Size kW | Mode
COCCH | 1 | 0.5 | 11.04 | SUMMARY OUTPUT
Kid Kare | 1 | 1 | 21.36
TCWWTP | 1 | 1 | 10.93 | Regression Statistics
COCFD | 2 | 1 | 21.12 | Multiple R | 0.96612
COCTV | 2 | 1 | 21.12 | R Square | 0.9334
COMKR | 2 | 1 | 20.65 | Adjusted R Square | 0.84249
COMW | 2 | 1 | 22.8 | Standard Error | 18.907
KE ECAM | 2 | 1 | 22.32 | Observations | 12
TCWP | 2 | 1 | 22.31
BayView | 3 | 1.5 | 33.36 | ANOVA
BNS GEN | 3 | 4.95 | 44.4 |  | df | SS | MS | F | Significance F
NQ | 4 | 10 | 228.96 | Regression | 1 | 55106.6017 | 55106.6017 | 154.1555 | 2.1191e-07
|  |  |  | Residual | 11 | 3932.2154 | 357.4741
|  |  |  | Total | 12 | 59038.8171
[5 empty] | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
|  |  |  | Intercept | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | X Variable 1 | 20.2037 | 1.6272 | 12.4159 | 8.1893e-08 | 16.6222 | 23.7852 | 16.6222 | 23.7852

## Treatment Data w Heater Size
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 66 | 10.42 | 1 | 66
COCFD | 2 | 1 | 48 | 18.38 | 1 | 48
COCFD | 2 | 1 | 70 | 8.26 | 1 | 70
COCFD | 2 | 1 | 76 | 6.77 | 1 | 76
COCFD | 2 | 1 | 61 | 12.87 | 1 | 61
COCFD | 2 | 1 | 67 | 11.41 | 1 | 67
COCFD | 2 | 1 | 73 | 8.99 | 1 | 73
COCFD | 2 | 1 | 69 | 10.32 | 1 | 69
COCFD | 2 | 1 | 76 | 8.3 | 1 | 76
COCFD | 2 | 1 | 81 | 6.57 | 1 | 81
COCFD | 2 | 1 | 78 | 6.79 | 1 | 78
COCFD | 2 | 1 | 70 | 8.7 | 1 | 70
COCFD | 2 | 1 | 63 | 13.54 | 1 | 63
COCFD | 2 | 1 | 73 | 8.71 | 1 | 73
COCFD | 2 | 1 | 64 | 15.11 | 1 | 64
COCFD | 2 | 1 | 80 | 4.11 | 1 | 80
COCFD | 2 | 1 | 57 | 13.6 | 1 | 57
COCFD | 2 | 1 | 58 | 12.83 | 1 | 58
COCFD | 2 | 1 | 57 | 12.04 | 1 | 57
COCFD | 2 | 1 | 62 | 12.06 | 1 | 62
COCFD | 2 | 1 | 54 | 14.79 | 1 | 54
COCFD | 2 | 1 | 81 | 7.18 | 1 | 81
COCFD | 2 | 1 | 78 | 7.91 | 1 | 78
COCFD | 2 | 1 | 68 | 11.03 | 1 | 68
COCFD | 2 | 1 | 74 | 5.53 | 1 | 74
COCFD | 2 | 1 | 54 | 16.96 | 1 | 54
COCFD | 2 | 1 | 65 | 12.97 | 1 | 65
COCFD | 2 | 1 | 54 | 15.47 | 1 | 54
COCFD | 2 | 1 | 51 | 16.28 | 1 | 51
COCFD | 2 | 1 | 52 | 13.98 | 1 | 52
COCFD | 2 | 1 | 60 | 11.82 | 1 | 60
COCFD | 2 | 1 | 60 | 11.86 | 1 | 60
COCFD | 2 | 1 | 63 | 11.75 | 1 | 63
COCFD | 2 | 1 | 65 | 10.49 | 1 | 65
COCFD | 2 | 1 | 67 | 8.82 | 1 | 67
COCFD | 2 | 1 | 58 | 14.66 | 1 | 58
COCFD | 2 | 1 | 56 | 14.25 | 1 | 56
COCFD | 2 | 1 | 76 | 7.76 | 1 | 76
COCFD | 2 | 1 | 54 | 15.72 | 1 | 54
COCFD | 2 | 1 | 51 | 15.47 | 1 | 51
COCFD | 2 | 1 | 49 | 17.77 | 1 | 49
COCFD | 2 | 1 | 49 | 18.79 | 1 | 49
COCFD | 2 | 1 | 54 | 15.29 | 1 | 54
COCFD | 2 | 1 | 56 | 16.1 | 1 | 56
COCFD | 2 | 1 | 69 | 9.36 | 1 | 69
COCFD | 2 | 1 | 43 | 21.31 | 1 | 43
COCFD | 2 | 1 | 50 | 17.61 | 1 | 50
COCFD | 2 | 1 | 65 | 10.46 | 1 | 65
COCFD | 2 | 1 | 69 | 9.64 | 1 | 69
COCFD | 2 | 1 | 78 | 7.01 | 1 | 78
COCFD | 2 | 1 | 79 | 6.39 | 1 | 79
COCFD | 2 | 1 | 75 | 8.71 | 1 | 75
COCFD | 2 | 1 | 72 | 7.5 | 1 | 72
COCFD | 2 | 1 | 66 | 9.42 | 1 | 66
COCFD | 2 | 1 | 62 | 11.73 | 1 | 62
COCFD | 2 | 1 | 66 | 11.12 | 1 | 66
COCFD | 2 | 1 | 69 | 9.71 | 1 | 69
COCFD | 2 | 1 | 68 | 9.53 | 1 | 68
COCFD | 2 | 1 | 65 | 9.72 | 1 | 65
KE ECAM | 2 | 1 | 68 | 16.93 | 1 | 68
KE ECAM | 2 | 1 | 66 | 12.05 | 1 | 66
KE ECAM | 2 | 1 | 65 | 12.97 | 1 | 65
KE ECAM | 2 | 1 | 70 | 10.35 | 1 | 70
KE ECAM | 2 | 1 | 74 | 8.51 | 1 | 74
KE ECAM | 2 | 1 | 71 | 11.1 | 1 | 71
KE ECAM | 2 | 1 | 66 | 11.65 | 1 | 66
KE ECAM | 2 | 1 | 72 | 12.36 | 1 | 72
KE ECAM | 2 | 1 | 69 | 10.35 | 1 | 69
KE ECAM | 2 | 1 | 69 | 10.5 | 1 | 69
KE ECAM | 2 | 1 | 72 | 10.37 | 1 | 72
KE ECAM | 2 | 1 | 72 | 11.15 | 1 | 72
KE ECAM | 2 | 1 | 75 | 10.83 | 1 | 75
KE ECAM | 2 | 1 | 78 | 7.17 | 1 | 78
KE ECAM | 2 | 1 | 73 | 12.69 | 1 | 73
KE ECAM | 2 | 1 | 66 | 14.54 | 1 | 66
KE ECAM | 2 | 1 | 63 | 12.58 | 1 | 63
KE ECAM | 2 | 1 | 59 | 13.99 | 1 | 59
KE ECAM | 2 | 1 | 60 | 13.88 | 1 | 60
KE ECAM | 2 | 1 | 65 | 13.56 | 1 | 65
KE ECAM | 2 | 1 | 59 | 14.75 | 1 | 59
KE ECAM | 2 | 1 | 60 | 15.37 | 1 | 60
KE ECAM | 2 | 1 | 50 | 20.37 | 1 | 50
KE ECAM | 2 | 1 | 81 | 7.73 | 1 | 81
KE ECAM | 2 | 1 | 71 | 16.36 | 1 | 71
KE ECAM | 2 | 1 | 70 | 11.17 | 1 | 70
KE ECAM | 2 | 1 | 54 | 14.73 | 1 | 54
KE ECAM | 2 | 1 | 79 | 10.78 | 1 | 79
KRMC | 3 | 0 | 71 | 14.29 | 6 | 426
KRMC | 3 | 0 | 76 | 13.02 | 6 | 456
KRMC | 3 | 0 | 72 | 15.42 | 6 | 432
KRMC | 3 | 0 | 72 | 14.38 | 6 | 432
KRMC | 3 | 0 | 72 | 14.21 | 6 | 432
KRMC | 3 | 0 | 74 | 14.39 | 6 | 444
KRMC | 3 | 0 | 73 | 13.16 | 6 | 438
KRMC | 3 | 0 | 71 | 14.88 | 6 | 426
KRMC | 3 | 0 | 67 | 16.17 | 6 | 402
KRMC | 3 | 0 | 71 | 10.77 | 6 | 426
KRMC | 3 | 0 | 67 | 18.29 | 6 | 402
KRMC | 3 | 0 | 76 | 13.36 | 6 | 456
KRMC | 3 | 0 | 68 | 18.15 | 6 | 408
KRMC | 3 | 0 | 62 | 23.68 | 6 | 372
KRMC | 3 | 0 | 58 | 24.13 | 6 | 348
KRMC | 3 | 0 | 52 | 25.73 | 6 | 312
KRMC | 3 | 0 | 55 | 25.04 | 6 | 330
KRMC | 3 | 0 | 52 | 27.79 | 6 | 312
KRMC | 3 | 0 | 56 | 27.79 | 6 | 336
KRMC | 3 | 0 | 53 | 27.79 | 6 | 318
KRMC | 3 | 0 | 54 | 27.92 | 6 | 324
KRMC | 3 | 0 | 54 | 29.43 | 6 | 324
KRMC | 3 | 0 | 51 | 31.62 | 6 | 306
KRMC | 3 | 0 | 54 | 29.98 | 6 | 324
KRMC | 3 | 0 | 56 | 26.97 | 6 | 336
KRMC | 3 | 0 | 58 | 26.69 | 6 | 348
KRMC | 3 | 0 | 59 | 26.56 | 6 | 354
KRMC | 3 | 0 | 62 | 21.39 | 6 | 372
KRMC | 3 | 0 | 50 | 29.57 | 6 | 300
KRMC | 3 | 0 | 51 | 29.43 | 6 | 306
KRMC | 3 | 0 | 51 | 29.02 | 6 | 306
KRMC | 3 | 0 | 57 | 26.97 | 6 | 342
KRMC | 3 | 0 | 58 | 26.28 | 6 | 348
KRMC | 3 | 0 | 52 | 28.06 | 6 | 312
KRMC | 3 | 0 | 62 | 18.9 | 6 | 372
KRMC | 3 | 0 | 47 | 31.21 | 6 | 282
KRMC | 3 | 0 | 60 | 13.42 | 6 | 360
KRMC | 3 | 0 | 49 | 28.2 | 6 | 294
KRMC | 3 | 0 | 49 | 29.43 | 6 | 294
KRMC | 3 | 0 | 78 | 11.77 | 6 | 468
KRMC | 3 | 0 | 62 | 22.59 | 6 | 372
KRMC | 3 | 0 | 71 | 10.99 | 6 | 426
KRMC | 3 | 0 | 65 | 20.95 | 6 | 390
KRMC | 3 | 0 | 42 | 34.49 | 6 | 252
KRMC | 3 | 0 | 67 | 18.24 | 6 | 402
KRMC | 3 | 0 | 72 | 15.53 | 6 | 432
KRMC | 3 | 0 | 68 | 15.72 | 6 | 408
KRMC | 3 | 0 | 62 | 18.2 | 6 | 372
KRMC | 3 | 0 | 68 | 18.27 | 6 | 408
KRMC | 3 | 0 | 62 | 14.68 | 6 | 372
KRMC | 3 | 0 | 77 | 13.15 | 6 | 462
KRMC | 3 | 0 | 70 | 14.5 | 6 | 420
KRMC | 3 | 0 | 70 | 17.17 | 6 | 420
KRMC | 3 | 0 | 65 | 19.53 | 6 | 390
KRMC | 3 | 0 | 65 | 19.49 | 6 | 390
KRMC | 3 | 0 | 71 | 17.72 | 6 | 426
KRMC | 3 | 0 | 74 | 12.91 | 6 | 444
KRMC | 3 | 0 | 66 | 20 | 6 | 396
KRMC | 3 | 0 | 53 | 26.69 | 6 | 318
KRMC | 3 | 0 | 64 | 19.92 | 6 | 384
KRMC | 3 | 0 | 59 | 24.09 | 6 | 354
KRMC | 3 | 0 | 66 | 14.99 | 6 | 396
KRMC | 3 | 0 | 55 | 17.72 | 6 | 330
KRMC | 3 | 0 | 64 | 18.21 | 6 | 384
KRMC | 3 | 0 | 51 | 28.2 | 6 | 306
KRMC | 3 | 0 | 48 | 25.88 | 6 | 288
KRMC | 3 | 0 | 58 | 27.19 | 6 | 348
KRMC | 3 | 0 | 58 | 22.84 | 6 | 348
KRMC | 3 | 0 | 59 | 14 | 6 | 354
KRMC | 3 | 0 | 68 | 17.48 | 6 | 408
KRMC | 3 | 0 | 73 | 16.97 | 6 | 438
KRMC | 3 | 0 | 61 | 25.53 | 6 | 366
KRMC | 3 | 0 | 69 | 16.85 | 6 | 414
KRMC | 3 | 0 | 65 | 19.93 | 6 | 390
KRMC | 3 | 0 | 61 | 21.35 | 6 | 366
COCTV | 2 | 1 | 79 | 6.47 | 1 | 79
COCTV | 2 | 1 | 66 | 8.82 | 1 | 66
COCTV | 2 | 1 | 75 | 6.72 | 1 | 75
COCTV | 2 | 1 | 69 | 7.28 | 1 | 69
COCTV | 2 | 1 | 65 | 7.09 | 1 | 65
COCTV | 2 | 1 | 70 | 6.24 | 1 | 70
COCTV | 2 | 1 | 66 | 8.71 | 1 | 66
COCTV | 2 | 1 | 62 | 8.78 | 1 | 62
COCTV | 2 | 1 | 69 | 7.62 | 1 | 69
COCTV | 2 | 1 | 68 | 7.36 | 1 | 68
COCTV | 2 | 1 | 73 | 7.39 | 1 | 73
COCTV | 2 | 1 | 66 | 8.88 | 1 | 66
COCTV | 2 | 1 | 76 | 5.31 | 1 | 76
COCTV | 2 | 1 | 73 | 6.52 | 1 | 73
COCTV | 2 | 1 | 78 | 6.54 | 1 | 78
COCTV | 2 | 1 | 81 | 6.89 | 1 | 81
COCTV | 2 | 1 | 74 | 5.81 | 1 | 74
COCTV | 2 | 1 | 61 | 7.77 | 1 | 61
COCTV | 2 | 1 | 76 | 6.11 | 1 | 76
COCTV | 2 | 1 | 63 | 8.66 | 1 | 63
COCTV | 2 | 1 | 72 | 5.25 | 1 | 72
COCTV | 2 | 1 | 69 | 7.89 | 1 | 69
COCTV | 2 | 1 | 64 | 9.89 | 1 | 64
COCTV | 2 | 1 | 70 | 7.76 | 1 | 70
COCTV | 2 | 1 | 58 | 10.48 | 1 | 58
COCTV | 2 | 1 | 57 | 10.26 | 1 | 57
COCTV | 2 | 1 | 67 | 7.51 | 1 | 67
COCTV | 2 | 1 | 78 | 4.96 | 1 | 78
COCTV | 2 | 1 | 78 | 4.93 | 1 | 78
COCTV | 2 | 1 | 76 | 5.97 | 1 | 76
COCTV | 2 | 1 | 81 | 4.98 | 1 | 81
COCTV | 2 | 1 | 80 | 4.56 | 1 | 80
TCWWTP | 1 | 1 | 12 | 9.48 | 1 | 12
TCWWTP | 1 | 1 | 32 | 7.79 | 1 | 32
TCWWTP | 1 | 1 | 29 | 8.01 | 1 | 29
TCWWTP | 1 | 1 | 38 | 7.82 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.02 | 1 | 34
TCWWTP | 1 | 1 | 33 | 8.17 | 1 | 33
TCWWTP | 1 | 1 | 33 | 8.26 | 1 | 33
TCWWTP | 1 | 1 | 31 | 8.39 | 1 | 31
TCWWTP | 1 | 1 | 31 | 8.22 | 1 | 31
TCWWTP | 1 | 1 | 33 | 8.56 | 1 | 33
TCWWTP | 1 | 1 | 34 | 8.1 | 1 | 34
TCWWTP | 1 | 1 | 35 | 8.48 | 1 | 35
TCWWTP | 1 | 1 | 22 | 8.26 | 1 | 22
TCWWTP | 1 | 1 | 30 | 8.8 | 1 | 30
TCWWTP | 1 | 1 | 29 | 8.52 | 1 | 29
TCWWTP | 1 | 1 | 31 | 8.56 | 1 | 31
TCWWTP | 1 | 1 | 39 | 7.86 | 1 | 39
TCWWTP | 1 | 1 | 22 | 8.58 | 1 | 22
TCWWTP | 1 | 1 | 22 | 8.38 | 1 | 22
TCWWTP | 1 | 1 | 19 | 9.05 | 1 | 19
TCWWTP | 1 | 1 | 27 | 8.4 | 1 | 27
TCWWTP | 1 | 1 | 30 | 8.21 | 1 | 30
TCWWTP | 1 | 1 | 38 | 8.13 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.15 | 1 | 34
TCWWTP | 1 | 1 | 32 | 8.02 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.22 | 1 | 25
TCWWTP | 1 | 1 | 19 | 8.66 | 1 | 19
TCWWTP | 1 | 1 | 30 | 7.94 | 1 | 30
TCWWTP | 1 | 1 | 18 | 8.99 | 1 | 18
TCWWTP | 1 | 1 | 34 | 8.21 | 1 | 34
TCWWTP | 1 | 1 | 26 | 8.22 | 1 | 26
TCWWTP | 1 | 1 | 3 | 9.57 | 1 | 3
TCWWTP | 1 | 1 | 5 | 9.52 | 1 | 5
TCWWTP | 1 | 1 | 26 | 8.55 | 1 | 26
TCWWTP | 1 | 1 | 26 | 8.41 | 1 | 26
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 36 | 7.55 | 1 | 36
TCWWTP | 1 | 1 | 24 | 8.82 | 1 | 24
TCWWTP | 1 | 1 | 22 | 8.55 | 1 | 22
TCWWTP | 1 | 1 | 16 | 9.03 | 1 | 16
TCWWTP | 1 | 1 | 19 | 8.73 | 1 | 19
TCWWTP | 1 | 1 | 39 | 7.17 | 1 | 39
TCWWTP | 1 | 1 | 30 | 7.02 | 1 | 30
TCWWTP | 1 | 1 | 37 | 7.08 | 1 | 37
TCWWTP | 1 | 1 | 28 | 7.83 | 1 | 28
TCWWTP | 1 | 1 | 32 | 8.65 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 16 | 7.7 | 1 | 16
TCWWTP | 1 | 1 | 27 | 8.19 | 1 | 27
TCWWTP | 1 | 1 | 30 | 7.1 | 1 | 30
TCWWTP | 1 | 1 | 15 | 8.83 | 1 | 15
TCWWTP | 1 | 1 | 33 | 8.41 | 1 | 33
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 38 | 8.06 | 1 | 38
TCWWTP | 1 | 1 | 32 | 7.87 | 1 | 32
TCWWTP | 1 | 1 | 37 | 7.99 | 1 | 37
TCWWTP | 1 | 1 | 35 | 8.99 | 1 | 35
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 39 | 7.74 | 1 | 39
TCWWTP | 1 | 1 | 15 | 8.89 | 1 | 15
TCWWTP | 1 | 1 | 19 | 8.77 | 1 | 19
TCWWTP | 1 | 1 | 29 | 8.39 | 1 | 29
TCWWTP | 1 | 1 | 35 | 8.57 | 1 | 35
TCWWTP | 1 | 1 | 34 | 7.95 | 1 | 34
TCWWTP | 1 | 1 | 36 | 7.69 | 1 | 36
TCWWTP | 1 | 1 | 23 | 9.35 | 1 | 23
TCWWTP | 1 | 1 | 24 | 8.18 | 1 | 24
TCWWTP | 1 | 1 | 39 | 7.02 | 1 | 39
TCWWTP | 1 | 1 | 42 | 7.72 | 1 | 42
TCWWTP | 1 | 1 | 41 | 8.17 | 1 | 41
TCWWTP | 1 | 1 | 25 | 8.17 | 1 | 25
TCWWTP | 1 | 1 | 36 | 8.28 | 1 | 36
TCWWTP | 1 | 1 | 34 | 8.16 | 1 | 34
TCWWTP | 1 | 1 | 40 | 7.97 | 1 | 40
TCWWTP | 1 | 1 | 32 | 8.14 | 1 | 32
TCWWTP | 1 | 1 | 28 | 7.21 | 1 | 28
TCWWTP | 1 | 1 | 33 | 7.14 | 1 | 33
TCWWTP | 1 | 1 | 27 | 7.16 | 1 | 27
TCWWTP | 1 | 1 | 18 | 9.38 | 1 | 18
TCWP | 2 | 1 | 45 | 10.17 | 1 | 45
TCWP | 2 | 1 | 35 | 10.82 | 1 | 35
TCWP | 2 | 1 | 37 | 10.57 | 1 | 37
TCWP | 2 | 1 | 37 | 10.64 | 1 | 37
TCWP | 2 | 1 | 31 | 10.96 | 1 | 31
TCWP | 2 | 1 | 31 | 11.14 | 1 | 31
TCWP | 2 | 1 | 33 | 10.77 | 1 | 33
TCWP | 2 | 1 | 44 | 10.73 | 1 | 44
TCWP | 2 | 1 | 28 | 11.01 | 1 | 28
TCWP | 2 | 1 | 34 | 10.58 | 1 | 34
TCWP | 2 | 1 | 33 | 10.71 | 1 | 33
TCWP | 2 | 1 | 38 | 10.75 | 1 | 38
TCWP | 2 | 1 | 37 | 10.92 | 1 | 37
TCWP | 2 | 1 | 30 | 10.54 | 1 | 30
TCWP | 2 | 1 | 32 | 9.94 | 1 | 32
TCWP | 2 | 1 | 37 | 10.42 | 1 | 37
TCWP | 2 | 1 | 34 | 10.4 | 1 | 34
TCWP | 2 | 1 | 50 | 10.27 | 1 | 50
TCWP | 2 | 1 | 29 | 10.54 | 1 | 29
TCWP | 2 | 1 | 51 | 9.15 | 1 | 51
TCWP | 2 | 1 | 35 | 9.89 | 1 | 35
TCWP | 2 | 1 | 33 | 10.34 | 1 | 33
TCWP | 2 | 1 | 40 | 9.99 | 1 | 40
TCWP | 2 | 1 | 34 | 10.71 | 1 | 34
TCWP | 2 | 1 | 34 | 9.68 | 1 | 34
TCWP | 2 | 1 | 50 | 10.4 | 1 | 50
TCWP | 2 | 1 | 29 | 10.73 | 1 | 29
TCWP | 2 | 1 | 44 | 10.78 | 1 | 44
TCWP | 2 | 1 | 41 | 10.68 | 1 | 41
TCWP | 2 | 1 | 39 | 10.71 | 1 | 39
TCWP | 2 | 1 | 35 | 10.66 | 1 | 35
TCWP | 2 | 1 | 32 | 10.73 | 1 | 32
TCWP | 2 | 1 | 39 | 10.46 | 1 | 39
TCWP | 2 | 1 | 43 | 10.08 | 1 | 43
TCWP | 2 | 1 | 35 | 10.91 | 1 | 35
TCWP | 2 | 1 | 32 | 10.45 | 1 | 32
TCWP | 2 | 1 | 32 | 10.51 | 1 | 32
TCWP | 2 | 1 | 30 | 10.78 | 1 | 30
TCWP | 2 | 1 | 40 | 10.71 | 1 | 40
TCWP | 2 | 1 | 29 | 11.05 | 1 | 29
HCNW | 1 | 0 | 54 | 37.7 | 6 | 324
HCNW | 1 | 0 | 58 | 19.7 | 6 | 348
HCNW | 1 | 0 | 54 | 29.2 | 6 | 324
HCNW | 1 | 0 | 51 | 41 | 6 | 306
HCNW | 1 | 0 | 51 | 42.2 | 6 | 306
HCNW | 1 | 0 | 44 | 46.2 | 6 | 264
HCNW | 1 | 0 | 38 | 54.9 | 6 | 228
HCNW | 1 | 0 | 34 | 55.2 | 6 | 204
HCNW | 1 | 0 | 43 | 51.4 | 6 | 258
HCNW | 1 | 0 | 55 | 38.2 | 6 | 330
HCNW | 1 | 0 | 60 | 18.8 | 6 | 360
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 43 | 49.5 | 6 | 258
HCNW | 1 | 0 | 35 | 56.8 | 6 | 210
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 47 | 46.9 | 6 | 282
HCNW | 1 | 0 | 44 | 48.8 | 6 | 264
HCNW | 1 | 0 | 34 | 57 | 6 | 204
HCNW | 1 | 0 | 53 | 40.3 | 6 | 318
HCNW | 1 | 0 | 51 | 40 | 6 | 306
HCNW | 1 | 0 | 56 | 35.6 | 6 | 336
HCNW | 1 | 0 | 53 | 37 | 6 | 318
HCNW | 1 | 0 | 54 | 36.3 | 6 | 324
HCNW | 1 | 0 | 54 | 37.2 | 6 | 324
HCNW | 1 | 0 | 50 | 41.5 | 6 | 300
HCNW | 1 | 0 | 47 | 44.3 | 6 | 282
HCNW | 1 | 0 | 42 | 48.1 | 6 | 252
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 59 | 31.8 | 6 | 354
HCNW | 1 | 0 | 57 | 34.4 | 6 | 342
HCNW | 1 | 0 | 62 | 28 | 6 | 372
HCNW | 1 | 0 | 51 | 40.8 | 6 | 306
HCNW | 1 | 0 | 51 | 39.1 | 6 | 306
HCNW | 1 | 0 | 49 | 37.9 | 6 | 294
HCNW | 1 | 0 | 49 | 41.7 | 6 | 294
HCNW | 1 | 0 | 53 | 38.2 | 6 | 318
HCNW | 1 | 0 | 62 | 29.9 | 6 | 372
HCNW | 1 | 0 | 65 | 25.6 | 6 | 390
HCNW | 1 | 0 | 62 | 29.7 | 6 | 372
HCNW | 1 | 0 | 35 | 52.5 | 6 | 210
HCNW | 1 | 0 | 58 | 33.4 | 6 | 348
HCNW | 1 | 0 | 32 | 57.3 | 6 | 192
HCNW | 1 | 0 | 27 | 64.4 | 6 | 162
HCNW | 1 | 0 | 52 | 38.9 | 6 | 312
HCNW | 1 | 0 | 26 | 64.4 | 6 | 156
HCNW | 1 | 0 | 41 | 50.9 | 6 | 246
HCNW | 1 | 0 | 31 | 60.4 | 6 | 186
HCNW | 1 | 0 | 37 | 53.2 | 6 | 222
HCNW | 1 | 0 | 34 | 55.7 | 6 | 204
HCNW | 1 | 0 | 38 | 52.8 | 6 | 228
HCNW | 1 | 0 | 42 | 47.4 | 6 | 252
HCNW | 1 | 0 | 38 | 51 | 6 | 228
HCNW | 1 | 0 | 41 | 51.8 | 6 | 246
HCNW | 1 | 0 | 43 | 47.8 | 6 | 258
HCNW | 1 | 0 | 42 | 47.7 | 6 | 252
HCNW | 1 | 0 | 49 | 43 | 6 | 294
HCNW | 1 | 0 | 40 | 50.6 | 6 | 240
HCNW | 1 | 0 | 35 | 57.8 | 6 | 210
HCNW | 1 | 0 | 33 | 59 | 6 | 198
HCNW | 1 | 0 | 31 | 57.6 | 6 | 186
HCNW | 1 | 0 | 36 | 56.4 | 6 | 216
HCNW | 1 | 0 | 35 | 49.6 | 6 | 210
HCNW | 1 | 0 | 36 | 55.3 | 6 | 216
HCNW | 1 | 0 | 37 | 51.4 | 6 | 222
HCNW | 1 | 0 | 33 | 58.2 | 6 | 198
HCNW | 1 | 0 | 42 | 46.7 | 6 | 252
HCNW | 1 | 0 | 43 | 46.5 | 6 | 258
HCNW | 1 | 0 | 44 | 45.8 | 6 | 264
HCNW | 1 | 0 | 46 | 41.6 | 6 | 276
HCNW | 1 | 0 | 47 | 42.5 | 6 | 282
HCNW | 1 | 0 | 49 | 42.1 | 6 | 294
HCNW | 1 | 0 | 44 | 44.6 | 6 | 264
HCNW | 1 | 0 | 36 | 57.5 | 6 | 216
HCNW | 1 | 0 | 46 | 47.3 | 6 | 276
HCNW | 1 | 0 | 30 | 60.2 | 6 | 180
HCNW | 1 | 0 | 27 | 62.5 | 6 | 162
HCNW | 1 | 0 | 33 | 60.7 | 6 | 198
HCNW | 1 | 0 | 33 | 51.9 | 6 | 198
HCNW | 1 | 0 | 43 | 49.3 | 6 | 258
HCNW | 1 | 0 | 39 | 53 | 6 | 234
HCNW | 1 | 0 | 38 | 54.2 | 6 | 228
HCNW | 1 | 0 | 35 | 57.5 | 6 | 210
HCNW | 1 | 0 | 32 | 48.1 | 6 | 192
HCNW | 1 | 0 | 30 | 61.2 | 6 | 180
HCNW | 1 | 0 | 49 | 43.2 | 6 | 294
HCNW | 1 | 0 | 33 | 53.8 | 6 | 198
PCDC | 2 | 0 | 56 | 35.7 | 6 | 336
PCDC | 2 | 0 | 35 | 54.4 | 6 | 210
PCDC | 2 | 0 | 49 | 48 | 6 | 294
PCDC | 2 | 0 | 57 | 38.7 | 6 | 342
PCDC | 2 | 0 | 56 | 37.5 | 6 | 336
PCDC | 2 | 0 | 59 | 34.8 | 6 | 354
PCDC | 2 | 0 | 54 | 32.1 | 6 | 324
PCDC | 2 | 0 | 44 | 39.4 | 6 | 264
PCDC | 2 | 0 | 55 | 30.4 | 6 | 330
PCDC | 2 | 0 | 46 | 53.7 | 6 | 276
PCDC | 2 | 0 | 56 | 27.3 | 6 | 336
PCDC | 2 | 0 | 59 | 25.6 | 6 | 354
PCDC | 2 | 0 | 48 | 49 | 6 | 288
PCDC | 2 | 0 | 34 | 63 | 6 | 204
PCDC | 2 | 0 | 51 | 43.2 | 6 | 306
PCDC | 2 | 0 | 44 | 52.7 | 6 | 264
PCDC | 2 | 0 | 57 | 39.8 | 6 | 342
PCDC | 2 | 0 | 42 | 52.7 | 6 | 252
PCDC | 2 | 0 | 49 | 47.7 | 6 | 294
PCDC | 2 | 0 | 58 | 35.4 | 6 | 348
PCDC | 2 | 0 | 59 | 34.3 | 6 | 354
PCDC | 2 | 0 | 59 | 36.2 | 6 | 354
PCDC | 2 | 0 | 63 | 30.7 | 6 | 378
PCDC | 2 | 0 | 62 | 33.8 | 6 | 372
PCDC | 2 | 0 | 60 | 36.5 | 6 | 360
PCDC | 2 | 0 | 38 | 59.1 | 6 | 228
PCDC | 2 | 0 | 38 | 58.9 | 6 | 228
PCDC | 2 | 0 | 37 | 48.4 | 6 | 222
PCDC | 2 | 0 | 48 | 49.1 | 6 | 288
PCDC | 2 | 0 | 44 | 44.4 | 6 | 264
PCDC | 2 | 0 | 34 | 62.4 | 6 | 204
PCDC | 2 | 0 | 45 | 42.2 | 6 | 270
PCDC | 2 | 0 | 57 | 37.1 | 6 | 342
PCDC | 2 | 0 | 64 | 31.3 | 6 | 384
PCDC | 2 | 0 | 57 | 35.6 | 6 | 342
PCDC | 2 | 0 | 44 | 51.3 | 6 | 264
PCDC | 2 | 0 | 31 | 72 | 6 | 186
PCDC | 2 | 0 | 48 | 51.3 | 6 | 288
PCDC | 2 | 0 | 46 | 50.6 | 6 | 276
PCDC | 2 | 0 | 43 | 51 | 6 | 258
PCDC | 2 | 0 | 45 | 50.5 | 6 | 270
PCDC | 2 | 0 | 40 | 59.6 | 6 | 240
PCDC | 2 | 0 | 58 | 36.2 | 6 | 348
PCDC | 2 | 0 | 41 | 57.7 | 6 | 246
PCDC | 2 | 0 | 61 | 33.8 | 6 | 366
PCDC | 2 | 0 | 43 | 53.6 | 6 | 258
PCDC | 2 | 0 | 48 | 48.5 | 6 | 288
PCDC | 2 | 0 | 43 | 45.5 | 6 | 258
PCDC | 2 | 0 | 54 | 39.6 | 6 | 324
PCDC | 2 | 0 | 61 | 32.2 | 6 | 366
PCDC | 2 | 0 | 57 | 37 | 6 | 342
COMW | 2 | 1 | 36 | 18.4 | 1 | 36
COMW | 2 | 1 | 45 | 16.9 | 1 | 45
COMW | 2 | 1 | 52 | 15.3 | 1 | 52
COMW | 2 | 1 | 53 | 15.9 | 1 | 53
COMW | 2 | 1 | 53 | 14.2 | 1 | 53
COMW | 2 | 1 | 50 | 15.1 | 1 | 50
COMW | 2 | 1 | 43 | 15.3 | 1 | 43
COMW | 2 | 1 | 29 | 16.9 | 1 | 29
COMW | 2 | 1 | 40 | 14 | 1 | 40
COMW | 2 | 1 | 44 | 15.6 | 1 | 44
COMW | 2 | 1 | 35 | 16.9 | 1 | 35
COMW | 2 | 1 | 37 | 18.1 | 1 | 37
COMW | 2 | 1 | 32 | 15.8 | 1 | 32
COMW | 2 | 1 | 31 | 16.9 | 1 | 31
COMW | 2 | 1 | 32 | 17.1 | 1 | 32
COMW | 2 | 1 | 35 | 16.6 | 1 | 35
COMW | 2 | 1 | 40 | 16.6 | 1 | 40
COMW | 2 | 1 | 43 | 15.2 | 1 | 43
COMW | 2 | 1 | 43 | 16.2 | 1 | 43
COMW | 2 | 1 | 42 | 14.7 | 1 | 42
COMW | 2 | 1 | 46 | 16.3 | 1 | 46
COMW | 2 | 1 | 34 | 16.5 | 1 | 34
COMKR | 2 | 1 | 40 | 10.9 | 1 | 40
COMKR | 2 | 1 | 43 | 11.1 | 1 | 43
COMKR | 2 | 1 | 50 | 8.7 | 1 | 50
COMKR | 2 | 1 | 53 | 9.3 | 1 | 53
COMKR | 2 | 1 | 53 | 10.8 | 1 | 53
COMKR | 2 | 1 | 52 | 10.6 | 1 | 52
COMKR | 2 | 1 | 35 | 11.9 | 1 | 35
COMKR | 2 | 1 | 36 | 12.5 | 1 | 36
COMKR | 2 | 1 | 32 | 12.8 | 1 | 32
COMKR | 2 | 1 | 45 | 12.7 | 1 | 45
COMKR | 2 | 1 | 29 | 12.8 | 1 | 29
COMKR | 2 | 1 | 34 | 12.3 | 1 | 34
COMKR | 2 | 1 | 46 | 11.8 | 1 | 46
COMKR | 2 | 1 | 37 | 11.4 | 1 | 37
COMKR | 2 | 1 | 32 | 14.7 | 1 | 32
COMKR | 2 | 1 | 31 | 13.4 | 1 | 31
COMKR | 2 | 1 | 35 | 12.9 | 1 | 35
COMKR | 2 | 1 | 43 | 10.6 | 1 | 43
COMKR | 2 | 1 | 43 | 11.7 | 1 | 43
COMKR | 2 | 1 | 42 | 11.2 | 1 | 42
COMKR | 2 | 1 | 44 | 10.1 | 1 | 44
COMKR | 2 | 1 | 40 | 13.5 | 1 | 40
COCWWTP | 3 | 0 | 81 | 32.05 | 6 | 486
COCWWTP | 3 | 0 | 78 | 31.93 | 6 | 468
COCWWTP | 3 | 0 | 79 | 29.67 | 6 | 474
COCWWTP | 3 | 0 | 76 | 28.4 | 6 | 456
COCWWTP | 3 | 0 | 76 | 30.83 | 6 | 456
COCWWTP | 3 | 0 | 62 | 40.46 | 6 | 372
COCWWTP | 3 | 0 | 54 | 44.24 | 6 | 324
COCWWTP | 3 | 0 | 67 | 34.75 | 6 | 402
COCWWTP | 3 | 0 | 69 | 38.29 | 6 | 414
COCWWTP | 3 | 0 | 68 | 35.65 | 6 | 408
COCWWTP | 3 | 0 | 65 | 44.66 | 6 | 390
COCWWTP | 3 | 0 | 54 | 55.77 | 6 | 324
COCWWTP | 3 | 0 | 51 | 55.72 | 6 | 306
COCWWTP | 3 | 0 | 52 | 52.55 | 6 | 312
COCWWTP | 3 | 0 | 60 | 46.88 | 6 | 360
COCWWTP | 3 | 0 | 60 | 42.96 | 6 | 360
COCWWTP | 3 | 0 | 50 | 60.42 | 6 | 300
COCWWTP | 3 | 0 | 65 | 38.29 | 6 | 390
COCWWTP | 3 | 0 | 64 | 47.7 | 6 | 384
COCWWTP | 3 | 0 | 65 | 38.9 | 6 | 390
COCWWTP | 3 | 0 | 56 | 50.26 | 6 | 336
COCWWTP | 3 | 0 | 54 | 51.97 | 6 | 324
COCWWTP | 3 | 0 | 54 | 49.76 | 6 | 324
COCWWTP | 3 | 0 | 49 | 61.9 | 6 | 294
COCWWTP | 3 | 0 | 54 | 52.64 | 6 | 324
COCWWTP | 3 | 0 | 56 | 52.56 | 6 | 336
COCWWTP | 3 | 0 | 48 | 60.48 | 6 | 288
COCWWTP | 3 | 0 | 43 | 66.12 | 6 | 258
COCWWTP | 3 | 0 | 63 | 43.44 | 6 | 378
COCWWTP | 3 | 0 | 70 | 35.71 | 6 | 420
COCWWTP | 3 | 0 | 62 | 43.08 | 6 | 372
COCWWTP | 3 | 0 | 78 | 25.51 | 6 | 468
COCWWTP | 3 | 0 | 68 | 35.74 | 6 | 408
COCWWTP | 3 | 0 | 66 | 41.92 | 6 | 396
COCWWTP | 3 | 0 | 66 | 37.87 | 6 | 396
COCWWTP | 3 | 0 | 72 | 30.53 | 6 | 432
COCWWTP | 3 | 0 | 69 | 32.6 | 6 | 414
COCWWTP | 3 | 0 | 75 | 32.73 | 6 | 450
COCWWTP | 3 | 0 | 69 | 37.08 | 6 | 414
COCWWTP | 3 | 0 | 66 | 39.5 | 6 | 396
COCWWTP | 3 | 0 | 51 | 55.2 | 6 | 306
COCWWTP | 3 | 0 | 78 | 26.82 | 6 | 468
COCWWTP | 3 | 0 | 81 | 26.05 | 6 | 486
COCWWTP | 3 | 0 | 76 | 27.53 | 6 | 456
COCWWTP | 3 | 0 | 69 | 35.64 | 6 | 414
COCWWTP | 3 | 0 | 73 | 30.06 | 6 | 438
COCWWTP | 3 | 0 | 67 | 36.65 | 6 | 402
COCWWTP | 3 | 0 | 61 | 44.7 | 6 | 366
COCWWTP | 3 | 0 | 58 | 48.21 | 6 | 348
COCWWTP | 3 | 0 | 63 | 44.13 | 6 | 378
COCWWTP | 3 | 0 | 65 | 36.59 | 6 | 390
COCWWTP | 3 | 0 | 58 | 33.82 | 6 | 348
COCWWTP | 3 | 0 | 57 | 40.95 | 6 | 342
COCWWTP | 3 | 0 | 80 | 16.14 | 6 | 480
COCWWTP | 3 | 0 | 70 | 33.86 | 6 | 420
COCWWTP | 3 | 0 | 73 | 25.06 | 6 | 438
COCWWTP | 3 | 0 | 74 | 29.67 | 6 | 444
COCWWTP | 3 | 0 | 57 | 45.79 | 6 | 342
COCWWTP | 3 | 0 | 49 | 57.41 | 6 | 294
COCCH | 1 | 1 | 43 | 10.92 | 1 | 43
COCCH | 1 | 1 | 75 | 5.69 | 1 | 75
COCCH | 1 | 1 | 65 | 6.05 | 1 | 65
COCCH | 1 | 1 | 66 | 6.18 | 1 | 66
COCCH | 1 | 1 | 70 | 5.47 | 1 | 70
COCCH | 1 | 1 | 48 | 9.79 | 1 | 48
COCCH | 1 | 1 | 56 | 8.88 | 1 | 56
COCCH | 1 | 1 | 54 | 8.39 | 1 | 54
COCCH | 1 | 1 | 69 | 5.75 | 1 | 69
COCCH | 1 | 1 | 49 | 9.58 | 1 | 49
COCCH | 1 | 1 | 68 | 6.16 | 1 | 68
COCCH | 1 | 1 | 49 | 9.53 | 1 | 49
COCCH | 1 | 1 | 51 | 8.89 | 1 | 51
COCCH | 1 | 1 | 54 | 8.04 | 1 | 54
COCCH | 1 | 1 | 78 | 4.5 | 1 | 78
COCCH | 1 | 1 | 74 | 4.48 | 1 | 74
COCCH | 1 | 1 | 81 | 4.91 | 1 | 81
COCCH | 1 | 1 | 69 | 5.99 | 1 | 69
COCCH | 1 | 1 | 54 | 8.46 | 1 | 54
COCCH | 1 | 1 | 79 | 4.88 | 1 | 79
COCCH | 1 | 1 | 66 | 6.86 | 1 | 66
COCCH | 1 | 1 | 76 | 4.95 | 1 | 76
COCCH | 1 | 1 | 70 | 5.14 | 1 | 70
COCCH | 1 | 1 | 73 | 5.66 | 1 | 73
COCCH | 1 | 1 | 69 | 6.21 | 1 | 69
COCCH | 1 | 1 | 78 | 5.17 | 1 | 78
COCCH | 1 | 1 | 62 | 6.84 | 1 | 62
COCCH | 1 | 1 | 66 | 6.01 | 1 | 66
COCCH | 1 | 1 | 72 | 5.01 | 1 | 72
COCCH | 1 | 1 | 76 | 4.63 | 1 | 76
COCCH | 1 | 1 | 58 | 7.58 | 1 | 58
COCCH | 1 | 1 | 78 | 4.44 | 1 | 78
COCCH | 1 | 1 | 80 | 3.54 | 1 | 80
COCCH | 1 | 1 | 81 | 4.31 | 1 | 81
COCCH | 1 | 1 | 76 | 5.27 | 1 | 76
COCCH | 1 | 1 | 69 | 6.46 | 1 | 69
COCCH | 1 | 1 | 73 | 5.58 | 1 | 73
COCCH | 1 | 1 | 67 | 6.66 | 1 | 67
COCCH | 1 | 1 | 61 | 7.24 | 1 | 61
COCCH | 1 | 1 | 57 | 7.56 | 1 | 57
COCCH | 1 | 1 | 58 | 8.15 | 1 | 58
COCCH | 1 | 1 | 63 | 7.36 | 1 | 63
COCCH | 1 | 1 | 65 | 7.53 | 1 | 65
COCCH | 1 | 1 | 50 | 9.31 | 1 | 50
COCCH | 1 | 1 | 60 | 6.8 | 1 | 60
COCCH | 1 | 1 | 56 | 8 | 1 | 56
COCCH | 1 | 1 | 62 | 7.56 | 1 | 62
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
COCCH | 1 | 1 | 67 | 5.7 | 1 | 67
COCCH | 1 | 1 | 64 | 8.62 | 1 | 64
COCCH | 1 | 1 | 63 | 6.87 | 1 | 63
COCCH | 1 | 1 | 54 | 9.34 | 1 | 54
COCCH | 1 | 1 | 60 | 7.48 | 1 | 60
COCCH | 1 | 1 | 57 | 7.16 | 1 | 57
COCCH | 1 | 1 | 52 | 8.28 | 1 | 52
COCCH | 1 | 1 | 51 | 8.97 | 1 | 51
COCCH | 1 | 1 | 54 | 8.45 | 1 | 54
COCCH | 1 | 1 | 68 | 6.43 | 1 | 68
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
Kid Kare | 1 | 1 | 41 | 20.69 | 1 | 41
Kid Kare | 1 | 1 | 78 | 7.5 | 1 | 78
Kid Kare | 1 | 1 | 72 | 9.59 | 1 | 72
Kid Kare | 1 | 1 | 68 | 10.17 | 1 | 68
Kid Kare | 1 | 1 | 62 | 11.27 | 1 | 62
Kid Kare | 1 | 1 | 68 | 11.04 | 1 | 68
Kid Kare | 1 | 1 | 43 | 22.64 | 1 | 43
Kid Kare | 1 | 1 | 39 | 20.69 | 1 | 39
Kid Kare | 1 | 1 | 38 | 23.26 | 1 | 38
Kid Kare | 1 | 1 | 35 | 23.28 | 1 | 35
Kid Kare | 1 | 1 | 32 | 18.46 | 1 | 32
Kid Kare | 1 | 1 | 33 | 22.23 | 1 | 33
Kid Kare | 1 | 1 | 63 | 12.61 | 1 | 63
Kid Kare | 1 | 1 | 44 | 19.43 | 1 | 44
Kid Kare | 1 | 1 | 47 | 20.43 | 1 | 47
Kid Kare | 1 | 1 | 51 | 9.5 | 1 | 51
Kid Kare | 1 | 1 | 51 | 9.48 | 1 | 51
Kid Kare | 1 | 1 | 54 | 12.26 | 1 | 54
Kid Kare | 1 | 1 | 56 | 13.89 | 1 | 56
Kid Kare | 1 | 1 | 58 | 11.35 | 1 | 58
Kid Kare | 1 | 1 | 59 | 12.26 | 1 | 59
Kid Kare | 1 | 1 | 62 | 12.26 | 1 | 62
Kid Kare | 1 | 1 | 60 | 11.11 | 1 | 60
Kid Kare | 1 | 1 | 33 | 23.26 | 1 | 33
Kid Kare | 1 | 1 | 62 | 10.31 | 1 | 62
Kid Kare | 1 | 1 | 73 | 9.86 | 1 | 73
Kid Kare | 1 | 1 | 69 | 10.03 | 1 | 69
Kid Kare | 1 | 1 | 68 | 11.18 | 1 | 68
Kid Kare | 1 | 1 | 65 | 11.66 | 1 | 65
Kid Kare | 1 | 1 | 61 | 12.61 | 1 | 61
Kid Kare | 1 | 1 | 59 | 13.78 | 1 | 59
Kid Kare | 1 | 1 | 59 | 13 | 1 | 59
Kid Kare | 1 | 1 | 58 | 13.64 | 1 | 58
Kid Kare | 1 | 1 | 61 | 14.85 | 1 | 61
Kid Kare | 1 | 1 | 77 | 8.39 | 1 | 77
Kid Kare | 1 | 1 | 58 | 15.53 | 1 | 58
Kid Kare | 1 | 1 | 76 | 8.35 | 1 | 76
Kid Kare | 1 | 1 | 48 | 17.38 | 1 | 48
Kid Kare | 1 | 1 | 55 | 14.8 | 1 | 55
Kid Kare | 1 | 1 | 66 | 10.44 | 1 | 66
Kid Kare | 1 | 1 | 66 | 11.75 | 1 | 66
Kid Kare | 1 | 1 | 62 | 12.5 | 1 | 62
Kid Kare | 1 | 1 | 58 | 13.38 | 1 | 58
Kid Kare | 1 | 1 | 52 | 15.88 | 1 | 52
Kid Kare | 1 | 1 | 55 | 11.67 | 1 | 55
Kid Kare | 1 | 1 | 60 | 13.04 | 1 | 60
Kid Kare | 1 | 1 | 64 | 11.97 | 1 | 64
Kid Kare | 1 | 1 | 58 | 22.14 | 1 | 58
Kid Kare | 1 | 1 | 71 | 9.59 | 1 | 71
Kid Kare | 1 | 1 | 64 | 12.42 | 1 | 64
Kid Kare | 1 | 1 | 70 | 10.52 | 1 | 70
Kid Kare | 1 | 1 | 70 | 9.76 | 1 | 70
Kid Kare | 1 | 1 | 65 | 16.86 | 1 | 65
Kid Kare | 1 | 1 | 67 | 10.61 | 1 | 67
Kid Kare | 1 | 1 | 51 | 13.92 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 71 | 8.72 | 1 | 71
Kid Kare | 1 | 1 | 74 | 9.73 | 1 | 74
Kid Kare | 1 | 1 | 63 | 10.92 | 1 | 63
Kid Kare | 1 | 1 | 71 | 9.94 | 1 | 71
Kid Kare | 1 | 1 | 64 | 10.92 | 1 | 64
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.29 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 74 | 9.34 | 1 | 74
Kid Kare | 1 | 1 | 76 | 8.73 | 1 | 76
Kid Kare | 1 | 1 | 73 | 8.9 | 1 | 73
Kid Kare | 1 | 1 | 71 | 9.34 | 1 | 71
Kid Kare | 1 | 1 | 67 | 10.52 | 1 | 67
Kid Kare | 1 | 1 | 68 | 10.35 | 1 | 68
Kid Kare | 1 | 1 | 67 | 12.09 | 1 | 67
Kid Kare | 1 | 1 | 71 | 9.45 | 1 | 71
Kid Kare | 1 | 1 | 51 | 15.23 | 1 | 51
Kid Kare | 1 | 1 | 62 | 17.43 | 1 | 62
Kid Kare | 1 | 1 | 53 | 14.35 | 1 | 53
Kid Kare | 1 | 1 | 49 | 16.25 | 1 | 49
Kid Kare | 1 | 1 | 49 | 14.87 | 1 | 49
Kid Kare | 1 | 1 | 65 | 12.06 | 1 | 65
Kid Kare | 1 | 1 | 51 | 16.27 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 57 | 13.23 | 1 | 57
Kid Kare | 1 | 1 | 52 | 17.6 | 1 | 52
Kid Kare | 1 | 1 | 42 | 17.22 | 1 | 42
Kid Kare | 1 | 1 | 47 | 16.86 | 1 | 47
Kid Kare | 1 | 1 | 62 | 11.99 | 1 | 62
Kid Kare | 1 | 1 | 50 | 13.25 | 1 | 50
Kid Kare | 1 | 1 | 54 | 14.51 | 1 | 54
Kid Kare | 1 | 1 | 55 | 15.2 | 1 | 55
Kid Kare | 1 | 1 | 58 | 14.01 | 1 | 58
Kid Kare | 1 | 1 | 54 | 14.42 | 1 | 54
Kid Kare | 1 | 1 | 53 | 17.53 | 1 | 53
Kid Kare | 1 | 1 | 53 | 15.06 | 1 | 53
Kid Kare | 1 | 1 | 54 | 14.11 | 1 | 54
Kid Kare | 1 | 1 | 54 | 15.27 | 1 | 54
Kid Kare | 1 | 1 | 52 | 15.61 | 1 | 52
BayView | 3 | 1 | 80 | 8.74 | 1.5 | 120
BayView | 3 | 1 | 68 | 12.23 | 1.5 | 102
BayView | 3 | 1 | 60 | 14.08 | 1.5 | 90
BayView | 3 | 1 | 65 | 15.18 | 1.5 | 97.5
BayView | 3 | 1 | 66 | 15.69 | 1.5 | 99
BayView | 3 | 1 | 64 | 15.84 | 1.5 | 96
BayView | 3 | 1 | 61 | 16.67 | 1.5 | 91.5
BayView | 3 | 1 | 70 | 15.07 | 1.5 | 105
BayView | 3 | 1 | 72 | 13.24 | 1.5 | 108
BayView | 3 | 1 | 63 | 15.04 | 1.5 | 94.5
BayView | 3 | 1 | 68 | 14.34 | 1.5 | 102
BayView | 3 | 1 | 66 | 14.26 | 1.5 | 99
BayView | 3 | 1 | 67 | 15.14 | 1.5 | 100.5
BayView | 3 | 1 | 69 | 13.98 | 1.5 | 103.5
BayView | 3 | 1 | 63 | 16.05 | 1.5 | 94.5
BayView | 3 | 1 | 74 | 11.75 | 1.5 | 111
BayView | 3 | 1 | 48 | 21.14 | 1.5 | 72
BayView | 3 | 1 | 77 | 11.9 | 1.5 | 115.5
BayView | 3 | 1 | 55 | 18.48 | 1.5 | 82.5
BayView | 3 | 1 | 53 | 18.99 | 1.5 | 79.5
BayView | 3 | 1 | 59 | 16.45 | 1.5 | 88.5
BayView | 3 | 1 | 60 | 15.65 | 1.5 | 90
BayView | 3 | 1 | 64 | 14.88 | 1.5 | 96
BayView | 3 | 1 | 70 | 14.07 | 1.5 | 105
BayView | 3 | 1 | 63 | 15.02 | 1.5 | 94.5
BayView | 3 | 1 | 72 | 13.41 | 1.5 | 108
BayView | 3 | 1 | 77 | 12.35 | 1.5 | 115.5
BayView | 3 | 1 | 53 | 18.37 | 1.5 | 79.5
BLDG210 | 2 | 0 | 66 | 22.72 | 3 | 198
BLDG210 | 2 | 0 | 68 | 22.83 | 3 | 204
BLDG210 | 2 | 0 | 63 | 25.24 | 3 | 189
BLDG210 | 2 | 0 | 68 | 24.21 | 3 | 204
BLDG210 | 2 | 0 | 70 | 21.78 | 3 | 210
BLDG210 | 2 | 0 | 61 | 26.47 | 3 | 183
BLDG210 | 2 | 0 | 64 | 25.63 | 3 | 192
BLDG210 | 2 | 0 | 66 | 24.01 | 3 | 198
BLDG210 | 2 | 0 | 74 | 25.43 | 3 | 222
BLDG210 | 2 | 0 | 67 | 22.81 | 3 | 201
BLDG210 | 2 | 0 | 77 | 14.89 | 3 | 231
BLDG210 | 2 | 0 | 59 | 26.25 | 3 | 177
BLDG210 | 2 | 0 | 60 | 22.05 | 3 | 180
BLDG210 | 2 | 0 | 69 | 21.65 | 3 | 207
BLDG210 | 2 | 0 | 80 | 16.75 | 3 | 240
BLDG210 | 2 | 0 | 77 | 19.08 | 3 | 231
BLDG210 | 2 | 0 | 72 | 20.72 | 3 | 216
BLDG210 | 2 | 0 | 63 | 27.04 | 3 | 189
BLDG210 | 2 | 0 | 70 | 22.17 | 3 | 210
BLDG210 | 2 | 0 | 60 | 28.55 | 3 | 180
BLDG210 | 2 | 0 | 63 | 27.9 | 3 | 189
BLDG210 | 2 | 0 | 55 | 31.26 | 3 | 165
BLDG210 | 2 | 0 | 53 | 32.4 | 3 | 159
BLDG210 | 2 | 0 | 48 | 33.31 | 3 | 144
BLDG210 | 2 | 0 | 72 | 17.54 | 3 | 216
BLDG210 | 2 | 0 | 53 | 25.38 | 3 | 159
BLDG210 | 2 | 0 | 64 | 25.29 | 3 | 192
BLDG210 | 2 | 0 | 65 | 24.17 | 3 | 195
BNS GEN | 3 | 1 | 68 | 19.59 | 2.5 | 170
BNS GEN | 3 | 1 | 77 | 18.89 | 2.5 | 192.5
BNS GEN | 3 | 1 | 74 | 18.44 | 2.5 | 185
BNS GEN | 3 | 1 | 80 | 13.56 | 2.5 | 200
BNS GEN | 3 | 1 | 60 | 24.43 | 2.5 | 150
BNS GEN | 3 | 1 | 65 | 25.28 | 2.5 | 162.5
BNS GEN | 3 | 1 | 66 | 27.62 | 2.5 | 165
BNS GEN | 3 | 1 | 64 | 26.73 | 2.5 | 160
BNS GEN | 3 | 1 | 61 | 28.58 | 2.5 | 152.5
BNS GEN | 3 | 1 | 70 | 24.45 | 2.5 | 175
BNS GEN | 3 | 1 | 72 | 23.16 | 2.5 | 180
BNS GEN | 3 | 1 | 63 | 25.76 | 2.5 | 157.5
BNS GEN | 3 | 1 | 68 | 25.53 | 2.5 | 170
BNS GEN | 3 | 1 | 66 | 26.12 | 2.5 | 165
BNS GEN | 3 | 1 | 63 | 30.02 | 2.5 | 157.5
BNS GEN | 3 | 1 | 67 | 24.42 | 2.5 | 167.5
BNS GEN | 3 | 1 | 77 | 20.16 | 2.5 | 192.5
BNS GEN | 3 | 1 | 70 | 24.19 | 2.5 | 175
BNS GEN | 3 | 1 | 64 | 27.54 | 2.5 | 160
BNS GEN | 3 | 1 | 59 | 30.4 | 2.5 | 147.5
BNS GEN | 3 | 1 | 63 | 28.78 | 2.5 | 157.5
BNS GEN | 3 | 1 | 55 | 35 | 2.5 | 137.5
BNS GEN | 3 | 1 | 53 | 36.17 | 2.5 | 132.5
BNS GEN | 3 | 1 | 48 | 40.62 | 2.5 | 120
BNS GEN | 3 | 1 | 53 | 36.65 | 2.5 | 132.5
BNS GEN | 3 | 1 | 69 | 22.37 | 2.5 | 172.5
BNS GEN | 3 | 1 | 72 | 23.45 | 2.5 | 180
BNS GEN | 3 | 1 | 60 | 28.74 | 2.5 | 150
NQ | 4 | 1 | 66 | 68.56 | 10 | 660
NQ | 4 | 1 | 45 | 109.25 | 10 | 450
NQ | 4 | 1 | 45 | 112.09 | 10 | 450
NQ | 4 | 1 | 58 | 80.08 | 10 | 580
NQ | 4 | 1 | 51 | 100.12 | 10 | 510
NQ | 4 | 1 | 56 | 81.13 | 10 | 560
NQ | 4 | 1 | 47 | 108.9 | 10 | 470
NQ | 4 | 1 | 48 | 103.73 | 10 | 480
NQ | 4 | 1 | 52 | 90.78 | 10 | 520
NQ | 4 | 1 | 53 | 91.16 | 10 | 530
NQ | 4 | 1 | 55 | 91.45 | 10 | 550
NQ | 4 | 1 | 43 | 128.86 | 10 | 430
NQ | 4 | 1 | 49 | 103.44 | 10 | 490
NQ | 4 | 1 | 52 | 87.74 | 10 | 520
NQ | 4 | 1 | 60 | 70.99 | 10 | 600
NQ | 4 | 1 | 46 | 107.2 | 10 | 460
NQ | 4 | 1 | 33 | 135.86 | 10 | 330
NQ | 4 | 1 | 53 | 93.8 | 10 | 530
NQ | 4 | 1 | 52 | 93.36 | 10 | 520
NQ | 4 | 1 | 55 | 78.49 | 10 | 550
NQ | 4 | 1 | 43 | 124.67 | 10 | 430
NQ | 4 | 1 | 49 | 102.32 | 10 | 490
NQ | 4 | 1 | 41 | 132.18 | 10 | 410
NQ | 4 | 1 | 46 | 125.94 | 10 | 460
NQ | 4 | 1 | 40 | 138.28 | 10 | 400
NQ | 4 | 1 | 36 | 132.52 | 10 | 360
NQ | 4 | 1 | 37 | 142.15 | 10 | 370
NQ | 4 | 1 | 37 | 124.63 | 10 | 370
NQ | 4 | 1 | 39 | 123 | 10 | 390
NQ | 4 | 1 | 46 | 107.66 | 10 | 460
NQ | 4 | 1 | 47 | 105.97 | 10 | 470
NQ | 4 | 1 | 37 | 140.25 | 10 | 370
NQ | 4 | 1 | 44 | 124.86 | 10 | 440
NQ | 4 | 1 | 39 | 132.78 | 10 | 390
NQ | 4 | 1 | 37 | 129.63 | 10 | 370
NQ | 4 | 1 | 41 | 121.86 | 10 | 410
NQ | 4 | 1 | 44 | 109.08 | 10 | 440
NQ | 4 | 1 | 44 | 116.95 | 10 | 440
NQ | 4 | 1 | 44 | 126.81 | 10 | 440
NQ | 4 | 1 | 41 | 112.37 | 10 | 410

## T1 Size1
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
TCWWTP | 1 | 1 | 12 | 9.48 | 1 | 12 | SUMMARY OUTPUT
TCWWTP | 1 | 1 | 32 | 7.79 | 1 | 32
TCWWTP | 1 | 1 | 29 | 8.01 | 1 | 29 | Regression Statistics
TCWWTP | 1 | 1 | 38 | 7.82 | 1 | 38 | Multiple R | 0.97077
TCWWTP | 1 | 1 | 34 | 8.02 | 1 | 34 | R Square | 0.94239
TCWWTP | 1 | 1 | 33 | 8.17 | 1 | 33 | Adjusted R Square | 0.94203
TCWWTP | 1 | 1 | 33 | 8.26 | 1 | 33 | Standard Error | 4.2279
TCWWTP | 1 | 1 | 31 | 8.39 | 1 | 31 | Observations | 320
TCWWTP | 1 | 1 | 31 | 8.22 | 1 | 31
TCWWTP | 1 | 1 | 33 | 8.56 | 1 | 33 | ANOVA
TCWWTP | 1 | 1 | 34 | 8.1 | 1 | 34 |  | df | SS | MS | F | Significance F
TCWWTP | 1 | 1 | 35 | 8.48 | 1 | 35 | Regression | 2 | 92698.299 | 46349.1495 | 2592.9769 | 3.4154e-197
TCWWTP | 1 | 1 | 22 | 8.26 | 1 | 22 | Residual | 317 | 5666.3367 | 17.8749
TCWWTP | 1 | 1 | 30 | 8.8 | 1 | 30 | Total | 319 | 98364.6357
TCWWTP | 1 | 1 | 29 | 8.52 | 1 | 29
TCWWTP | 1 | 1 | 31 | 8.56 | 1 | 31 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
TCWWTP | 1 | 1 | 39 | 7.86 | 1 | 39 | Intercept | 3.7032 | 0.349 | 10.6109 | 1.0392e-22 | 3.0165 | 4.3898 | 3.0165 | 4.3898
TCWWTP | 1 | 1 | 22 | 8.58 | 1 | 22 | X Variable 1 | 13.1354 | 0.31426 | 41.7974 | 5.2816e-131 | 12.5171 | 13.7538 | 12.5171 | 13.7538
TCWWTP | 1 | 1 | 22 | 8.38 | 1 | 22 | X Variable 2 | -0.13649 | 0.0069953 | -19.5119 | 2.9953e-56 | -0.15025 | -0.12273 | -0.15025 | -0.12273
TCWWTP | 1 | 1 | 19 | 9.05 | 1 | 19
TCWWTP | 1 | 1 | 27 | 8.4 | 1 | 27
TCWWTP | 1 | 1 | 30 | 8.21 | 1 | 30
TCWWTP | 1 | 1 | 38 | 8.13 | 1 | 38
TCWWTP | 1 | 1 | 34 | 8.15 | 1 | 34
TCWWTP | 1 | 1 | 32 | 8.02 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.22 | 1 | 25
TCWWTP | 1 | 1 | 19 | 8.66 | 1 | 19
TCWWTP | 1 | 1 | 30 | 7.94 | 1 | 30
TCWWTP | 1 | 1 | 18 | 8.99 | 1 | 18
TCWWTP | 1 | 1 | 34 | 8.21 | 1 | 34
TCWWTP | 1 | 1 | 26 | 8.22 | 1 | 26
TCWWTP | 1 | 1 | 3 | 9.57 | 1 | 3
TCWWTP | 1 | 1 | 5 | 9.52 | 1 | 5
TCWWTP | 1 | 1 | 26 | 8.55 | 1 | 26
TCWWTP | 1 | 1 | 26 | 8.41 | 1 | 26
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 36 | 7.55 | 1 | 36
TCWWTP | 1 | 1 | 24 | 8.82 | 1 | 24
TCWWTP | 1 | 1 | 22 | 8.55 | 1 | 22
TCWWTP | 1 | 1 | 16 | 9.03 | 1 | 16
TCWWTP | 1 | 1 | 19 | 8.73 | 1 | 19
TCWWTP | 1 | 1 | 39 | 7.17 | 1 | 39
TCWWTP | 1 | 1 | 30 | 7.02 | 1 | 30
TCWWTP | 1 | 1 | 37 | 7.08 | 1 | 37
TCWWTP | 1 | 1 | 28 | 7.83 | 1 | 28
TCWWTP | 1 | 1 | 32 | 8.65 | 1 | 32
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 16 | 7.7 | 1 | 16
TCWWTP | 1 | 1 | 27 | 8.19 | 1 | 27
TCWWTP | 1 | 1 | 30 | 7.1 | 1 | 30
TCWWTP | 1 | 1 | 15 | 8.83 | 1 | 15
TCWWTP | 1 | 1 | 33 | 8.41 | 1 | 33
TCWWTP | 1 | 1 | 40 | 7.94 | 1 | 40
TCWWTP | 1 | 1 | 38 | 8.06 | 1 | 38
TCWWTP | 1 | 1 | 32 | 7.87 | 1 | 32
TCWWTP | 1 | 1 | 37 | 7.99 | 1 | 37
TCWWTP | 1 | 1 | 35 | 8.99 | 1 | 35
TCWWTP | 1 | 1 | 25 | 8.4 | 1 | 25
TCWWTP | 1 | 1 | 39 | 7.74 | 1 | 39
TCWWTP | 1 | 1 | 15 | 8.89 | 1 | 15
TCWWTP | 1 | 1 | 19 | 8.77 | 1 | 19
TCWWTP | 1 | 1 | 29 | 8.39 | 1 | 29
TCWWTP | 1 | 1 | 35 | 8.57 | 1 | 35
TCWWTP | 1 | 1 | 34 | 7.95 | 1 | 34
TCWWTP | 1 | 1 | 36 | 7.69 | 1 | 36
TCWWTP | 1 | 1 | 23 | 9.35 | 1 | 23
TCWWTP | 1 | 1 | 24 | 8.18 | 1 | 24
TCWWTP | 1 | 1 | 39 | 7.02 | 1 | 39
TCWWTP | 1 | 1 | 42 | 7.72 | 1 | 42
TCWWTP | 1 | 1 | 41 | 8.17 | 1 | 41
TCWWTP | 1 | 1 | 25 | 8.17 | 1 | 25
TCWWTP | 1 | 1 | 36 | 8.28 | 1 | 36
TCWWTP | 1 | 1 | 34 | 8.16 | 1 | 34
TCWWTP | 1 | 1 | 40 | 7.97 | 1 | 40
TCWWTP | 1 | 1 | 32 | 8.14 | 1 | 32
TCWWTP | 1 | 1 | 28 | 7.21 | 1 | 28
TCWWTP | 1 | 1 | 33 | 7.14 | 1 | 33
TCWWTP | 1 | 1 | 27 | 7.16 | 1 | 27
TCWWTP | 1 | 1 | 18 | 9.38 | 1 | 18
HCNW | 1 | 0 | 54 | 37.7 | 6 | 324
HCNW | 1 | 0 | 58 | 19.7 | 6 | 348
HCNW | 1 | 0 | 54 | 29.2 | 6 | 324
HCNW | 1 | 0 | 51 | 41 | 6 | 306
HCNW | 1 | 0 | 51 | 42.2 | 6 | 306
HCNW | 1 | 0 | 44 | 46.2 | 6 | 264
HCNW | 1 | 0 | 38 | 54.9 | 6 | 228
HCNW | 1 | 0 | 34 | 55.2 | 6 | 204
HCNW | 1 | 0 | 43 | 51.4 | 6 | 258
HCNW | 1 | 0 | 55 | 38.2 | 6 | 330
HCNW | 1 | 0 | 60 | 18.8 | 6 | 360
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 43 | 49.5 | 6 | 258
HCNW | 1 | 0 | 35 | 56.8 | 6 | 210
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 32 | 60.8 | 6 | 192
HCNW | 1 | 0 | 47 | 46.9 | 6 | 282
HCNW | 1 | 0 | 44 | 48.8 | 6 | 264
HCNW | 1 | 0 | 34 | 57 | 6 | 204
HCNW | 1 | 0 | 53 | 40.3 | 6 | 318
HCNW | 1 | 0 | 51 | 40 | 6 | 306
HCNW | 1 | 0 | 56 | 35.6 | 6 | 336
HCNW | 1 | 0 | 53 | 37 | 6 | 318
HCNW | 1 | 0 | 54 | 36.3 | 6 | 324
HCNW | 1 | 0 | 54 | 37.2 | 6 | 324
HCNW | 1 | 0 | 50 | 41.5 | 6 | 300
HCNW | 1 | 0 | 47 | 44.3 | 6 | 282
HCNW | 1 | 0 | 42 | 48.1 | 6 | 252
HCNW | 1 | 0 | 52 | 40.3 | 6 | 312
HCNW | 1 | 0 | 59 | 31.8 | 6 | 354
HCNW | 1 | 0 | 57 | 34.4 | 6 | 342
HCNW | 1 | 0 | 62 | 28 | 6 | 372
HCNW | 1 | 0 | 51 | 40.8 | 6 | 306
HCNW | 1 | 0 | 51 | 39.1 | 6 | 306
HCNW | 1 | 0 | 49 | 37.9 | 6 | 294
HCNW | 1 | 0 | 49 | 41.7 | 6 | 294
HCNW | 1 | 0 | 53 | 38.2 | 6 | 318
HCNW | 1 | 0 | 62 | 29.9 | 6 | 372
HCNW | 1 | 0 | 65 | 25.6 | 6 | 390
HCNW | 1 | 0 | 62 | 29.7 | 6 | 372
HCNW | 1 | 0 | 35 | 52.5 | 6 | 210
HCNW | 1 | 0 | 58 | 33.4 | 6 | 348
HCNW | 1 | 0 | 32 | 57.3 | 6 | 192
HCNW | 1 | 0 | 27 | 64.4 | 6 | 162
HCNW | 1 | 0 | 52 | 38.9 | 6 | 312
HCNW | 1 | 0 | 26 | 64.4 | 6 | 156
HCNW | 1 | 0 | 41 | 50.9 | 6 | 246
HCNW | 1 | 0 | 31 | 60.4 | 6 | 186
HCNW | 1 | 0 | 37 | 53.2 | 6 | 222
HCNW | 1 | 0 | 34 | 55.7 | 6 | 204
HCNW | 1 | 0 | 38 | 52.8 | 6 | 228
HCNW | 1 | 0 | 42 | 47.4 | 6 | 252
HCNW | 1 | 0 | 38 | 51 | 6 | 228
HCNW | 1 | 0 | 41 | 51.8 | 6 | 246
HCNW | 1 | 0 | 43 | 47.8 | 6 | 258
HCNW | 1 | 0 | 42 | 47.7 | 6 | 252
HCNW | 1 | 0 | 49 | 43 | 6 | 294
HCNW | 1 | 0 | 40 | 50.6 | 6 | 240
HCNW | 1 | 0 | 35 | 57.8 | 6 | 210
HCNW | 1 | 0 | 33 | 59 | 6 | 198
HCNW | 1 | 0 | 31 | 57.6 | 6 | 186
HCNW | 1 | 0 | 36 | 56.4 | 6 | 216
HCNW | 1 | 0 | 35 | 49.6 | 6 | 210
HCNW | 1 | 0 | 36 | 55.3 | 6 | 216
HCNW | 1 | 0 | 37 | 51.4 | 6 | 222
HCNW | 1 | 0 | 33 | 58.2 | 6 | 198
HCNW | 1 | 0 | 42 | 46.7 | 6 | 252
HCNW | 1 | 0 | 43 | 46.5 | 6 | 258
HCNW | 1 | 0 | 44 | 45.8 | 6 | 264
HCNW | 1 | 0 | 46 | 41.6 | 6 | 276
HCNW | 1 | 0 | 47 | 42.5 | 6 | 282
HCNW | 1 | 0 | 49 | 42.1 | 6 | 294
HCNW | 1 | 0 | 44 | 44.6 | 6 | 264
HCNW | 1 | 0 | 36 | 57.5 | 6 | 216
HCNW | 1 | 0 | 46 | 47.3 | 6 | 276
HCNW | 1 | 0 | 30 | 60.2 | 6 | 180
HCNW | 1 | 0 | 27 | 62.5 | 6 | 162
HCNW | 1 | 0 | 33 | 60.7 | 6 | 198
HCNW | 1 | 0 | 33 | 51.9 | 6 | 198
HCNW | 1 | 0 | 43 | 49.3 | 6 | 258
HCNW | 1 | 0 | 39 | 53 | 6 | 234
HCNW | 1 | 0 | 38 | 54.2 | 6 | 228
HCNW | 1 | 0 | 35 | 57.5 | 6 | 210
HCNW | 1 | 0 | 32 | 48.1 | 6 | 192
HCNW | 1 | 0 | 30 | 61.2 | 6 | 180
HCNW | 1 | 0 | 49 | 43.2 | 6 | 294
HCNW | 1 | 0 | 33 | 53.8 | 6 | 198
COCCH | 1 | 1 | 43 | 10.92 | 1 | 43
COCCH | 1 | 1 | 75 | 5.69 | 1 | 75
COCCH | 1 | 1 | 65 | 6.05 | 1 | 65
COCCH | 1 | 1 | 66 | 6.18 | 1 | 66
COCCH | 1 | 1 | 70 | 5.47 | 1 | 70
COCCH | 1 | 1 | 48 | 9.79 | 1 | 48
COCCH | 1 | 1 | 56 | 8.88 | 1 | 56
COCCH | 1 | 1 | 54 | 8.39 | 1 | 54
COCCH | 1 | 1 | 69 | 5.75 | 1 | 69
COCCH | 1 | 1 | 49 | 9.58 | 1 | 49
COCCH | 1 | 1 | 68 | 6.16 | 1 | 68
COCCH | 1 | 1 | 49 | 9.53 | 1 | 49
COCCH | 1 | 1 | 51 | 8.89 | 1 | 51
COCCH | 1 | 1 | 54 | 8.04 | 1 | 54
COCCH | 1 | 1 | 78 | 4.5 | 1 | 78
COCCH | 1 | 1 | 74 | 4.48 | 1 | 74
COCCH | 1 | 1 | 81 | 4.91 | 1 | 81
COCCH | 1 | 1 | 69 | 5.99 | 1 | 69
COCCH | 1 | 1 | 54 | 8.46 | 1 | 54
COCCH | 1 | 1 | 79 | 4.88 | 1 | 79
COCCH | 1 | 1 | 66 | 6.86 | 1 | 66
COCCH | 1 | 1 | 76 | 4.95 | 1 | 76
COCCH | 1 | 1 | 70 | 5.14 | 1 | 70
COCCH | 1 | 1 | 73 | 5.66 | 1 | 73
COCCH | 1 | 1 | 69 | 6.21 | 1 | 69
COCCH | 1 | 1 | 78 | 5.17 | 1 | 78
COCCH | 1 | 1 | 62 | 6.84 | 1 | 62
COCCH | 1 | 1 | 66 | 6.01 | 1 | 66
COCCH | 1 | 1 | 72 | 5.01 | 1 | 72
COCCH | 1 | 1 | 76 | 4.63 | 1 | 76
COCCH | 1 | 1 | 58 | 7.58 | 1 | 58
COCCH | 1 | 1 | 78 | 4.44 | 1 | 78
COCCH | 1 | 1 | 80 | 3.54 | 1 | 80
COCCH | 1 | 1 | 81 | 4.31 | 1 | 81
COCCH | 1 | 1 | 76 | 5.27 | 1 | 76
COCCH | 1 | 1 | 69 | 6.46 | 1 | 69
COCCH | 1 | 1 | 73 | 5.58 | 1 | 73
COCCH | 1 | 1 | 67 | 6.66 | 1 | 67
COCCH | 1 | 1 | 61 | 7.24 | 1 | 61
COCCH | 1 | 1 | 57 | 7.56 | 1 | 57
COCCH | 1 | 1 | 58 | 8.15 | 1 | 58
COCCH | 1 | 1 | 63 | 7.36 | 1 | 63
COCCH | 1 | 1 | 65 | 7.53 | 1 | 65
COCCH | 1 | 1 | 50 | 9.31 | 1 | 50
COCCH | 1 | 1 | 60 | 6.8 | 1 | 60
COCCH | 1 | 1 | 56 | 8 | 1 | 56
COCCH | 1 | 1 | 62 | 7.56 | 1 | 62
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
COCCH | 1 | 1 | 67 | 5.7 | 1 | 67
COCCH | 1 | 1 | 64 | 8.62 | 1 | 64
COCCH | 1 | 1 | 63 | 6.87 | 1 | 63
COCCH | 1 | 1 | 54 | 9.34 | 1 | 54
COCCH | 1 | 1 | 60 | 7.48 | 1 | 60
COCCH | 1 | 1 | 57 | 7.16 | 1 | 57
COCCH | 1 | 1 | 52 | 8.28 | 1 | 52
COCCH | 1 | 1 | 51 | 8.97 | 1 | 51
COCCH | 1 | 1 | 54 | 8.45 | 1 | 54
COCCH | 1 | 1 | 68 | 6.43 | 1 | 68
COCCH | 1 | 1 | 65 | 6.33 | 1 | 65
Kid Kare | 1 | 1 | 41 | 20.69 | 1 | 41
Kid Kare | 1 | 1 | 78 | 7.5 | 1 | 78
Kid Kare | 1 | 1 | 72 | 9.59 | 1 | 72
Kid Kare | 1 | 1 | 68 | 10.17 | 1 | 68
Kid Kare | 1 | 1 | 62 | 11.27 | 1 | 62
Kid Kare | 1 | 1 | 68 | 11.04 | 1 | 68
Kid Kare | 1 | 1 | 43 | 22.64 | 1 | 43
Kid Kare | 1 | 1 | 39 | 20.69 | 1 | 39
Kid Kare | 1 | 1 | 38 | 23.26 | 1 | 38
Kid Kare | 1 | 1 | 35 | 23.28 | 1 | 35
Kid Kare | 1 | 1 | 32 | 18.46 | 1 | 32
Kid Kare | 1 | 1 | 33 | 22.23 | 1 | 33
Kid Kare | 1 | 1 | 63 | 12.61 | 1 | 63
Kid Kare | 1 | 1 | 44 | 19.43 | 1 | 44
Kid Kare | 1 | 1 | 47 | 20.43 | 1 | 47
Kid Kare | 1 | 1 | 51 | 9.5 | 1 | 51
Kid Kare | 1 | 1 | 51 | 9.48 | 1 | 51
Kid Kare | 1 | 1 | 54 | 12.26 | 1 | 54
Kid Kare | 1 | 1 | 56 | 13.89 | 1 | 56
Kid Kare | 1 | 1 | 58 | 11.35 | 1 | 58
Kid Kare | 1 | 1 | 59 | 12.26 | 1 | 59
Kid Kare | 1 | 1 | 62 | 12.26 | 1 | 62
Kid Kare | 1 | 1 | 60 | 11.11 | 1 | 60
Kid Kare | 1 | 1 | 33 | 23.26 | 1 | 33
Kid Kare | 1 | 1 | 62 | 10.31 | 1 | 62
Kid Kare | 1 | 1 | 73 | 9.86 | 1 | 73
Kid Kare | 1 | 1 | 69 | 10.03 | 1 | 69
Kid Kare | 1 | 1 | 68 | 11.18 | 1 | 68
Kid Kare | 1 | 1 | 65 | 11.66 | 1 | 65
Kid Kare | 1 | 1 | 61 | 12.61 | 1 | 61
Kid Kare | 1 | 1 | 59 | 13.78 | 1 | 59
Kid Kare | 1 | 1 | 59 | 13 | 1 | 59
Kid Kare | 1 | 1 | 58 | 13.64 | 1 | 58
Kid Kare | 1 | 1 | 61 | 14.85 | 1 | 61
Kid Kare | 1 | 1 | 77 | 8.39 | 1 | 77
Kid Kare | 1 | 1 | 58 | 15.53 | 1 | 58
Kid Kare | 1 | 1 | 76 | 8.35 | 1 | 76
Kid Kare | 1 | 1 | 48 | 17.38 | 1 | 48
Kid Kare | 1 | 1 | 55 | 14.8 | 1 | 55
Kid Kare | 1 | 1 | 66 | 10.44 | 1 | 66
Kid Kare | 1 | 1 | 66 | 11.75 | 1 | 66
Kid Kare | 1 | 1 | 62 | 12.5 | 1 | 62
Kid Kare | 1 | 1 | 58 | 13.38 | 1 | 58
Kid Kare | 1 | 1 | 52 | 15.88 | 1 | 52
Kid Kare | 1 | 1 | 55 | 11.67 | 1 | 55
Kid Kare | 1 | 1 | 60 | 13.04 | 1 | 60
Kid Kare | 1 | 1 | 64 | 11.97 | 1 | 64
Kid Kare | 1 | 1 | 58 | 22.14 | 1 | 58
Kid Kare | 1 | 1 | 71 | 9.59 | 1 | 71
Kid Kare | 1 | 1 | 64 | 12.42 | 1 | 64
Kid Kare | 1 | 1 | 70 | 10.52 | 1 | 70
Kid Kare | 1 | 1 | 70 | 9.76 | 1 | 70
Kid Kare | 1 | 1 | 65 | 16.86 | 1 | 65
Kid Kare | 1 | 1 | 67 | 10.61 | 1 | 67
Kid Kare | 1 | 1 | 51 | 13.92 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 71 | 8.72 | 1 | 71
Kid Kare | 1 | 1 | 74 | 9.73 | 1 | 74
Kid Kare | 1 | 1 | 63 | 10.92 | 1 | 63
Kid Kare | 1 | 1 | 71 | 9.94 | 1 | 71
Kid Kare | 1 | 1 | 64 | 10.92 | 1 | 64
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.29 | 1 | 72
Kid Kare | 1 | 1 | 72 | 9.14 | 1 | 72
Kid Kare | 1 | 1 | 74 | 9.34 | 1 | 74
Kid Kare | 1 | 1 | 76 | 8.73 | 1 | 76
Kid Kare | 1 | 1 | 73 | 8.9 | 1 | 73
Kid Kare | 1 | 1 | 71 | 9.34 | 1 | 71
Kid Kare | 1 | 1 | 67 | 10.52 | 1 | 67
Kid Kare | 1 | 1 | 68 | 10.35 | 1 | 68
Kid Kare | 1 | 1 | 67 | 12.09 | 1 | 67
Kid Kare | 1 | 1 | 71 | 9.45 | 1 | 71
Kid Kare | 1 | 1 | 51 | 15.23 | 1 | 51
Kid Kare | 1 | 1 | 62 | 17.43 | 1 | 62
Kid Kare | 1 | 1 | 53 | 14.35 | 1 | 53
Kid Kare | 1 | 1 | 49 | 16.25 | 1 | 49
Kid Kare | 1 | 1 | 49 | 14.87 | 1 | 49
Kid Kare | 1 | 1 | 65 | 12.06 | 1 | 65
Kid Kare | 1 | 1 | 51 | 16.27 | 1 | 51
Kid Kare | 1 | 1 | 65 | 11.38 | 1 | 65
Kid Kare | 1 | 1 | 57 | 13.23 | 1 | 57
Kid Kare | 1 | 1 | 52 | 17.6 | 1 | 52
Kid Kare | 1 | 1 | 42 | 17.22 | 1 | 42
Kid Kare | 1 | 1 | 47 | 16.86 | 1 | 47
Kid Kare | 1 | 1 | 62 | 11.99 | 1 | 62
Kid Kare | 1 | 1 | 50 | 13.25 | 1 | 50
Kid Kare | 1 | 1 | 54 | 14.51 | 1 | 54
Kid Kare | 1 | 1 | 55 | 15.2 | 1 | 55
Kid Kare | 1 | 1 | 58 | 14.01 | 1 | 58
Kid Kare | 1 | 1 | 54 | 14.42 | 1 | 54
Kid Kare | 1 | 1 | 53 | 17.53 | 1 | 53
Kid Kare | 1 | 1 | 53 | 15.06 | 1 | 53
Kid Kare | 1 | 1 | 54 | 14.11 | 1 | 54
Kid Kare | 1 | 1 | 54 | 15.27 | 1 | 54
Kid Kare | 1 | 1 | 52 | 15.61 | 1 | 52

## T1 Size2
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCFD | 2 | 1 | 66 | 10.42 | 1 | 66 | SUMMARY OUTPUT
COCFD | 2 | 1 | 48 | 18.38 | 1 | 48
COCFD | 2 | 1 | 70 | 8.26 | 1 | 70 | Regression Statistics
COCFD | 2 | 1 | 76 | 6.77 | 1 | 76 | Multiple R | 0.96247
COCFD | 2 | 1 | 61 | 12.87 | 1 | 61 | R Square | 0.92635
COCFD | 2 | 1 | 67 | 11.41 | 1 | 67 | Adjusted R Square | 0.92583
COCFD | 2 | 1 | 73 | 8.99 | 1 | 73 | Standard Error | 3.7553
COCFD | 2 | 1 | 69 | 10.32 | 1 | 69 | Observations | 282
COCFD | 2 | 1 | 76 | 8.3 | 1 | 76
COCFD | 2 | 1 | 81 | 6.57 | 1 | 81 | ANOVA
COCFD | 2 | 1 | 78 | 6.79 | 1 | 78 |  | df | SS | MS | F | Significance F
COCFD | 2 | 1 | 70 | 8.7 | 1 | 70 | Regression | 2 | 49489.4526 | 24744.7263 | 1754.6913 | 9.2784e-159
COCFD | 2 | 1 | 63 | 13.54 | 1 | 63 | Residual | 279 | 3934.469 | 14.102
COCFD | 2 | 1 | 73 | 8.71 | 1 | 73 | Total | 281 | 53423.9215
COCFD | 2 | 1 | 64 | 15.11 | 1 | 64
COCFD | 2 | 1 | 80 | 4.11 | 1 | 80 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCFD | 2 | 1 | 57 | 13.6 | 1 | 57 | Intercept | 5.8599 | 0.3374 | 17.368 | 2.6033e-46 | 5.1957 | 6.5241 | 5.1957 | 6.5241
COCFD | 2 | 1 | 58 | 12.83 | 1 | 58 | X Variable 1 | 13.1949 | 0.3888 | 33.9374 | 4.8565e-101 | 12.4295 | 13.9603 | 12.4295 | 13.9603
COCFD | 2 | 1 | 57 | 12.04 | 1 | 57 | X Variable 2 | -0.13339 | 0.0074641 | -17.8713 | 3.8622e-48 | -0.14809 | -0.1187 | -0.14809 | -0.1187
COCFD | 2 | 1 | 62 | 12.06 | 1 | 62
COCFD | 2 | 1 | 54 | 14.79 | 1 | 54
COCFD | 2 | 1 | 81 | 7.18 | 1 | 81
COCFD | 2 | 1 | 78 | 7.91 | 1 | 78
COCFD | 2 | 1 | 68 | 11.03 | 1 | 68
COCFD | 2 | 1 | 74 | 5.53 | 1 | 74
COCFD | 2 | 1 | 54 | 16.96 | 1 | 54
COCFD | 2 | 1 | 65 | 12.97 | 1 | 65
COCFD | 2 | 1 | 54 | 15.47 | 1 | 54
COCFD | 2 | 1 | 51 | 16.28 | 1 | 51
COCFD | 2 | 1 | 52 | 13.98 | 1 | 52
COCFD | 2 | 1 | 60 | 11.82 | 1 | 60
COCFD | 2 | 1 | 60 | 11.86 | 1 | 60
COCFD | 2 | 1 | 63 | 11.75 | 1 | 63
COCFD | 2 | 1 | 65 | 10.49 | 1 | 65
COCFD | 2 | 1 | 67 | 8.82 | 1 | 67
COCFD | 2 | 1 | 58 | 14.66 | 1 | 58
COCFD | 2 | 1 | 56 | 14.25 | 1 | 56
COCFD | 2 | 1 | 76 | 7.76 | 1 | 76
COCFD | 2 | 1 | 54 | 15.72 | 1 | 54
COCFD | 2 | 1 | 51 | 15.47 | 1 | 51
COCFD | 2 | 1 | 49 | 17.77 | 1 | 49
COCFD | 2 | 1 | 49 | 18.79 | 1 | 49
COCFD | 2 | 1 | 54 | 15.29 | 1 | 54
COCFD | 2 | 1 | 56 | 16.1 | 1 | 56
COCFD | 2 | 1 | 69 | 9.36 | 1 | 69
COCFD | 2 | 1 | 43 | 21.31 | 1 | 43
COCFD | 2 | 1 | 50 | 17.61 | 1 | 50
COCFD | 2 | 1 | 65 | 10.46 | 1 | 65
COCFD | 2 | 1 | 69 | 9.64 | 1 | 69
COCFD | 2 | 1 | 78 | 7.01 | 1 | 78
COCFD | 2 | 1 | 79 | 6.39 | 1 | 79
COCFD | 2 | 1 | 75 | 8.71 | 1 | 75
COCFD | 2 | 1 | 72 | 7.5 | 1 | 72
COCFD | 2 | 1 | 66 | 9.42 | 1 | 66
COCFD | 2 | 1 | 62 | 11.73 | 1 | 62
COCFD | 2 | 1 | 66 | 11.12 | 1 | 66
COCFD | 2 | 1 | 69 | 9.71 | 1 | 69
COCFD | 2 | 1 | 68 | 9.53 | 1 | 68
COCFD | 2 | 1 | 65 | 9.72 | 1 | 65
KE ECAM | 2 | 1 | 68 | 16.93 | 1 | 68
KE ECAM | 2 | 1 | 66 | 12.05 | 1 | 66
KE ECAM | 2 | 1 | 65 | 12.97 | 1 | 65
KE ECAM | 2 | 1 | 70 | 10.35 | 1 | 70
KE ECAM | 2 | 1 | 74 | 8.51 | 1 | 74
KE ECAM | 2 | 1 | 71 | 11.1 | 1 | 71
KE ECAM | 2 | 1 | 66 | 11.65 | 1 | 66
KE ECAM | 2 | 1 | 72 | 12.36 | 1 | 72
KE ECAM | 2 | 1 | 69 | 10.35 | 1 | 69
KE ECAM | 2 | 1 | 69 | 10.5 | 1 | 69
KE ECAM | 2 | 1 | 72 | 10.37 | 1 | 72
KE ECAM | 2 | 1 | 72 | 11.15 | 1 | 72
KE ECAM | 2 | 1 | 75 | 10.83 | 1 | 75
KE ECAM | 2 | 1 | 78 | 7.17 | 1 | 78
KE ECAM | 2 | 1 | 73 | 12.69 | 1 | 73
KE ECAM | 2 | 1 | 66 | 14.54 | 1 | 66
KE ECAM | 2 | 1 | 63 | 12.58 | 1 | 63
KE ECAM | 2 | 1 | 59 | 13.99 | 1 | 59
KE ECAM | 2 | 1 | 60 | 13.88 | 1 | 60
KE ECAM | 2 | 1 | 65 | 13.56 | 1 | 65
KE ECAM | 2 | 1 | 59 | 14.75 | 1 | 59
KE ECAM | 2 | 1 | 60 | 15.37 | 1 | 60
KE ECAM | 2 | 1 | 50 | 20.37 | 1 | 50
KE ECAM | 2 | 1 | 81 | 7.73 | 1 | 81
KE ECAM | 2 | 1 | 71 | 16.36 | 1 | 71
KE ECAM | 2 | 1 | 70 | 11.17 | 1 | 70
KE ECAM | 2 | 1 | 54 | 14.73 | 1 | 54
KE ECAM | 2 | 1 | 79 | 10.78 | 1 | 79
COCTV | 2 | 1 | 79 | 6.47 | 1 | 79
COCTV | 2 | 1 | 66 | 8.82 | 1 | 66
COCTV | 2 | 1 | 75 | 6.72 | 1 | 75
COCTV | 2 | 1 | 69 | 7.28 | 1 | 69
COCTV | 2 | 1 | 65 | 7.09 | 1 | 65
COCTV | 2 | 1 | 70 | 6.24 | 1 | 70
COCTV | 2 | 1 | 66 | 8.71 | 1 | 66
COCTV | 2 | 1 | 62 | 8.78 | 1 | 62
COCTV | 2 | 1 | 69 | 7.62 | 1 | 69
COCTV | 2 | 1 | 68 | 7.36 | 1 | 68
COCTV | 2 | 1 | 73 | 7.39 | 1 | 73
COCTV | 2 | 1 | 66 | 8.88 | 1 | 66
COCTV | 2 | 1 | 76 | 5.31 | 1 | 76
COCTV | 2 | 1 | 73 | 6.52 | 1 | 73
COCTV | 2 | 1 | 78 | 6.54 | 1 | 78
COCTV | 2 | 1 | 81 | 6.89 | 1 | 81
COCTV | 2 | 1 | 74 | 5.81 | 1 | 74
COCTV | 2 | 1 | 61 | 7.77 | 1 | 61
COCTV | 2 | 1 | 76 | 6.11 | 1 | 76
COCTV | 2 | 1 | 63 | 8.66 | 1 | 63
COCTV | 2 | 1 | 72 | 5.25 | 1 | 72
COCTV | 2 | 1 | 69 | 7.89 | 1 | 69
COCTV | 2 | 1 | 64 | 9.89 | 1 | 64
COCTV | 2 | 1 | 70 | 7.76 | 1 | 70
COCTV | 2 | 1 | 58 | 10.48 | 1 | 58
COCTV | 2 | 1 | 57 | 10.26 | 1 | 57
COCTV | 2 | 1 | 67 | 7.51 | 1 | 67
COCTV | 2 | 1 | 78 | 4.96 | 1 | 78
COCTV | 2 | 1 | 78 | 4.93 | 1 | 78
COCTV | 2 | 1 | 76 | 5.97 | 1 | 76
COCTV | 2 | 1 | 81 | 4.98 | 1 | 81
COCTV | 2 | 1 | 80 | 4.56 | 1 | 80
TCWP | 2 | 1 | 45 | 10.17 | 1 | 45
TCWP | 2 | 1 | 35 | 10.82 | 1 | 35
TCWP | 2 | 1 | 37 | 10.57 | 1 | 37
TCWP | 2 | 1 | 37 | 10.64 | 1 | 37
TCWP | 2 | 1 | 31 | 10.96 | 1 | 31
TCWP | 2 | 1 | 31 | 11.14 | 1 | 31
TCWP | 2 | 1 | 33 | 10.77 | 1 | 33
TCWP | 2 | 1 | 44 | 10.73 | 1 | 44
TCWP | 2 | 1 | 28 | 11.01 | 1 | 28
TCWP | 2 | 1 | 34 | 10.58 | 1 | 34
TCWP | 2 | 1 | 33 | 10.71 | 1 | 33
TCWP | 2 | 1 | 38 | 10.75 | 1 | 38
TCWP | 2 | 1 | 37 | 10.92 | 1 | 37
TCWP | 2 | 1 | 30 | 10.54 | 1 | 30
TCWP | 2 | 1 | 32 | 9.94 | 1 | 32
TCWP | 2 | 1 | 37 | 10.42 | 1 | 37
TCWP | 2 | 1 | 34 | 10.4 | 1 | 34
TCWP | 2 | 1 | 50 | 10.27 | 1 | 50
TCWP | 2 | 1 | 29 | 10.54 | 1 | 29
TCWP | 2 | 1 | 51 | 9.15 | 1 | 51
TCWP | 2 | 1 | 35 | 9.89 | 1 | 35
TCWP | 2 | 1 | 33 | 10.34 | 1 | 33
TCWP | 2 | 1 | 40 | 9.99 | 1 | 40
TCWP | 2 | 1 | 34 | 10.71 | 1 | 34
TCWP | 2 | 1 | 34 | 9.68 | 1 | 34
TCWP | 2 | 1 | 50 | 10.4 | 1 | 50
TCWP | 2 | 1 | 29 | 10.73 | 1 | 29
TCWP | 2 | 1 | 44 | 10.78 | 1 | 44
TCWP | 2 | 1 | 41 | 10.68 | 1 | 41
TCWP | 2 | 1 | 39 | 10.71 | 1 | 39
TCWP | 2 | 1 | 35 | 10.66 | 1 | 35
TCWP | 2 | 1 | 32 | 10.73 | 1 | 32
TCWP | 2 | 1 | 39 | 10.46 | 1 | 39
TCWP | 2 | 1 | 43 | 10.08 | 1 | 43
TCWP | 2 | 1 | 35 | 10.91 | 1 | 35
TCWP | 2 | 1 | 32 | 10.45 | 1 | 32
TCWP | 2 | 1 | 32 | 10.51 | 1 | 32
TCWP | 2 | 1 | 30 | 10.78 | 1 | 30
TCWP | 2 | 1 | 40 | 10.71 | 1 | 40
TCWP | 2 | 1 | 29 | 11.05 | 1 | 29
PCDC | 2 | 0 | 56 | 35.7 | 6 | 336
PCDC | 2 | 0 | 35 | 54.4 | 6 | 210
PCDC | 2 | 0 | 49 | 48 | 6 | 294
PCDC | 2 | 0 | 57 | 38.7 | 6 | 342
PCDC | 2 | 0 | 56 | 37.5 | 6 | 336
PCDC | 2 | 0 | 59 | 34.8 | 6 | 354
PCDC | 2 | 0 | 54 | 32.1 | 6 | 324
PCDC | 2 | 0 | 44 | 39.4 | 6 | 264
PCDC | 2 | 0 | 55 | 30.4 | 6 | 330
PCDC | 2 | 0 | 46 | 53.7 | 6 | 276
PCDC | 2 | 0 | 56 | 27.3 | 6 | 336
PCDC | 2 | 0 | 59 | 25.6 | 6 | 354
PCDC | 2 | 0 | 48 | 49 | 6 | 288
PCDC | 2 | 0 | 34 | 63 | 6 | 204
PCDC | 2 | 0 | 51 | 43.2 | 6 | 306
PCDC | 2 | 0 | 44 | 52.7 | 6 | 264
PCDC | 2 | 0 | 57 | 39.8 | 6 | 342
PCDC | 2 | 0 | 42 | 52.7 | 6 | 252
PCDC | 2 | 0 | 49 | 47.7 | 6 | 294
PCDC | 2 | 0 | 58 | 35.4 | 6 | 348
PCDC | 2 | 0 | 59 | 34.3 | 6 | 354
PCDC | 2 | 0 | 59 | 36.2 | 6 | 354
PCDC | 2 | 0 | 63 | 30.7 | 6 | 378
PCDC | 2 | 0 | 62 | 33.8 | 6 | 372
PCDC | 2 | 0 | 60 | 36.5 | 6 | 360
PCDC | 2 | 0 | 38 | 59.1 | 6 | 228
PCDC | 2 | 0 | 38 | 58.9 | 6 | 228
PCDC | 2 | 0 | 37 | 48.4 | 6 | 222
PCDC | 2 | 0 | 48 | 49.1 | 6 | 288
PCDC | 2 | 0 | 44 | 44.4 | 6 | 264
PCDC | 2 | 0 | 34 | 62.4 | 6 | 204
PCDC | 2 | 0 | 45 | 42.2 | 6 | 270
PCDC | 2 | 0 | 57 | 37.1 | 6 | 342
PCDC | 2 | 0 | 64 | 31.3 | 6 | 384
PCDC | 2 | 0 | 57 | 35.6 | 6 | 342
PCDC | 2 | 0 | 44 | 51.3 | 6 | 264
PCDC | 2 | 0 | 31 | 72 | 6 | 186
PCDC | 2 | 0 | 48 | 51.3 | 6 | 288
PCDC | 2 | 0 | 46 | 50.6 | 6 | 276
PCDC | 2 | 0 | 43 | 51 | 6 | 258
PCDC | 2 | 0 | 45 | 50.5 | 6 | 270
PCDC | 2 | 0 | 40 | 59.6 | 6 | 240
PCDC | 2 | 0 | 58 | 36.2 | 6 | 348
PCDC | 2 | 0 | 41 | 57.7 | 6 | 246
PCDC | 2 | 0 | 61 | 33.8 | 6 | 366
PCDC | 2 | 0 | 43 | 53.6 | 6 | 258
PCDC | 2 | 0 | 48 | 48.5 | 6 | 288
PCDC | 2 | 0 | 43 | 45.5 | 6 | 258
PCDC | 2 | 0 | 54 | 39.6 | 6 | 324
PCDC | 2 | 0 | 61 | 32.2 | 6 | 366
PCDC | 2 | 0 | 57 | 37 | 6 | 342
COMW | 2 | 1 | 36 | 18.4 | 1 | 36
COMW | 2 | 1 | 45 | 16.9 | 1 | 45
COMW | 2 | 1 | 52 | 15.3 | 1 | 52
COMW | 2 | 1 | 53 | 15.9 | 1 | 53
COMW | 2 | 1 | 53 | 14.2 | 1 | 53
COMW | 2 | 1 | 50 | 15.1 | 1 | 50
COMW | 2 | 1 | 43 | 15.3 | 1 | 43
COMW | 2 | 1 | 29 | 16.9 | 1 | 29
COMW | 2 | 1 | 40 | 14 | 1 | 40
COMW | 2 | 1 | 44 | 15.6 | 1 | 44
COMW | 2 | 1 | 35 | 16.9 | 1 | 35
COMW | 2 | 1 | 37 | 18.1 | 1 | 37
COMW | 2 | 1 | 32 | 15.8 | 1 | 32
COMW | 2 | 1 | 31 | 16.9 | 1 | 31
COMW | 2 | 1 | 32 | 17.1 | 1 | 32
COMW | 2 | 1 | 35 | 16.6 | 1 | 35
COMW | 2 | 1 | 40 | 16.6 | 1 | 40
COMW | 2 | 1 | 43 | 15.2 | 1 | 43
COMW | 2 | 1 | 43 | 16.2 | 1 | 43
COMW | 2 | 1 | 42 | 14.7 | 1 | 42
COMW | 2 | 1 | 46 | 16.3 | 1 | 46
COMW | 2 | 1 | 34 | 16.5 | 1 | 34
COMKR | 2 | 1 | 40 | 10.9 | 1 | 40
COMKR | 2 | 1 | 43 | 11.1 | 1 | 43
COMKR | 2 | 1 | 50 | 8.7 | 1 | 50
COMKR | 2 | 1 | 53 | 9.3 | 1 | 53
COMKR | 2 | 1 | 53 | 10.8 | 1 | 53
COMKR | 2 | 1 | 52 | 10.6 | 1 | 52
COMKR | 2 | 1 | 35 | 11.9 | 1 | 35
COMKR | 2 | 1 | 36 | 12.5 | 1 | 36
COMKR | 2 | 1 | 32 | 12.8 | 1 | 32
COMKR | 2 | 1 | 45 | 12.7 | 1 | 45
COMKR | 2 | 1 | 29 | 12.8 | 1 | 29
COMKR | 2 | 1 | 34 | 12.3 | 1 | 34
COMKR | 2 | 1 | 46 | 11.8 | 1 | 46
COMKR | 2 | 1 | 37 | 11.4 | 1 | 37
COMKR | 2 | 1 | 32 | 14.7 | 1 | 32
COMKR | 2 | 1 | 31 | 13.4 | 1 | 31
COMKR | 2 | 1 | 35 | 12.9 | 1 | 35
COMKR | 2 | 1 | 43 | 10.6 | 1 | 43
COMKR | 2 | 1 | 43 | 11.7 | 1 | 43
COMKR | 2 | 1 | 42 | 11.2 | 1 | 42
COMKR | 2 | 1 | 44 | 10.1 | 1 | 44
COMKR | 2 | 1 | 40 | 13.5 | 1 | 40
BLDG210 | 2 | 0 | 66 | 22.72 | 3 | 198
BLDG210 | 2 | 0 | 68 | 22.83 | 3 | 204
BLDG210 | 2 | 0 | 63 | 25.24 | 3 | 189
BLDG210 | 2 | 0 | 68 | 24.21 | 3 | 204
BLDG210 | 2 | 0 | 70 | 21.78 | 3 | 210
BLDG210 | 2 | 0 | 61 | 26.47 | 3 | 183
BLDG210 | 2 | 0 | 64 | 25.63 | 3 | 192
BLDG210 | 2 | 0 | 66 | 24.01 | 3 | 198
BLDG210 | 2 | 0 | 74 | 25.43 | 3 | 222
BLDG210 | 2 | 0 | 67 | 22.81 | 3 | 201
BLDG210 | 2 | 0 | 77 | 14.89 | 3 | 231
BLDG210 | 2 | 0 | 59 | 26.25 | 3 | 177
BLDG210 | 2 | 0 | 60 | 22.05 | 3 | 180
BLDG210 | 2 | 0 | 69 | 21.65 | 3 | 207
BLDG210 | 2 | 0 | 80 | 16.75 | 3 | 240
BLDG210 | 2 | 0 | 77 | 19.08 | 3 | 231
BLDG210 | 2 | 0 | 72 | 20.72 | 3 | 216
BLDG210 | 2 | 0 | 63 | 27.04 | 3 | 189
BLDG210 | 2 | 0 | 70 | 22.17 | 3 | 210
BLDG210 | 2 | 0 | 60 | 28.55 | 3 | 180
BLDG210 | 2 | 0 | 63 | 27.9 | 3 | 189
BLDG210 | 2 | 0 | 55 | 31.26 | 3 | 165
BLDG210 | 2 | 0 | 53 | 32.4 | 3 | 159
BLDG210 | 2 | 0 | 48 | 33.31 | 3 | 144
BLDG210 | 2 | 0 | 72 | 17.54 | 3 | 216
BLDG210 | 2 | 0 | 53 | 25.38 | 3 | 159
BLDG210 | 2 | 0 | 64 | 25.29 | 3 | 192
BLDG210 | 2 | 0 | 65 | 24.17 | 3 | 195

## T1 Size3
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
COCWWTP | 3 | 0 | 81 | 32.05 | 6 | 486 | SUMMARY OUTPUT
COCWWTP | 3 | 0 | 78 | 31.93 | 6 | 468
COCWWTP | 3 | 0 | 79 | 29.67 | 6 | 474 | Regression Statistics
COCWWTP | 3 | 0 | 76 | 28.4 | 6 | 456 | Multiple R | 0.96003
COCWWTP | 3 | 0 | 76 | 30.83 | 6 | 456 | R Square | 0.92165
COCWWTP | 3 | 0 | 62 | 40.46 | 6 | 372 | Adjusted R Square | 0.92025
COCWWTP | 3 | 0 | 54 | 44.24 | 6 | 324 | Standard Error | 3.8637
COCWWTP | 3 | 0 | 67 | 34.75 | 6 | 402 | Observations | 115
COCWWTP | 3 | 0 | 69 | 38.29 | 6 | 414
COCWWTP | 3 | 0 | 68 | 35.65 | 6 | 408 | ANOVA
COCWWTP | 3 | 0 | 65 | 44.66 | 6 | 390 |  | df | SS | MS | F | Significance F
COCWWTP | 3 | 0 | 54 | 55.77 | 6 | 324 | Regression | 2 | 19668.2901 | 9834.145 | 658.7702 | 1.162e-62
COCWWTP | 3 | 0 | 51 | 55.72 | 6 | 306 | Residual | 112 | 1671.9401 | 14.928
COCWWTP | 3 | 0 | 52 | 52.55 | 6 | 312 | Total | 114 | 21340.2302
COCWWTP | 3 | 0 | 60 | 46.88 | 6 | 360
COCWWTP | 3 | 0 | 60 | 42.96 | 6 | 360 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
COCWWTP | 3 | 0 | 50 | 60.42 | 6 | 300 | Intercept | 10.2591 | 0.80485 | 12.7465 | 1.5412e-23 | 8.6643 | 11.8538 | 8.6643 | 11.8538
COCWWTP | 3 | 0 | 65 | 38.29 | 6 | 390 | X Variable 1 | 16.6877 | 0.56831 | 29.3639 | 1.9647e-54 | 15.5616 | 17.8137 | 15.5616 | 17.8137
COCWWTP | 3 | 0 | 64 | 47.7 | 6 | 384 | X Variable 2 | -0.17943 | 0.008452 | -21.2292 | 4.6265e-41 | -0.19618 | -0.16268 | -0.19618 | -0.16268
COCWWTP | 3 | 0 | 65 | 38.9 | 6 | 390
COCWWTP | 3 | 0 | 56 | 50.26 | 6 | 336
COCWWTP | 3 | 0 | 54 | 51.97 | 6 | 324
COCWWTP | 3 | 0 | 54 | 49.76 | 6 | 324
COCWWTP | 3 | 0 | 49 | 61.9 | 6 | 294
COCWWTP | 3 | 0 | 54 | 52.64 | 6 | 324
COCWWTP | 3 | 0 | 56 | 52.56 | 6 | 336
COCWWTP | 3 | 0 | 48 | 60.48 | 6 | 288
COCWWTP | 3 | 0 | 43 | 66.12 | 6 | 258
COCWWTP | 3 | 0 | 63 | 43.44 | 6 | 378
COCWWTP | 3 | 0 | 70 | 35.71 | 6 | 420
COCWWTP | 3 | 0 | 62 | 43.08 | 6 | 372
COCWWTP | 3 | 0 | 78 | 25.51 | 6 | 468
COCWWTP | 3 | 0 | 68 | 35.74 | 6 | 408
COCWWTP | 3 | 0 | 66 | 41.92 | 6 | 396
COCWWTP | 3 | 0 | 66 | 37.87 | 6 | 396
COCWWTP | 3 | 0 | 72 | 30.53 | 6 | 432
COCWWTP | 3 | 0 | 69 | 32.6 | 6 | 414
COCWWTP | 3 | 0 | 75 | 32.73 | 6 | 450
COCWWTP | 3 | 0 | 69 | 37.08 | 6 | 414
COCWWTP | 3 | 0 | 66 | 39.5 | 6 | 396
COCWWTP | 3 | 0 | 51 | 55.2 | 6 | 306
COCWWTP | 3 | 0 | 78 | 26.82 | 6 | 468
COCWWTP | 3 | 0 | 81 | 26.05 | 6 | 486
COCWWTP | 3 | 0 | 76 | 27.53 | 6 | 456
COCWWTP | 3 | 0 | 69 | 35.64 | 6 | 414
COCWWTP | 3 | 0 | 73 | 30.06 | 6 | 438
COCWWTP | 3 | 0 | 67 | 36.65 | 6 | 402
COCWWTP | 3 | 0 | 61 | 44.7 | 6 | 366
COCWWTP | 3 | 0 | 58 | 48.21 | 6 | 348
COCWWTP | 3 | 0 | 63 | 44.13 | 6 | 378
COCWWTP | 3 | 0 | 65 | 36.59 | 6 | 390
COCWWTP | 3 | 0 | 58 | 33.82 | 6 | 348
COCWWTP | 3 | 0 | 57 | 40.95 | 6 | 342
COCWWTP | 3 | 0 | 80 | 16.14 | 6 | 480
COCWWTP | 3 | 0 | 70 | 33.86 | 6 | 420
COCWWTP | 3 | 0 | 73 | 25.06 | 6 | 438
COCWWTP | 3 | 0 | 74 | 29.67 | 6 | 444
COCWWTP | 3 | 0 | 57 | 45.79 | 6 | 342
COCWWTP | 3 | 0 | 49 | 57.41 | 6 | 294
BayView | 3 | 1 | 80 | 8.74 | 1.5 | 120
BayView | 3 | 1 | 68 | 12.23 | 1.5 | 102
BayView | 3 | 1 | 60 | 14.08 | 1.5 | 90
BayView | 3 | 1 | 65 | 15.18 | 1.5 | 97.5
BayView | 3 | 1 | 66 | 15.69 | 1.5 | 99
BayView | 3 | 1 | 64 | 15.84 | 1.5 | 96
BayView | 3 | 1 | 61 | 16.67 | 1.5 | 91.5
BayView | 3 | 1 | 70 | 15.07 | 1.5 | 105
BayView | 3 | 1 | 72 | 13.24 | 1.5 | 108
BayView | 3 | 1 | 63 | 15.04 | 1.5 | 94.5
BayView | 3 | 1 | 68 | 14.34 | 1.5 | 102
BayView | 3 | 1 | 66 | 14.26 | 1.5 | 99
BayView | 3 | 1 | 67 | 15.14 | 1.5 | 100.5
BayView | 3 | 1 | 69 | 13.98 | 1.5 | 103.5
BayView | 3 | 1 | 63 | 16.05 | 1.5 | 94.5
BayView | 3 | 1 | 74 | 11.75 | 1.5 | 111
BayView | 3 | 1 | 48 | 21.14 | 1.5 | 72
BayView | 3 | 1 | 77 | 11.9 | 1.5 | 115.5
BayView | 3 | 1 | 55 | 18.48 | 1.5 | 82.5
BayView | 3 | 1 | 53 | 18.99 | 1.5 | 79.5
BayView | 3 | 1 | 59 | 16.45 | 1.5 | 88.5
BayView | 3 | 1 | 60 | 15.65 | 1.5 | 90
BayView | 3 | 1 | 64 | 14.88 | 1.5 | 96
BayView | 3 | 1 | 70 | 14.07 | 1.5 | 105
BayView | 3 | 1 | 63 | 15.02 | 1.5 | 94.5
BayView | 3 | 1 | 72 | 13.41 | 1.5 | 108
BayView | 3 | 1 | 77 | 12.35 | 1.5 | 115.5
BayView | 3 | 1 | 53 | 18.37 | 1.5 | 79.5
BNS GEN | 3 | 1 | 68 | 19.59 | 2.5 | 170
BNS GEN | 3 | 1 | 77 | 18.89 | 2.5 | 192.5
BNS GEN | 3 | 1 | 74 | 18.44 | 2.5 | 185
BNS GEN | 3 | 1 | 80 | 13.56 | 2.5 | 200
BNS GEN | 3 | 1 | 60 | 24.43 | 2.5 | 150
BNS GEN | 3 | 1 | 65 | 25.28 | 2.5 | 162.5
BNS GEN | 3 | 1 | 66 | 27.62 | 2.5 | 165
BNS GEN | 3 | 1 | 64 | 26.73 | 2.5 | 160
BNS GEN | 3 | 1 | 61 | 28.58 | 2.5 | 152.5
BNS GEN | 3 | 1 | 70 | 24.45 | 2.5 | 175
BNS GEN | 3 | 1 | 72 | 23.16 | 2.5 | 180
BNS GEN | 3 | 1 | 63 | 25.76 | 2.5 | 157.5
BNS GEN | 3 | 1 | 68 | 25.53 | 2.5 | 170
BNS GEN | 3 | 1 | 66 | 26.12 | 2.5 | 165
BNS GEN | 3 | 1 | 63 | 30.02 | 2.5 | 157.5
BNS GEN | 3 | 1 | 67 | 24.42 | 2.5 | 167.5
BNS GEN | 3 | 1 | 77 | 20.16 | 2.5 | 192.5
BNS GEN | 3 | 1 | 70 | 24.19 | 2.5 | 175
BNS GEN | 3 | 1 | 64 | 27.54 | 2.5 | 160
BNS GEN | 3 | 1 | 59 | 30.4 | 2.5 | 147.5
BNS GEN | 3 | 1 | 63 | 28.78 | 2.5 | 157.5
BNS GEN | 3 | 1 | 55 | 35 | 2.5 | 137.5
BNS GEN | 3 | 1 | 53 | 36.17 | 2.5 | 132.5
BNS GEN | 3 | 1 | 48 | 40.62 | 2.5 | 120
BNS GEN | 3 | 1 | 53 | 36.65 | 2.5 | 132.5
BNS GEN | 3 | 1 | 69 | 22.37 | 2.5 | 172.5
BNS GEN | 3 | 1 | 72 | 23.45 | 2.5 | 180
BNS GEN | 3 | 1 | 60 | 28.74 | 2.5 | 150

## T1 Size4
Site | Size Category | Flat Baseline | Avg OA Temp | Avg KWh Total | New Rated Heater Size kW | Heater Size X Temp
NQ | 4 | 1 | 66 | 68.56 | 10 | 660 | SUMMARY OUTPUT
NQ | 4 | 1 | 45 | 109.25 | 10 | 450
NQ | 4 | 1 | 45 | 112.09 | 10 | 450 | Regression Statistics
NQ | 4 | 1 | 58 | 80.08 | 10 | 580 | Multiple R | 0.94496
NQ | 4 | 1 | 51 | 100.12 | 10 | 510 | R Square | 0.89295
NQ | 4 | 1 | 56 | 81.13 | 10 | 560 | Adjusted R Square | 0.88716
NQ | 4 | 1 | 47 | 108.9 | 10 | 470 | Standard Error | 6.7103
NQ | 4 | 1 | 48 | 103.73 | 10 | 480 | Observations | 40
NQ | 4 | 1 | 52 | 90.78 | 10 | 520
NQ | 4 | 1 | 53 | 91.16 | 10 | 530 | ANOVA
NQ | 4 | 1 | 55 | 91.45 | 10 | 550 |  | df | SS | MS | F | Significance F
NQ | 4 | 1 | 43 | 128.86 | 10 | 430 | Regression | 2 | 13896.9214 | 6948.4607 | 154.3119 | 1.1157e-18
NQ | 4 | 1 | 49 | 103.44 | 10 | 490 | Residual | 37 | 1666.0608 | 45.0287
NQ | 4 | 1 | 52 | 87.74 | 10 | 520 | Total | 39 | 15562.9822
NQ | 4 | 1 | 60 | 70.99 | 10 | 600
NQ | 4 | 1 | 46 | 107.2 | 10 | 460 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
NQ | 4 | 1 | 33 | 135.86 | 10 | 330 | Intercept | 229.5194 | 6.8715 | 33.4016 | 3.1035e-29 | 215.5964 | 243.4424 | 215.5964 | 243.4424
NQ | 4 | 1 | 53 | 93.8 | 10 | 530 | X Variable 1 | 0 | 0 | 65535 | #NUM! | 0 | 0 | 0 | 0
NQ | 4 | 1 | 52 | 93.36 | 10 | 520 | X Variable 2 | -0.25769 | 0.014671 | -17.5644 | #NUM! | -0.28742 | -0.22797 | -0.28742 | -0.22797
NQ | 4 | 1 | 55 | 78.49 | 10 | 550
NQ | 4 | 1 | 43 | 124.67 | 10 | 430
NQ | 4 | 1 | 49 | 102.32 | 10 | 490 | SUMMARY OUTPUT
NQ | 4 | 1 | 41 | 132.18 | 10 | 410
NQ | 4 | 1 | 46 | 125.94 | 10 | 460 | Regression Statistics
NQ | 4 | 1 | 40 | 138.28 | 10 | 400 | Multiple R | 0.94478
NQ | 4 | 1 | 36 | 132.52 | 10 | 360 | R Square | 0.89262
NQ | 4 | 1 | 37 | 142.15 | 10 | 370 | Adjusted R Square | 0.88979
NQ | 4 | 1 | 37 | 124.63 | 10 | 370 | Standard Error | 6.6317
NQ | 4 | 1 | 39 | 123 | 10 | 390 | Observations | 40
NQ | 4 | 1 | 46 | 107.66 | 10 | 460
NQ | 4 | 1 | 47 | 105.97 | 10 | 470 | ANOVA
NQ | 4 | 1 | 37 | 140.25 | 10 | 370 |  | df | SS | MS | F | Significance F
NQ | 4 | 1 | 44 | 124.86 | 10 | 440 | Regression | 1 | 13891.7706 | 13891.7706 | 315.871 | 5.2529e-20
NQ | 4 | 1 | 39 | 132.78 | 10 | 390 | Residual | 38 | 1671.2116 | 43.9793
NQ | 4 | 1 | 37 | 129.63 | 10 | 370 | Total | 39 | 15562.9822
NQ | 4 | 1 | 41 | 121.86 | 10 | 410
NQ | 4 | 1 | 44 | 109.08 | 10 | 440 |  | Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
NQ | 4 | 1 | 44 | 116.95 | 10 | 440 | Intercept | 229.5194 | 6.791 | 33.7977 | 5.8085e-30 | 215.7718 | 243.267 | 215.7718 | 243.267
NQ | 4 | 1 | 44 | 126.81 | 10 | 440 | X Variable 1 | -2.5769 | 0.14499 | -17.7728 | 5.2529e-20 | -2.8704 | -2.2834 | -2.8704 | -2.2834
NQ | 4 | 1 | 41 | 112.37 | 10 | 410