## Summary_Scaling_EPr&ESe&CZ
Building Type | CZ09 |  | CZ08
| kWh savings/ton |  | kWh savings/ton
| AC | HP | AC | HP
ERC | 60.3691 | 68.7747 | 65.1436 | 72.4644
ESe | 62.7425 | 65.8856 | 68.5314 | 71.3396
EPr | 55.3252 | 76.5742 | 59.1498 | 72.9524
Coefficient of Variation | 6.369% | 7.853% | 7.391% | 1.145%
AC-68775 (AC) | CZ09 |  |  |  | CZ8 |  |  |  | Average |  |  |  | % variation between CZs
| GMC($)/ton |  | IMC($)/ton |  | GMC($)/ton |  | IMC($)/ton |  | GMC($)/ton |  | IMC($)/ton
| Material | Labor | Material | Labor | Material | Labor | Material | Labor | Material | Labor | Material | Labor
ERC | 75 | 33 | 39 | 0 | 79 | 35 | 41 | 0 | 77 | 34 | 40 | 0 | -5.333% | -6.061%
ESe | 45 | 20 | 23 | 0 | 54 | 24 | 28 | 0 | 49.5 | 22 | 25.5 | 0 | -20% | -20%
EPr | 41 | 18 | 21 | 0 | 42 | 19 | 22 | 0 | 41.5 | 18.5 | 21.5 | 0 | -2.439% | -5.556%
AC-72229 (HP) | CZ09 |  |  |  | CZ8 |  |  |  | Average |  |  |  | % variation between CZs
| GMC($)/ton |  | IMC($)/ton |  | GMC($)/ton |  | IMC($)/ton |  | GMC($)/ton |  | IMC($)/ton
| Material | Labor | Material | Labor | Material | Labor | Material | Labor | Material | Labor | Material | Labor
ERC | 76.77 | 34.32 | 39.6 | 0 | 81.07 | 36.24 | 41.81 | 0 | 78.92 | 35.28 | 40.705 | 0 | -5.601% | -5.594%
ESe | 23.54 | 10.52 | 12.14 | 0 | 27.91 | 12.48 | 14.4 | 0 | 25.725 | 11.5 | 13.27 | 0 | -18.56% | -18.63%
EPr | 41.35 | 18.48 | 21.33 | 0 | 43.19 | 19.3 | 22.27 | 0 | 42.27 | 18.89 | 21.8 | 0 | -4.45% | -4.437%
[9 empty] | GMC($)/ton |  |  | BASE Cost($)/ton |  |  | IMC($)/ton
[9 empty] | Material | Labor | Total | Material | Labor | Total | Material | Labor | Total
[5 empty] | Costs used in Workpaper (AC and HP) |  |  | ERC | 78.92 | 35.28 | 114.2 | 38.215 | 35.28 | 73.495 | 40.705 | 0 | 40.705
[8 empty] | ESe | 49.5 | 22 | 71.5 | 24 | 22 | 46 | 25.5 | 0 | 25.5
[8 empty] | EPr | 42.27 | 18.89 | 61.16 | 20.47 | 18.89 | 39.36 | 21.8 | 0 | 21.8

## CZ09 Analysis
CZ09 | HVAC Type |  | AC | [8 empty] | GMC($)/ton |  | Base Cost/ton |  | IMC($)/ton |  | ERC -AC-09 | HVAC System Type | Btuh |  |  | Ese-09 | [8 empty] | Epr-09 |  |  |  | AC | HP
|  | Area Classroom (sq.ft.) | Tonnage | Sq.ft./Ton | kWh savings | Savings/ton | # AC units | Savings/unit | # of classroom spaces | Savings/space | Average Unit Size (Tons) | Material | Labor | Material | Labor | Material | Labor | EL1 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 55571 | 961 | EL1 Ground Flr | Floor Name | Area | HVAC System Name | HVAC System Type | AC Btuh | HVAC System Name | HVAC System Type | HP Btuh | HP Cooling Btuh | Floor Name | Area | HVAC System Type | System Type | Btuh | Btuh
[18 empty] | EL2 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 56599 | 961 | EL2 Ground Flr | E1 Ground Flr | 3751 | E2 Sys1 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 64077 | E2 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 264477 | 264477 | EL1 Ground Flr | 15747 | EL1 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 223015 | 218418
| ERC | 1922 | 9.3475 | 205.6165 | 564.3 | 60.3691 | 2 | 282.15 | 2 | 282.15 | 4.6738 | 74.6724 | 33.3779 | 36.1594 | 33.3779 | 38.513 | 0 | [5 empty] | E2 Ground Flr | 5813 | E2 Sys1 (PVVT) (G.S2) | Pkgd Var Vol Var Temp | 112316 | E4 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 661289 | 661289 | EL2 Ground Flr | 9251 | EL1 Sys1 (PVVT) (G.NNE2) | Pkgd Var Vol Var Temp | 147994 | 144585
| ESe | 94502 | 376.6064 | 250.9304 | 23629.2172 | 62.7425 | 49 | 482.2289 | 40 | 590.7304 | #REF! | 45.4082 | 20.2971 | 21.9885 | 20.2971 | 23.4197 | 0 | ERC-HP |  |  |  |  | E3 Ground Flr | 8248 | E2 Sys1 (PVVT) (G.N3) | Pkgd Var Vol Var Temp | 92391 | E6 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 265750 | 265750 | EL3 Ground Flr | 15747 | EL1 Sys1 (PVVT) (G.SSE3) | Pkgd Var Vol Var Temp | 188677 | 183599
| EPr | 31494.2 | 120.348 | 261.6927 | 6658.2734 | 55.3252 | 14 | 475.591 | 8 | 832.2842 | 13.6466 | 40.5989 | 18.1474 | 19.6596 | 18.1474 | 20.9393 | 0 | EL1 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 54060 |  |  | E4 Ground Flr | 14062 | E4 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 235152 | E8 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 664001 | 664001 | EL4 Ground Flr | 9251 | EL1 Sys1 (PVVT) (G.W4) | Pkgd Var Vol Var Temp | 170542 | 166016
| Coefficient of variation |  |  |  |  | 6.369% | [11 empty] | EL2 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 55044 |  |  | E5 Ground Flr | 3751 | E4 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 95868 | E10 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 265447 | 265447 |  |  | EL2 Sys1 (PVVT) (G.SSW1) | Pkgd Var Vol Var Temp | 193207 | 189801
[23 empty] | E6 Ground Flr | 5813 | E4 Sys1 (PVVT) (G.N3) | Pkgd Var Vol Var Temp | 184520 | E12 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 662279 | 662279 |  |  | EL2 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 129961 | 126965
| HVAC Type |  | HP | [8 empty] | GMC/ton |  | Base Cost/ton |  | IMC/ton | [6 empty] | E7 Ground Flr | 8248 | E4 Sys1 (PVVT) (G.W4) | Pkgd Var Vol Var Temp | 87330 | E14 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 265836 | 265836 |  |  | EL3 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 223015 | 218418
|  | Area Classroom (sq.ft.) | Cooling Tons | Sq.ft./Ton | kWh savings | Savings/ton | # HP units | Savings/unit | # of classroom spaces | Savings/space | Average Unit Size (Tons) | Material | Labor | Material | Labor | Material | Labor | [5 empty] | E8 Ground Flr | 14062 | E4 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 70507 | E16 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 665534 | 665534 |  |  | EL3 Sys1 (PVVT) (G.ESE2) | Pkgd Var Vol Var Temp | 178851 | 174184
[23 empty] | E9 Ground Flr | 3751 | E6 Sys1 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 64077 | E1 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 169177 | 169177 |  |  | EL3 Sys1 (PVVT) (G.WSW3) | Pkgd Var Vol Var Temp | 154821 | 150939
| ERC | 1922 | 9.092 | 211.3946 | 625.3 | 68.7747 | 2 | 312.65 | 2 | 312.65 | #DIV/0! | 76.7708 | 34.3159 | 37.1755 | 34.3159 | 39.5952 | 0 | [5 empty] | E10 Ground Flr | 5813 | E6 Sys1 (PVVT) (G.W2) | Pkgd Var Vol Var Temp | 97369 | E3 Sys2 (PVVT) (G.SW1) | Pkgd Var Vol Var Temp | 323348 | 323348 |  |  | EL3 Sys1 (PVVT) (G.N4) | Pkgd Var Vol Var Temp | 161979 | 158033
| ESe | 94502 | 370.6796 | 254.9425 | 24422.4336 | 65.8856 | 25 | 976.8973 | 40 | 610.5608 | #REF! | 23.5378 | 10.5212 | 11.398 | 10.5212 | 12.1399 | 0 | [5 empty] | E11 Ground Flr | 8248 | E6 Sys1 (PVVT) (G.E3) | Pkgd Var Vol Var Temp | 108893 | E4 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 31819 | 31819 |  |  | EL4 Sys1 (PVVT) (G.WNW1) | Pkgd Var Vol Var Temp | 181989 | 178994
| EPr | 31494.2 | 118.1563 | 266.5469 | 9047.7242 | 76.5742 | 14 | 646.266 | 8 | 1130.9655 | #DIV/0! | 41.352 | 18.484 | 20.0243 | 18.484 | 21.3277 | 0 | [5 empty] | E12 Ground Flr | 14062 | E8 Sys1 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 208001 | E5 Sys2 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 168381 | 168381 |  |  | EL4 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 138927 | 135594
| Coefficient of variation |  |  |  |  | 7.853% | [16 empty] | E13 Ground Flr | 3751 | E8 Sys1 (PVVT) (G.S2) | Pkgd Var Vol Var Temp | 100183 | E7 Sys2 (PVVT) (G.NW1) | Pkgd Var Vol Var Temp | 340084 | 340084 |  |  | EL2 Sys2 (PSZ) (G.E3) | Pkgd Single Zone | 98915 | 101725
[23 empty] | E14 Ground Flr | 5813 | E8 Sys1 (PVVT) (G.E3) | Pkgd Var Vol Var Temp | 226516 | E8 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 31819 | 31819 |  |  | EL4 Sys2 (PSZ) (G.S3) | Pkgd Single Zone | 100735 | 103605
[23 empty] | E15 Ground Flr | 8248 | E8 Sys1 (PVVT) (G.N4) | Pkgd Var Vol Var Temp | 71670 | E9 Sys2 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 175430 | 175430
[23 empty] | E16 Ground Flr | 14062 | E8 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 70507 | E11 Sys2 (PVVT) (G.NE1) | Pkgd Var Vol Var Temp | 317422 | 317422
[23 empty] | E17 Ground Flr | 22500 | E10 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 64077 | E12 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 31819 | 31819
[25 empty] | E10 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 92384 | E13 Sys2 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 175601 | 175601
[25 empty] | E10 Sys1 (PVVT) (G.S3) | Pkgd Var Vol Var Temp | 113279 | E15 Sys2 (PVVT) (G.SE1) | Pkgd Var Vol Var Temp | 328297 | 328297
[25 empty] | E12 Sys1 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 184389 | E16 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 31819 | 31819
[25 empty] | E12 Sys1 (PVVT) (G.W2) | Pkgd Var Vol Var Temp | 89972 | E17 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 793625 | 793625
[18 empty] | Thermostat Unit Cost | [6 empty] | E12 Sys1 (PVVT) (G.S3) | Pkgd Var Vol Var Temp | 235921 | E3 Sys3 (PSZ) (G.NE2) | Pkgd Single Zone | 103796 | 103796
[19 empty] | GMC | Base | IMC |  |  |  | E12 Sys1 (PVVT) (G.E4) | Pkgd Var Vol Var Temp | 93544 | E7 Sys3 (PSZ) (G.SE2) | Pkgd Single Zone | 113027 | 113027
[18 empty] | Material | 349 | 169 | 180 |  |  |  | E12 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 70507 | E11 Sys3 (PSZ) (G.SW2) | Pkgd Single Zone | 109634 | 109634
[18 empty] | Labor | 156 | 156 | 0 |  |  |  | E14 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 64077 | E15 Sys3 (PSZ) (G.NW2) | Pkgd Single Zone | 100440 | 100440
[25 empty] | E14 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 107943
[25 empty] | E14 Sys1 (PVVT) (G.W3) | Pkgd Var Vol Var Temp | 98398
[25 empty] | E16 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 225777
[25 empty] | E16 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 75116
[25 empty] | E16 Sys1 (PVVT) (G.W3) | Pkgd Var Vol Var Temp | 208798
[25 empty] | E16 Sys1 (PVVT) (G.S4) | Pkgd Var Vol Var Temp | 98488
[25 empty] | E16 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 70507
[25 empty] | E1 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 172816
[25 empty] | E3 Sys2 (PVVT) (G.SW1) | Pkgd Var Vol Var Temp | 328249
[25 empty] | E4 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 32869
[25 empty] | E5 Sys2 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 171988
[25 empty] | E7 Sys2 (PVVT) (G.NW1) | Pkgd Var Vol Var Temp | 345512
[25 empty] | E8 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 32869
[25 empty] | E9 Sys2 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 179327
[25 empty] | E11 Sys2 (PVVT) (G.NE1) | Pkgd Var Vol Var Temp | 322143
[25 empty] | E12 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 32869
[25 empty] | E13 Sys2 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 179505
[25 empty] | E15 Sys2 (PVVT) (G.SE1) | Pkgd Var Vol Var Temp | 333351
[25 empty] | E16 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 32869
[25 empty] | E17 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 810127
[25 empty] | E3 Sys3 (PSZ) (G.NE2) | Pkgd Single Zone | 101139
[25 empty] | E7 Sys3 (PSZ) (G.SE2) | Pkgd Single Zone | 110144
[25 empty] | E11 Sys3 (PSZ) (G.SW2) | Pkgd Single Zone | 106831
[25 empty] | E15 Sys3 (PSZ) (G.NW2) | Pkgd Single Zone | 97873

## CZ08 Analysis
CZ08 | HVAC Type |  | AC | [8 empty] | GMC/ton |  | Base Cost/ton |  | IMC/ton |  | ERC -AC-08 | HVAC System Type | Btuh |  |  | Ese-08 | [8 empty] | Epr-08 |  |  |  | AC | HP
|  | Area Classroom (sq.ft.) | Tonnage | Sq.ft./Ton | kWh savings | Savings/ton | # AC units | Savings/unit | # of classroom spaces | Savings/space | Average Unit Size (Tons) | Material | Labor | Material | Labor | Material | Labor | EL1 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 52699 | 961 | EL1 Ground Flr | Floor Name | Area | HVAC System Name | HVAC System Type | AC Btuh | HVAC System Name | HVAC System Type | HP Btuh | HP Cooling Btuh | Floor Name | Area | HVAC System Type | System Type | Btuh | Btuh
[18 empty] | EL2 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 53663 | 961 | EL2 Ground Flr | E1 Ground Flr | 3751 | E2 Sys1 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 54750 | E2 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 226971 | 264477 | EL1 Ground Flr | 15747 | EL1 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 212877 | 208140
| ERC | 1922 | 8.8635 | 216.8444 | 577.4 | 65.1436 | 2 | 288.7 | 2 | 288.7 | 4.4318 | 78.7499 | 35.2005 | 38.1339 | 35.2005 | 40.616 | 0 | [5 empty] | E2 Ground Flr | 5813 | E2 Sys1 (PVVT) (G.S2) | Pkgd Var Vol Var Temp | 99528 | E4 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 567091 | 661289 | EL2 Ground Flr | 9251 | EL1 Sys1 (PVVT) (G.NNE2) | Pkgd Var Vol Var Temp | 141284 | 137808
| ESe | 94502 | 318.5984 | 296.6179 | 21833.9902 | 68.5314 | 49 | 445.5916 | 40 | 545.8498 | #REF! | 53.6757 | 23.9926 | 25.992 | 23.9926 | 27.6838 | 0 | ERC-HP |  |  |  |  | E3 Ground Flr | 8248 | E2 Sys1 (PVVT) (G.N3) | Pkgd Var Vol Var Temp | 77203 | E6 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 223220 | 265750 | EL3 Ground Flr | 15747 | EL1 Sys1 (PVVT) (G.SSE3) | Pkgd Var Vol Var Temp | 180412 | 175301
| EPr | 31494.2 | 115.3778 | 272.9658 | 6824.5727 | 59.1498 | 14 | 487.4695 | 8 | 853.0716 | 13.083 | 42.3478 | 18.9291 | 20.5065 | 18.9291 | 21.8413 | 0 | EL1 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 51197 |  |  | E4 Ground Flr | 14062 | E4 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 209717 | E8 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 564519 | 664001 | EL4 Ground Flr | 9251 | EL1 Sys1 (PVVT) (G.W4) | Pkgd Var Vol Var Temp | 166271 | 161784
| Coefficient of variation |  |  |  |  | 7.391% | [11 empty] | EL2 Sys1 (PVVT) (G.1) | Pkgd Var Vol Var Temp | 52120 |  |  | E5 Ground Flr | 3751 | E4 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 81418 | E10 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 227662 | 265447 |  |  | EL2 Sys1 (PVVT) (G.SSW1) | Pkgd Var Vol Var Temp | 185210 | 181555
[23 empty] | E6 Ground Flr | 5813 | E4 Sys1 (PVVT) (G.N3) | Pkgd Var Vol Var Temp | 154538 | E12 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 567940 | 662279 |  |  | EL2 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 129237 | 126051
| HVAC Type |  | HP | [8 empty] | GMC/ton |  | Base Cost/ton |  | IMC/ton | [6 empty] | E7 Ground Flr | 8248 | E4 Sys1 (PVVT) (G.W4) | Pkgd Var Vol Var Temp | 73406 | E14 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 223287 | 265836 |  |  | EL3 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 212877 | 208140
|  | Area Classroom (sq.ft.) | Cooling Tons | Sq.ft./Ton | kWh savings | Savings/ton | # HP units | Savings/unit | # of classroom spaces | Savings/space | Average Unit Size (Tons) | Material | Labor | Material | Labor | Material | Labor | [5 empty] | E8 Ground Flr | 14062 | E4 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 60480 | E16 Sys1 (PVVT) (G) | Pkgd Var Vol Var Temp | 564842 | 665534 |  |  | EL3 Sys1 (PVVT) (G.ESE2) | Pkgd Var Vol Var Temp | 168536 | 163929
[23 empty] | E9 Ground Flr | 3751 | E6 Sys1 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 54750 | E1 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 144923 | 169177 |  |  | EL3 Sys1 (PVVT) (G.WSW3) | Pkgd Var Vol Var Temp | 143711 | 139938
| ERC | 1922 | 8.6098 | 223.2353 | 623.9 | 72.4644 | 2 | 311.95 | 2 | 311.95 | #DIV/0! | 81.0709 | 36.238 | 39.2578 | 36.238 | 41.8131 | 0 | [5 empty] | E10 Ground Flr | 5813 | E6 Sys1 (PVVT) (G.W2) | Pkgd Var Vol Var Temp | 81248 | E3 Sys2 (PVVT) (G.SW1) | Pkgd Var Vol Var Temp | 263542 | 323348 |  |  | EL3 Sys1 (PVVT) (G.N4) | Pkgd Var Vol Var Temp | 154538 | 150541
| ESe | 94502 | 312.5686 | 302.34 | 22298.5164 | 71.3396 | 25 | 891.9407 | 40 | 557.4629 | #REF! | 27.9139 | 12.4773 | 13.517 | 12.4773 | 14.3968 | 0 | [5 empty] | E11 Ground Flr | 8248 | E6 Sys1 (PVVT) (G.E3) | Pkgd Var Vol Var Temp | 92019 | E4 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 29059 | 31819 |  |  | EL4 Sys1 (PVVT) (G.WNW1) | Pkgd Var Vol Var Temp | 174909 | 171658
| EPr | 31494.2 | 113.1353 | 278.3765 | 8253.4873 | 72.9524 | 14 | 589.5348 | 8 | 1031.6859 | #DIV/0! | 43.1872 | 19.3043 | 20.913 | 19.3043 | 22.2742 | 0 | [5 empty] | E12 Ground Flr | 14062 | E8 Sys1 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 174946 | E5 Sys2 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 143665 | 168381 |  |  | EL4 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 136850 | 133366
| Coefficient of variation |  |  |  |  | 1.145% | [16 empty] | E13 Ground Flr | 3751 | E8 Sys1 (PVVT) (G.S2) | Pkgd Var Vol Var Temp | 90015 | E7 Sys2 (PVVT) (G.NW1) | Pkgd Var Vol Var Temp | 274500 | 340084 |  |  | EL2 Sys2 (PSZ) (G.E3) | Pkgd Single Zone | 94178 | 97022
[23 empty] | E14 Ground Flr | 5813 | E8 Sys1 (PVVT) (G.E3) | Pkgd Var Vol Var Temp | 192486 | E8 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 29059 | 31819 |  |  | EL4 Sys2 (PSZ) (G.S3) | Pkgd Single Zone | 97056 | 99992
[23 empty] | E15 Ground Flr | 8248 | E8 Sys1 (PVVT) (G.N4) | Pkgd Var Vol Var Temp | 59629 | E9 Sys2 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 150368 | 175430
[23 empty] | E16 Ground Flr | 14062 | E8 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 60480 | E11 Sys2 (PVVT) (G.NE1) | Pkgd Var Vol Var Temp | 255328 | 317422
[23 empty] | E17 Ground Flr | 22500 | E10 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 54750 | E12 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 29059 | 31819
[25 empty] | E10 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 77205 | E13 Sys2 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 150951 | 175601
[25 empty] | E10 Sys1 (PVVT) (G.S3) | Pkgd Var Vol Var Temp | 100211 | E15 Sys2 (PVVT) (G.SE1) | Pkgd Var Vol Var Temp | 264437 | 328297
[25 empty] | E12 Sys1 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 154405 | E16 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 29059 | 31819
[25 empty] | E12 Sys1 (PVVT) (G.W2) | Pkgd Var Vol Var Temp | 75843 | E17 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 672198 | 793625
[18 empty] | Thermostat Unit Cost | [6 empty] | E12 Sys1 (PVVT) (G.S3) | Pkgd Var Vol Var Temp | 210445 | E3 Sys3 (PSZ) (G.NE2) | Pkgd Single Zone | 84218 | 103796
[19 empty] | GMC | Base | IMC |  |  |  | E12 Sys1 (PVVT) (G.E4) | Pkgd Var Vol Var Temp | 79199 | E7 Sys3 (PSZ) (G.SE2) | Pkgd Single Zone | 94031 | 113027
[18 empty] | Material | 349 | 169 | 180 |  |  |  | E12 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 60480 | E11 Sys3 (PSZ) (G.SW2) | Pkgd Single Zone | 91737 | 109634
[18 empty] | Labor | 156 | 156 | 0 |  |  |  | E14 Sys1 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 54750 | E15 Sys3 (PSZ) (G.NW2) | Pkgd Single Zone | 81673 | 100440
[25 empty] | E14 Sys1 (PVVT) (G.E2) | Pkgd Var Vol Var Temp | 91128
[25 empty] | E14 Sys1 (PVVT) (G.W3) | Pkgd Var Vol Var Temp | 82193
[25 empty] | E16 Sys1 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 191786
[25 empty] | E16 Sys1 (PVVT) (G.N2) | Pkgd Var Vol Var Temp | 62771
[25 empty] | E16 Sys1 (PVVT) (G.W3) | Pkgd Var Vol Var Temp | 175694
[25 empty] | E16 Sys1 (PVVT) (G.S4) | Pkgd Var Vol Var Temp | 87388
[25 empty] | E16 Sys1 (PVVT) (G.C6) | Pkgd Var Vol Var Temp | 60480
[25 empty] | E1 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 148634
[25 empty] | E3 Sys2 (PVVT) (G.SW1) | Pkgd Var Vol Var Temp | 268582
[25 empty] | E4 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 30095
[25 empty] | E5 Sys2 (PVVT) (G.N1) | Pkgd Var Vol Var Temp | 147321
[25 empty] | E7 Sys2 (PVVT) (G.NW1) | Pkgd Var Vol Var Temp | 279901
[25 empty] | E8 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 30095
[25 empty] | E9 Sys2 (PVVT) (G.E1) | Pkgd Var Vol Var Temp | 154318
[25 empty] | E11 Sys2 (PVVT) (G.NE1) | Pkgd Var Vol Var Temp | 260092
[25 empty] | E12 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 30095
[25 empty] | E13 Sys2 (PVVT) (G.S1) | Pkgd Var Vol Var Temp | 154927
[25 empty] | E15 Sys2 (PVVT) (G.SE1) | Pkgd Var Vol Var Temp | 269506
[25 empty] | E16 Sys2 (PVVT) (G.C5) | Pkgd Var Vol Var Temp | 30095
[25 empty] | E17 Sys2 (PVVT) (G.W1) | Pkgd Var Vol Var Temp | 687779
[25 empty] | E3 Sys3 (PSZ) (G.NE2) | Pkgd Single Zone | 81744
[25 empty] | E7 Sys3 (PSZ) (G.SE2) | Pkgd Single Zone | 91318
[25 empty] | E11 Sys3 (PSZ) (G.SW2) | Pkgd Single Zone | 89078
[25 empty] | E15 Sys3 (PSZ) (G.NW2) | Pkgd Single Zone | 79265

## DEER2014 Comm CZ weights
Commercial Climate Zone Weights by IOU, Vintage and Building Type
Weight Group: | ComIOUterr
Weighed Field: | BldgLoc |  |  | Resulting Weighted Field Value: | IOU
Weight Basis: | Stock Area (millions of square feet)
Usage: | For a given IOU, Building Type and Location, the table provides the weights to be applied to Existing and New vintage results to arrive at an "IOU" location result. | [11 empty] | CZ01 | 1
[13 empty] | CZ02 | 5
Notes: | Applies to records previously weighted into Existing vintage or New vintage and weighted HVAC type | [11 empty] | CZ03 | 19
[13 empty] | CZ04 | 10
[13 empty] | CZ05 | 1
[13 empty] | CZ06 | 26
DEER InterMeasWtDef Table (unique rows only): | [9 empty] | DEER InterMeasWts Table: |  |  | CZ07 | 8
WtGroup | WtSet | Fld Code | IOU in | IOU out | Bldg Type | Vint | Loc | HVAC | lookup | WtSet | Wtd Field | Weight | CZ08 | 45
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ01 | AsmExPGE | CZ01 | 0.98847 | CZ09 | 33
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ02 | AsmExPGE | CZ02 | 9.5992 | CZ10 | 31
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ03 | AsmExPGE | CZ03 | 48.5794 | CZ11 | 4
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ04 | AsmExPGE | CZ04 | 25.8347 | CZ12 | 15
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ05 | AsmExPGE | CZ05 | 3.0837 | CZ13 | 17
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ06 | AsmExPGE | CZ06 | 0 | CZ14 | 7
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ07 | AsmExPGE | CZ07 | 0 | CZ15 | 2
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ08 | AsmExPGE | CZ08 | 0 | CZ16 | 4
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ09 | AsmExPGE | CZ09 | 0
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ10 | AsmExPGE | CZ10 | 0
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ11 | AsmExPGE | CZ11 | 6.9356
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ12 | AsmExPGE | CZ12 | 27.1607
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ13 | AsmExPGE | CZ13 | 17.1849
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ14 | AsmExPGE | CZ14 | 0
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ15 | AsmExPGE | CZ15 | 0
ComIOUterr | AsmExPGE | IOU | PGE | PGE | Asm | Ex | Multiple | Any | AsmExPGECZ16 | AsmExPGE | CZ16 | 1.5283
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ01 | EPrExPGE | CZ01 | 0.6656
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ02 | EPrExPGE | CZ02 | 4.9532
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ03 | EPrExPGE | CZ03 | 19.0541
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ04 | EPrExPGE | CZ04 | 9.6712
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ05 | EPrExPGE | CZ05 | 1.3378
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ06 | EPrExPGE | CZ06 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ07 | EPrExPGE | CZ07 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ08 | EPrExPGE | CZ08 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ09 | EPrExPGE | CZ09 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ10 | EPrExPGE | CZ10 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ11 | EPrExPGE | CZ11 | 4.1641
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ12 | EPrExPGE | CZ12 | 14.6834
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ13 | EPrExPGE | CZ13 | 11.1814
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ14 | EPrExPGE | CZ14 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ15 | EPrExPGE | CZ15 | 0
ComIOUterr | EPrExPGE | IOU | PGE | PGE | EPr | Ex | Multiple | Any | EPrExPGECZ16 | EPrExPGE | CZ16 | 0.6365
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ01 | ESeExPGE | CZ01 | 0.6656
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ02 | ESeExPGE | CZ02 | 4.9532
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ03 | ESeExPGE | CZ03 | 19.0541
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ04 | ESeExPGE | CZ04 | 9.6712
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ05 | ESeExPGE | CZ05 | 1.3378
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ06 | ESeExPGE | CZ06 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ07 | ESeExPGE | CZ07 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ08 | ESeExPGE | CZ08 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ09 | ESeExPGE | CZ09 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ10 | ESeExPGE | CZ10 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ11 | ESeExPGE | CZ11 | 4.1641
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ12 | ESeExPGE | CZ12 | 14.6834
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ13 | ESeExPGE | CZ13 | 11.1814
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ14 | ESeExPGE | CZ14 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ15 | ESeExPGE | CZ15 | 0
ComIOUterr | ESeExPGE | IOU | PGE | PGE | ESe | Ex | Multiple | Any | ESeExPGECZ16 | ESeExPGE | CZ16 | 0.6365
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ01 | ECCExPGE | CZ01 | 1.7287
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ02 | ECCExPGE | CZ02 | 4.4723
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ03 | ECCExPGE | CZ03 | 22.5617
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ04 | ECCExPGE | CZ04 | 5.5364
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ05 | ECCExPGE | CZ05 | 4.1862
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ06 | ECCExPGE | CZ06 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ07 | ECCExPGE | CZ07 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ08 | ECCExPGE | CZ08 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ09 | ECCExPGE | CZ09 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ10 | ECCExPGE | CZ10 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ11 | ECCExPGE | CZ11 | 5.4282
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ12 | ECCExPGE | CZ12 | 7.7298
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ13 | ECCExPGE | CZ13 | 8.2401
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ14 | ECCExPGE | CZ14 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ15 | ECCExPGE | CZ15 | 0
ComIOUterr | ECCExPGE | IOU | PGE | PGE | ECC | Ex | Multiple | Any | ECCExPGECZ16 | ECCExPGE | CZ16 | 0.17075
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ01 | EUnExPGE | CZ01 | 1.7287
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ02 | EUnExPGE | CZ02 | 4.4723
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ03 | EUnExPGE | CZ03 | 22.5617
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ04 | EUnExPGE | CZ04 | 5.5364
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ05 | EUnExPGE | CZ05 | 4.1862
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ06 | EUnExPGE | CZ06 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ07 | EUnExPGE | CZ07 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ08 | EUnExPGE | CZ08 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ09 | EUnExPGE | CZ09 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ10 | EUnExPGE | CZ10 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ11 | EUnExPGE | CZ11 | 5.4282
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ12 | EUnExPGE | CZ12 | 7.7298
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ13 | EUnExPGE | CZ13 | 8.2401
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ14 | EUnExPGE | CZ14 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ15 | EUnExPGE | CZ15 | 0
ComIOUterr | EUnExPGE | IOU | PGE | PGE | EUn | Ex | Multiple | Any | EUnExPGECZ16 | EUnExPGE | CZ16 | 0.17075
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ01 | ERCExPGE | CZ01 | 0.6656
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ02 | ERCExPGE | CZ02 | 4.9532
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ03 | ERCExPGE | CZ03 | 19.0541
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ04 | ERCExPGE | CZ04 | 9.6712
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ05 | ERCExPGE | CZ05 | 1.3378
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ06 | ERCExPGE | CZ06 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ07 | ERCExPGE | CZ07 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ08 | ERCExPGE | CZ08 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ09 | ERCExPGE | CZ09 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ10 | ERCExPGE | CZ10 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ11 | ERCExPGE | CZ11 | 4.1641
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ12 | ERCExPGE | CZ12 | 14.6834
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ13 | ERCExPGE | CZ13 | 11.1814
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ14 | ERCExPGE | CZ14 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ15 | ERCExPGE | CZ15 | 0
ComIOUterr | ERCExPGE | IOU | PGE | PGE | ERC | Ex | Multiple | Any | ERCExPGECZ16 | ERCExPGE | CZ16 | 0.6365
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ01 | GroExPGE | CZ01 | 1.0874
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ02 | GroExPGE | CZ02 | 7.9051
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ03 | GroExPGE | CZ03 | 27.6971
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ04 | GroExPGE | CZ04 | 12.2977
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ05 | GroExPGE | CZ05 | 2.7854
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ06 | GroExPGE | CZ06 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ07 | GroExPGE | CZ07 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ08 | GroExPGE | CZ08 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ09 | GroExPGE | CZ09 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ10 | GroExPGE | CZ10 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ11 | GroExPGE | CZ11 | 7.1695
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ12 | GroExPGE | CZ12 | 23.313
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ13 | GroExPGE | CZ13 | 16.2025
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ14 | GroExPGE | CZ14 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ15 | GroExPGE | CZ15 | 0
ComIOUterr | GroExPGE | IOU | PGE | PGE | Gro | Ex | Multiple | Any | GroExPGECZ16 | GroExPGE | CZ16 | 1.2151
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ01 | HspExPGE | CZ01 | 0.71595
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ02 | HspExPGE | CZ02 | 5.9349
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ03 | HspExPGE | CZ03 | 17.7045
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ04 | HspExPGE | CZ04 | 8.0267
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ05 | HspExPGE | CZ05 | 1.2216
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ06 | HspExPGE | CZ06 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ07 | HspExPGE | CZ07 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ08 | HspExPGE | CZ08 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ09 | HspExPGE | CZ09 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ10 | HspExPGE | CZ10 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ11 | HspExPGE | CZ11 | 4.0518
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ12 | HspExPGE | CZ12 | 13.3001
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ13 | HspExPGE | CZ13 | 10.3598
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ14 | HspExPGE | CZ14 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ15 | HspExPGE | CZ15 | 0
ComIOUterr | HspExPGE | IOU | PGE | PGE | Hsp | Ex | Multiple | Any | HspExPGECZ16 | HspExPGE | CZ16 | 0.2337
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ01 | NrsExPGE | CZ01 | 0.71595
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ02 | NrsExPGE | CZ02 | 5.9349
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ03 | NrsExPGE | CZ03 | 17.7045
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ04 | NrsExPGE | CZ04 | 8.0267
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ05 | NrsExPGE | CZ05 | 1.2216
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ06 | NrsExPGE | CZ06 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ07 | NrsExPGE | CZ07 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ08 | NrsExPGE | CZ08 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ09 | NrsExPGE | CZ09 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ10 | NrsExPGE | CZ10 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ11 | NrsExPGE | CZ11 | 4.0518
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ12 | NrsExPGE | CZ12 | 13.3001
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ13 | NrsExPGE | CZ13 | 10.3598
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ14 | NrsExPGE | CZ14 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ15 | NrsExPGE | CZ15 | 0
ComIOUterr | NrsExPGE | IOU | PGE | PGE | Nrs | Ex | Multiple | Any | NrsExPGECZ16 | NrsExPGE | CZ16 | 0.2337
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ01 | HtlExPGE | CZ01 | 0.8617
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ02 | HtlExPGE | CZ02 | 4.0187
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ03 | HtlExPGE | CZ03 | 25.6
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ04 | HtlExPGE | CZ04 | 8.4366
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ05 | HtlExPGE | CZ05 | 3.5217
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ06 | HtlExPGE | CZ06 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ07 | HtlExPGE | CZ07 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ08 | HtlExPGE | CZ08 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ09 | HtlExPGE | CZ09 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ10 | HtlExPGE | CZ10 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ11 | HtlExPGE | CZ11 | 2.2387
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ12 | HtlExPGE | CZ12 | 7.6127
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ13 | HtlExPGE | CZ13 | 4.901
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ14 | HtlExPGE | CZ14 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ15 | HtlExPGE | CZ15 | 0
ComIOUterr | HtlExPGE | IOU | PGE | PGE | Htl | Ex | Multiple | Any | HtlExPGECZ16 | HtlExPGE | CZ16 | 0.9397
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ01 | MtlExPGE | CZ01 | 0.8617
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ02 | MtlExPGE | CZ02 | 4.0187
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ03 | MtlExPGE | CZ03 | 25.6
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ04 | MtlExPGE | CZ04 | 8.4366
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ05 | MtlExPGE | CZ05 | 3.5217
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ06 | MtlExPGE | CZ06 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ07 | MtlExPGE | CZ07 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ08 | MtlExPGE | CZ08 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ09 | MtlExPGE | CZ09 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ10 | MtlExPGE | CZ10 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ11 | MtlExPGE | CZ11 | 2.2387
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ12 | MtlExPGE | CZ12 | 7.6127
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ13 | MtlExPGE | CZ13 | 4.901
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ14 | MtlExPGE | CZ14 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ15 | MtlExPGE | CZ15 | 0
ComIOUterr | MtlExPGE | IOU | PGE | PGE | Mtl | Ex | Multiple | Any | MtlExPGECZ16 | MtlExPGE | CZ16 | 0.9397
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ01 | MBTExPGE | CZ01 | 0.98847
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ02 | MBTExPGE | CZ02 | 9.5992
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ03 | MBTExPGE | CZ03 | 48.5794
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ04 | MBTExPGE | CZ04 | 25.8347
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ05 | MBTExPGE | CZ05 | 3.0837
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ06 | MBTExPGE | CZ06 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ07 | MBTExPGE | CZ07 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ08 | MBTExPGE | CZ08 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ09 | MBTExPGE | CZ09 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ10 | MBTExPGE | CZ10 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ11 | MBTExPGE | CZ11 | 6.9356
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ12 | MBTExPGE | CZ12 | 27.1607
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ13 | MBTExPGE | CZ13 | 17.1849
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ14 | MBTExPGE | CZ14 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ15 | MBTExPGE | CZ15 | 0
ComIOUterr | MBTExPGE | IOU | PGE | PGE | MBT | Ex | Multiple | Any | MBTExPGECZ16 | MBTExPGE | CZ16 | 1.5283
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ01 | MLIExPGE | CZ01 | 0.98847
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ02 | MLIExPGE | CZ02 | 9.5992
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ03 | MLIExPGE | CZ03 | 48.5794
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ04 | MLIExPGE | CZ04 | 25.8347
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ05 | MLIExPGE | CZ05 | 3.0837
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ06 | MLIExPGE | CZ06 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ07 | MLIExPGE | CZ07 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ08 | MLIExPGE | CZ08 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ09 | MLIExPGE | CZ09 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ10 | MLIExPGE | CZ10 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ11 | MLIExPGE | CZ11 | 6.9356
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ12 | MLIExPGE | CZ12 | 27.1607
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ13 | MLIExPGE | CZ13 | 17.1849
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ14 | MLIExPGE | CZ14 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ15 | MLIExPGE | CZ15 | 0
ComIOUterr | MLIExPGE | IOU | PGE | PGE | MLI | Ex | Multiple | Any | MLIExPGECZ16 | MLIExPGE | CZ16 | 1.5283
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ01 | OfLExPGE | CZ01 | 1.5904
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ02 | OfLExPGE | CZ02 | 18.4354
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ03 | OfLExPGE | CZ03 | 197.8423
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ04 | OfLExPGE | CZ04 | 82.2623
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ05 | OfLExPGE | CZ05 | 5.7737
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ06 | OfLExPGE | CZ06 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ07 | OfLExPGE | CZ07 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ08 | OfLExPGE | CZ08 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ09 | OfLExPGE | CZ09 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ10 | OfLExPGE | CZ10 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ11 | OfLExPGE | CZ11 | 6.9676
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ12 | OfLExPGE | CZ12 | 59.525
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ13 | OfLExPGE | CZ13 | 24.5407
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ14 | OfLExPGE | CZ14 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ15 | OfLExPGE | CZ15 | 0
ComIOUterr | OfLExPGE | IOU | PGE | PGE | OfL | Ex | Multiple | Any | OfLExPGECZ16 | OfLExPGE | CZ16 | 0.82
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ01 | OfSExPGE | CZ01 | 2.1001
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ02 | OfSExPGE | CZ02 | 5.0703
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ03 | OfSExPGE | CZ03 | 30.1967
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ04 | OfSExPGE | CZ04 | 23.5669
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ05 | OfSExPGE | CZ05 | 1.6589
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ06 | OfSExPGE | CZ06 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ07 | OfSExPGE | CZ07 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ08 | OfSExPGE | CZ08 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ09 | OfSExPGE | CZ09 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ10 | OfSExPGE | CZ10 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ11 | OfSExPGE | CZ11 | 7.4698
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ12 | OfSExPGE | CZ12 | 29.2663
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ13 | OfSExPGE | CZ13 | 25.9984
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ14 | OfSExPGE | CZ14 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ15 | OfSExPGE | CZ15 | 0
ComIOUterr | OfSExPGE | IOU | PGE | PGE | OfS | Ex | Multiple | Any | OfSExPGECZ16 | OfSExPGE | CZ16 | 1.0466
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ01 | RSDExPGE | CZ01 | 0.36885
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ02 | RSDExPGE | CZ02 | 1.6699
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ03 | RSDExPGE | CZ03 | 7.6247
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ04 | RSDExPGE | CZ04 | 3.354
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ05 | RSDExPGE | CZ05 | 0.65846
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ06 | RSDExPGE | CZ06 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ07 | RSDExPGE | CZ07 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ08 | RSDExPGE | CZ08 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ09 | RSDExPGE | CZ09 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ10 | RSDExPGE | CZ10 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ11 | RSDExPGE | CZ11 | 1.4843
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ12 | RSDExPGE | CZ12 | 5.1334
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ13 | RSDExPGE | CZ13 | 3.5955
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ14 | RSDExPGE | CZ14 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ15 | RSDExPGE | CZ15 | 0
ComIOUterr | RSDExPGE | IOU | PGE | PGE | RSD | Ex | Multiple | Any | RSDExPGECZ16 | RSDExPGE | CZ16 | 0.3024
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ01 | RFFExPGE | CZ01 | 0.36885
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ02 | RFFExPGE | CZ02 | 1.6699
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ03 | RFFExPGE | CZ03 | 7.6247
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ04 | RFFExPGE | CZ04 | 3.354
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ05 | RFFExPGE | CZ05 | 0.65846
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ06 | RFFExPGE | CZ06 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ07 | RFFExPGE | CZ07 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ08 | RFFExPGE | CZ08 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ09 | RFFExPGE | CZ09 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ10 | RFFExPGE | CZ10 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ11 | RFFExPGE | CZ11 | 1.4843
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ12 | RFFExPGE | CZ12 | 5.1334
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ13 | RFFExPGE | CZ13 | 3.5955
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ14 | RFFExPGE | CZ14 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ15 | RFFExPGE | CZ15 | 0
ComIOUterr | RFFExPGE | IOU | PGE | PGE | RFF | Ex | Multiple | Any | RFFExPGECZ16 | RFFExPGE | CZ16 | 0.3024
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ01 | Rt3ExPGE | CZ01 | 1.2409
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ02 | Rt3ExPGE | CZ02 | 8.3222
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ03 | Rt3ExPGE | CZ03 | 38.8235
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ04 | Rt3ExPGE | CZ04 | 16.9153
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ05 | Rt3ExPGE | CZ05 | 2.9099
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ06 | Rt3ExPGE | CZ06 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ07 | Rt3ExPGE | CZ07 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ08 | Rt3ExPGE | CZ08 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ09 | Rt3ExPGE | CZ09 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ10 | Rt3ExPGE | CZ10 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ11 | Rt3ExPGE | CZ11 | 6.6282
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ12 | Rt3ExPGE | CZ12 | 27.992
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ13 | Rt3ExPGE | CZ13 | 16.9871
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ14 | Rt3ExPGE | CZ14 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ15 | Rt3ExPGE | CZ15 | 0
ComIOUterr | Rt3ExPGE | IOU | PGE | PGE | Rt3 | Ex | Multiple | Any | Rt3ExPGECZ16 | Rt3ExPGE | CZ16 | 0.38043
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ01 | RtLExPGE | CZ01 | 1.2409
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ02 | RtLExPGE | CZ02 | 8.3222
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ03 | RtLExPGE | CZ03 | 38.8235
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ04 | RtLExPGE | CZ04 | 16.9153
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ05 | RtLExPGE | CZ05 | 2.9099
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ06 | RtLExPGE | CZ06 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ07 | RtLExPGE | CZ07 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ08 | RtLExPGE | CZ08 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ09 | RtLExPGE | CZ09 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ10 | RtLExPGE | CZ10 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ11 | RtLExPGE | CZ11 | 6.6282
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ12 | RtLExPGE | CZ12 | 27.992
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ13 | RtLExPGE | CZ13 | 16.9871
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ14 | RtLExPGE | CZ14 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ15 | RtLExPGE | CZ15 | 0
ComIOUterr | RtLExPGE | IOU | PGE | PGE | RtL | Ex | Multiple | Any | RtLExPGECZ16 | RtLExPGE | CZ16 | 0.38043
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ01 | RtSExPGE | CZ01 | 1.2409
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ02 | RtSExPGE | CZ02 | 8.3222
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ03 | RtSExPGE | CZ03 | 38.8235
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ04 | RtSExPGE | CZ04 | 16.9153
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ05 | RtSExPGE | CZ05 | 2.9099
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ06 | RtSExPGE | CZ06 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ07 | RtSExPGE | CZ07 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ08 | RtSExPGE | CZ08 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ09 | RtSExPGE | CZ09 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ10 | RtSExPGE | CZ10 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ11 | RtSExPGE | CZ11 | 6.6282
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ12 | RtSExPGE | CZ12 | 27.992
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ13 | RtSExPGE | CZ13 | 16.9871
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ14 | RtSExPGE | CZ14 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ15 | RtSExPGE | CZ15 | 0
ComIOUterr | RtSExPGE | IOU | PGE | PGE | RtS | Ex | Multiple | Any | RtSExPGECZ16 | RtSExPGE | CZ16 | 0.38043
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ01 | SCnExPGE | CZ01 | 1.2814
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ02 | SCnExPGE | CZ02 | 9.9171
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ03 | SCnExPGE | CZ03 | 52.8109
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ04 | SCnExPGE | CZ04 | 19.3915
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ05 | SCnExPGE | CZ05 | 1.4732
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ06 | SCnExPGE | CZ06 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ07 | SCnExPGE | CZ07 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ08 | SCnExPGE | CZ08 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ09 | SCnExPGE | CZ09 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ10 | SCnExPGE | CZ10 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ11 | SCnExPGE | CZ11 | 9.007
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ12 | SCnExPGE | CZ12 | 36.27
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ13 | SCnExPGE | CZ13 | 22.6415
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ14 | SCnExPGE | CZ14 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ15 | SCnExPGE | CZ15 | 0
ComIOUterr | SCnExPGE | IOU | PGE | PGE | SCn | Ex | Multiple | Any | SCnExPGECZ16 | SCnExPGE | CZ16 | 1.145
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ01 | SUnExPGE | CZ01 | 1.2814
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ02 | SUnExPGE | CZ02 | 9.9171
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ03 | SUnExPGE | CZ03 | 52.8109
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ04 | SUnExPGE | CZ04 | 19.3915
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ05 | SUnExPGE | CZ05 | 1.4732
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ06 | SUnExPGE | CZ06 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ07 | SUnExPGE | CZ07 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ08 | SUnExPGE | CZ08 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ09 | SUnExPGE | CZ09 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ10 | SUnExPGE | CZ10 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ11 | SUnExPGE | CZ11 | 9.007
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ12 | SUnExPGE | CZ12 | 36.27
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ13 | SUnExPGE | CZ13 | 22.6415
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ14 | SUnExPGE | CZ14 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ15 | SUnExPGE | CZ15 | 0
ComIOUterr | SUnExPGE | IOU | PGE | PGE | SUn | Ex | Multiple | Any | SUnExPGECZ16 | SUnExPGE | CZ16 | 1.145
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ01 | WRfExPGE | CZ01 | 0.13725
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ02 | WRfExPGE | CZ02 | 0.86962
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ03 | WRfExPGE | CZ03 | 9.5932
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ04 | WRfExPGE | CZ04 | 1.7915
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ05 | WRfExPGE | CZ05 | 1.0532
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ06 | WRfExPGE | CZ06 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ07 | WRfExPGE | CZ07 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ08 | WRfExPGE | CZ08 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ09 | WRfExPGE | CZ09 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ10 | WRfExPGE | CZ10 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ11 | WRfExPGE | CZ11 | 1.2274
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ12 | WRfExPGE | CZ12 | 5.5697
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ13 | WRfExPGE | CZ13 | 8.1963
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ14 | WRfExPGE | CZ14 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ15 | WRfExPGE | CZ15 | 0
ComIOUterr | WRfExPGE | IOU | PGE | PGE | WRf | Ex | Multiple | Any | WRfExPGECZ16 | WRfExPGE | CZ16 | 0.01111
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ01 | AsmNewPGE | CZ01 | 0.035233
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ02 | AsmNewPGE | CZ02 | 0.2687
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ03 | AsmNewPGE | CZ03 | 1.0456
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ04 | AsmNewPGE | CZ04 | 0.79527
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ05 | AsmNewPGE | CZ05 | 0.095
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ06 | AsmNewPGE | CZ06 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ07 | AsmNewPGE | CZ07 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ08 | AsmNewPGE | CZ08 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ09 | AsmNewPGE | CZ09 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ10 | AsmNewPGE | CZ10 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ11 | AsmNewPGE | CZ11 | 0.32423
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ12 | AsmNewPGE | CZ12 | 1.0404
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ13 | AsmNewPGE | CZ13 | 0.76687
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ14 | AsmNewPGE | CZ14 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ15 | AsmNewPGE | CZ15 | 0
ComIOUterr | AsmNewPGE | IOU | Any | PGE | Asm | New | Multiple | Any | AsmNewPGECZ16 | AsmNewPGE | CZ16 | 0.061667
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ01 | EPrNewPGE | CZ01 | 0.0176
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ02 | EPrNewPGE | CZ02 | 0.10477
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ03 | EPrNewPGE | CZ03 | 0.3133
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ04 | EPrNewPGE | CZ04 | 0.21137
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ05 | EPrNewPGE | CZ05 | 0.029333
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ06 | EPrNewPGE | CZ06 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ07 | EPrNewPGE | CZ07 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ08 | EPrNewPGE | CZ08 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ09 | EPrNewPGE | CZ09 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ10 | EPrNewPGE | CZ10 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ11 | EPrNewPGE | CZ11 | 0.17413
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ12 | EPrNewPGE | CZ12 | 0.53493
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ13 | EPrNewPGE | CZ13 | 0.42157
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ14 | EPrNewPGE | CZ14 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ15 | EPrNewPGE | CZ15 | 0
ComIOUterr | EPrNewPGE | IOU | Any | PGE | EPr | New | Multiple | Any | EPrNewPGECZ16 | EPrNewPGE | CZ16 | 0.024267
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ01 | ESeNewPGE | CZ01 | 0.0176
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ02 | ESeNewPGE | CZ02 | 0.10477
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ03 | ESeNewPGE | CZ03 | 0.3133
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ04 | ESeNewPGE | CZ04 | 0.21137
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ05 | ESeNewPGE | CZ05 | 0.029333
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ06 | ESeNewPGE | CZ06 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ07 | ESeNewPGE | CZ07 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ08 | ESeNewPGE | CZ08 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ09 | ESeNewPGE | CZ09 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ10 | ESeNewPGE | CZ10 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ11 | ESeNewPGE | CZ11 | 0.17413
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ12 | ESeNewPGE | CZ12 | 0.53493
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ13 | ESeNewPGE | CZ13 | 0.42157
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ14 | ESeNewPGE | CZ14 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ15 | ESeNewPGE | CZ15 | 0
ComIOUterr | ESeNewPGE | IOU | Any | PGE | ESe | New | Multiple | Any | ESeNewPGECZ16 | ESeNewPGE | CZ16 | 0.024267
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ01 | ECCNewPGE | CZ01 | 0.0319
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ02 | ECCNewPGE | CZ02 | 0.1506
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ03 | ECCNewPGE | CZ03 | 0.5735
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ04 | ECCNewPGE | CZ04 | 0.20252
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ05 | ECCNewPGE | CZ05 | 0.15313
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ06 | ECCNewPGE | CZ06 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ07 | ECCNewPGE | CZ07 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ08 | ECCNewPGE | CZ08 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ09 | ECCNewPGE | CZ09 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ10 | ECCNewPGE | CZ10 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ11 | ECCNewPGE | CZ11 | 0.2328
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ12 | ECCNewPGE | CZ12 | 0.3183
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ13 | ECCNewPGE | CZ13 | 0.3514
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ14 | ECCNewPGE | CZ14 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ15 | ECCNewPGE | CZ15 | 0
ComIOUterr | ECCNewPGE | IOU | Any | PGE | ECC | New | Multiple | Any | ECCNewPGECZ16 | ECCNewPGE | CZ16 | 0.0053
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ01 | EUnNewPGE | CZ01 | 0.0319
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ02 | EUnNewPGE | CZ02 | 0.1506
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ03 | EUnNewPGE | CZ03 | 0.5735
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ04 | EUnNewPGE | CZ04 | 0.20252
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ05 | EUnNewPGE | CZ05 | 0.15313
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ06 | EUnNewPGE | CZ06 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ07 | EUnNewPGE | CZ07 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ08 | EUnNewPGE | CZ08 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ09 | EUnNewPGE | CZ09 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ10 | EUnNewPGE | CZ10 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ11 | EUnNewPGE | CZ11 | 0.2328
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ12 | EUnNewPGE | CZ12 | 0.3183
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ13 | EUnNewPGE | CZ13 | 0.3514
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ14 | EUnNewPGE | CZ14 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ15 | EUnNewPGE | CZ15 | 0
ComIOUterr | EUnNewPGE | IOU | Any | PGE | EUn | New | Multiple | Any | EUnNewPGECZ16 | EUnNewPGE | CZ16 | 0.0053
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ01 | ERCNewPGE | CZ01 | 0.0176
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ02 | ERCNewPGE | CZ02 | 0.10477
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ03 | ERCNewPGE | CZ03 | 0.3133
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ04 | ERCNewPGE | CZ04 | 0.21137
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ05 | ERCNewPGE | CZ05 | 0.029333
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ06 | ERCNewPGE | CZ06 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ07 | ERCNewPGE | CZ07 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ08 | ERCNewPGE | CZ08 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ09 | ERCNewPGE | CZ09 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ10 | ERCNewPGE | CZ10 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ11 | ERCNewPGE | CZ11 | 0.17413
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ12 | ERCNewPGE | CZ12 | 0.53493
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ13 | ERCNewPGE | CZ13 | 0.42157
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ14 | ERCNewPGE | CZ14 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ15 | ERCNewPGE | CZ15 | 0
ComIOUterr | ERCNewPGE | IOU | Any | PGE | ERC | New | Multiple | Any | ERCNewPGECZ16 | ERCNewPGE | CZ16 | 0.024267
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ01 | GroNewPGE | CZ01 | 0.0347
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ02 | GroNewPGE | CZ02 | 0.2722
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ03 | GroNewPGE | CZ03 | 0.8736
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ04 | GroNewPGE | CZ04 | 0.43833
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ05 | GroNewPGE | CZ05 | 0.09937
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ06 | GroNewPGE | CZ06 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ07 | GroNewPGE | CZ07 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ08 | GroNewPGE | CZ08 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ09 | GroNewPGE | CZ09 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ10 | GroNewPGE | CZ10 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ11 | GroNewPGE | CZ11 | 0.3813
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ12 | GroNewPGE | CZ12 | 1.0839
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ13 | GroNewPGE | CZ13 | 0.8755
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ14 | GroNewPGE | CZ14 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ15 | GroNewPGE | CZ15 | 0
ComIOUterr | GroNewPGE | IOU | Any | PGE | Gro | New | Multiple | Any | GroNewPGECZ16 | GroNewPGE | CZ16 | 0.0577
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ01 | HspNewPGE | CZ01 | 0.022
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ02 | HspNewPGE | CZ02 | 0.2133
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ03 | HspNewPGE | CZ03 | 0.5822
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ04 | HspNewPGE | CZ04 | 0.29791
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ05 | HspNewPGE | CZ05 | 0.04534
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ06 | HspNewPGE | CZ06 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ07 | HspNewPGE | CZ07 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ08 | HspNewPGE | CZ08 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ09 | HspNewPGE | CZ09 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ10 | HspNewPGE | CZ10 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ11 | HspNewPGE | CZ11 | 0.17985
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ12 | HspNewPGE | CZ12 | 0.5935
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ13 | HspNewPGE | CZ13 | 0.46655
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ14 | HspNewPGE | CZ14 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ15 | HspNewPGE | CZ15 | 0
ComIOUterr | HspNewPGE | IOU | Any | PGE | Hsp | New | Multiple | Any | HspNewPGECZ16 | HspNewPGE | CZ16 | 0.0087
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ01 | NrsNewPGE | CZ01 | 0.022
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ02 | NrsNewPGE | CZ02 | 0.2133
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ03 | NrsNewPGE | CZ03 | 0.5822
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ04 | NrsNewPGE | CZ04 | 0.29791
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ05 | NrsNewPGE | CZ05 | 0.04534
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ06 | NrsNewPGE | CZ06 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ07 | NrsNewPGE | CZ07 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ08 | NrsNewPGE | CZ08 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ09 | NrsNewPGE | CZ09 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ10 | NrsNewPGE | CZ10 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ11 | NrsNewPGE | CZ11 | 0.17985
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ12 | NrsNewPGE | CZ12 | 0.5935
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ13 | NrsNewPGE | CZ13 | 0.46655
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ14 | NrsNewPGE | CZ14 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ15 | NrsNewPGE | CZ15 | 0
ComIOUterr | NrsNewPGE | IOU | Any | PGE | Nrs | New | Multiple | Any | NrsNewPGECZ16 | NrsNewPGE | CZ16 | 0.0087
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ01 | HtlNewPGE | CZ01 | 0.03815
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ02 | HtlNewPGE | CZ02 | 0.1676
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ03 | HtlNewPGE | CZ03 | 0.50165
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ04 | HtlNewPGE | CZ04 | 0.37215
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ05 | HtlNewPGE | CZ05 | 0.15605
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ06 | HtlNewPGE | CZ06 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ07 | HtlNewPGE | CZ07 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ08 | HtlNewPGE | CZ08 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ09 | HtlNewPGE | CZ09 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ10 | HtlNewPGE | CZ10 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ11 | HtlNewPGE | CZ11 | 0.10965
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ12 | HtlNewPGE | CZ12 | 0.4217
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ13 | HtlNewPGE | CZ13 | 0.23115
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ14 | HtlNewPGE | CZ14 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ15 | HtlNewPGE | CZ15 | 0
ComIOUterr | HtlNewPGE | IOU | Any | PGE | Htl | New | Multiple | Any | HtlNewPGECZ16 | HtlNewPGE | CZ16 | 0.04325
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ01 | MtlNewPGE | CZ01 | 0.03815
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ02 | MtlNewPGE | CZ02 | 0.1676
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ03 | MtlNewPGE | CZ03 | 0.50165
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ04 | MtlNewPGE | CZ04 | 0.37215
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ05 | MtlNewPGE | CZ05 | 0.15605
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ06 | MtlNewPGE | CZ06 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ07 | MtlNewPGE | CZ07 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ08 | MtlNewPGE | CZ08 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ09 | MtlNewPGE | CZ09 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ10 | MtlNewPGE | CZ10 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ11 | MtlNewPGE | CZ11 | 0.10965
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ12 | MtlNewPGE | CZ12 | 0.4217
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ13 | MtlNewPGE | CZ13 | 0.23115
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ14 | MtlNewPGE | CZ14 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ15 | MtlNewPGE | CZ15 | 0
ComIOUterr | MtlNewPGE | IOU | Any | PGE | Mtl | New | Multiple | Any | MtlNewPGECZ16 | MtlNewPGE | CZ16 | 0.04325
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ01 | MBTNewPGE | CZ01 | 0.035233
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ02 | MBTNewPGE | CZ02 | 0.2687
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ03 | MBTNewPGE | CZ03 | 1.0456
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ04 | MBTNewPGE | CZ04 | 0.79527
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ05 | MBTNewPGE | CZ05 | 0.095
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ06 | MBTNewPGE | CZ06 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ07 | MBTNewPGE | CZ07 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ08 | MBTNewPGE | CZ08 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ09 | MBTNewPGE | CZ09 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ10 | MBTNewPGE | CZ10 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ11 | MBTNewPGE | CZ11 | 0.32423
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ12 | MBTNewPGE | CZ12 | 1.0404
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ13 | MBTNewPGE | CZ13 | 0.76687
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ14 | MBTNewPGE | CZ14 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ15 | MBTNewPGE | CZ15 | 0
ComIOUterr | MBTNewPGE | IOU | Any | PGE | MBT | New | Multiple | Any | MBTNewPGECZ16 | MBTNewPGE | CZ16 | 0.061667
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ01 | MLINewPGE | CZ01 | 0.035233
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ02 | MLINewPGE | CZ02 | 0.2687
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ03 | MLINewPGE | CZ03 | 1.0456
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ04 | MLINewPGE | CZ04 | 0.79527
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ05 | MLINewPGE | CZ05 | 0.095
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ06 | MLINewPGE | CZ06 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ07 | MLINewPGE | CZ07 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ08 | MLINewPGE | CZ08 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ09 | MLINewPGE | CZ09 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ10 | MLINewPGE | CZ10 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ11 | MLINewPGE | CZ11 | 0.32423
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ12 | MLINewPGE | CZ12 | 1.0404
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ13 | MLINewPGE | CZ13 | 0.76687
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ14 | MLINewPGE | CZ14 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ15 | MLINewPGE | CZ15 | 0
ComIOUterr | MLINewPGE | IOU | Any | PGE | MLI | New | Multiple | Any | MLINewPGECZ16 | MLINewPGE | CZ16 | 0.061667
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ01 | OfLNewPGE | CZ01 | 0.0482
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ02 | OfLNewPGE | CZ02 | 0.7101
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ03 | OfLNewPGE | CZ03 | 6.4925
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ04 | OfLNewPGE | CZ04 | 3.6099
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ05 | OfLNewPGE | CZ05 | 0.2538
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ06 | OfLNewPGE | CZ06 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ07 | OfLNewPGE | CZ07 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ08 | OfLNewPGE | CZ08 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ09 | OfLNewPGE | CZ09 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ10 | OfLNewPGE | CZ10 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ11 | OfLNewPGE | CZ11 | 0.4104
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ12 | OfLNewPGE | CZ12 | 3.3869
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ13 | OfLNewPGE | CZ13 | 1.3971
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ14 | OfLNewPGE | CZ14 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ15 | OfLNewPGE | CZ15 | 0
ComIOUterr | OfLNewPGE | IOU | Any | PGE | OfL | New | Multiple | Any | OfLNewPGECZ16 | OfLNewPGE | CZ16 | 0.0346
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ01 | OfSNewPGE | CZ01 | 0.0704
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ02 | OfSNewPGE | CZ02 | 0.1989
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ03 | OfSNewPGE | CZ03 | 1.2048
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ04 | OfSNewPGE | CZ04 | 0.9704
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ05 | OfSNewPGE | CZ05 | 0.0683
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ06 | OfSNewPGE | CZ06 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ07 | OfSNewPGE | CZ07 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ08 | OfSNewPGE | CZ08 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ09 | OfSNewPGE | CZ09 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ10 | OfSNewPGE | CZ10 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ11 | OfSNewPGE | CZ11 | 0.2998
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ12 | OfSNewPGE | CZ12 | 1.2485
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ13 | OfSNewPGE | CZ13 | 1.0654
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ14 | OfSNewPGE | CZ14 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ15 | OfSNewPGE | CZ15 | 0
ComIOUterr | OfSNewPGE | IOU | Any | PGE | OfS | New | Multiple | Any | OfSNewPGECZ16 | OfSNewPGE | CZ16 | 0.0374
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ01 | RSDNewPGE | CZ01 | 0.00665
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ02 | RSDNewPGE | CZ02 | 0.03805
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ03 | RSDNewPGE | CZ03 | 0.19175
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ04 | RSDNewPGE | CZ04 | 0.076675
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ05 | RSDNewPGE | CZ05 | 0.015045
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ06 | RSDNewPGE | CZ06 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ07 | RSDNewPGE | CZ07 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ08 | RSDNewPGE | CZ08 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ09 | RSDNewPGE | CZ09 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ10 | RSDNewPGE | CZ10 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ11 | RSDNewPGE | CZ11 | 0.03925
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ12 | RSDNewPGE | CZ12 | 0.13865
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ13 | RSDNewPGE | CZ13 | 0.0959
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ14 | RSDNewPGE | CZ14 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ15 | RSDNewPGE | CZ15 | 0
ComIOUterr | RSDNewPGE | IOU | Any | PGE | RSD | New | Multiple | Any | RSDNewPGECZ16 | RSDNewPGE | CZ16 | 0.0072
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ01 | RFFNewPGE | CZ01 | 0.00665
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ02 | RFFNewPGE | CZ02 | 0.03805
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ03 | RFFNewPGE | CZ03 | 0.19175
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ04 | RFFNewPGE | CZ04 | 0.076675
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ05 | RFFNewPGE | CZ05 | 0.015045
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ06 | RFFNewPGE | CZ06 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ07 | RFFNewPGE | CZ07 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ08 | RFFNewPGE | CZ08 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ09 | RFFNewPGE | CZ09 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ10 | RFFNewPGE | CZ10 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ11 | RFFNewPGE | CZ11 | 0.03925
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ12 | RFFNewPGE | CZ12 | 0.13865
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ13 | RFFNewPGE | CZ13 | 0.0959
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ14 | RFFNewPGE | CZ14 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ15 | RFFNewPGE | CZ15 | 0
ComIOUterr | RFFNewPGE | IOU | Any | PGE | RFF | New | Multiple | Any | RFFNewPGECZ16 | RFFNewPGE | CZ16 | 0.0072
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ01 | Rt3NewPGE | CZ01 | 0.039633
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ02 | Rt3NewPGE | CZ02 | 0.28533
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ03 | Rt3NewPGE | CZ03 | 1.2201
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ04 | Rt3NewPGE | CZ04 | 0.60113
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ05 | Rt3NewPGE | CZ05 | 0.10377
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ06 | Rt3NewPGE | CZ06 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ07 | Rt3NewPGE | CZ07 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ08 | Rt3NewPGE | CZ08 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ09 | Rt3NewPGE | CZ09 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ10 | Rt3NewPGE | CZ10 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ11 | Rt3NewPGE | CZ11 | 0.3246
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ12 | Rt3NewPGE | CZ12 | 1.2358
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ13 | Rt3NewPGE | CZ13 | 0.8523
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ14 | Rt3NewPGE | CZ14 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ15 | Rt3NewPGE | CZ15 | 0
ComIOUterr | Rt3NewPGE | IOU | Any | PGE | Rt3 | New | Multiple | Any | Rt3NewPGECZ16 | Rt3NewPGE | CZ16 | 0.015367
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ01 | RtLNewPGE | CZ01 | 0.039633
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ02 | RtLNewPGE | CZ02 | 0.28533
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ03 | RtLNewPGE | CZ03 | 1.2201
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ04 | RtLNewPGE | CZ04 | 0.60113
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ05 | RtLNewPGE | CZ05 | 0.10377
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ06 | RtLNewPGE | CZ06 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ07 | RtLNewPGE | CZ07 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ08 | RtLNewPGE | CZ08 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ09 | RtLNewPGE | CZ09 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ10 | RtLNewPGE | CZ10 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ11 | RtLNewPGE | CZ11 | 0.3246
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ12 | RtLNewPGE | CZ12 | 1.2358
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ13 | RtLNewPGE | CZ13 | 0.8523
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ14 | RtLNewPGE | CZ14 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ15 | RtLNewPGE | CZ15 | 0
ComIOUterr | RtLNewPGE | IOU | Any | PGE | RtL | New | Multiple | Any | RtLNewPGECZ16 | RtLNewPGE | CZ16 | 0.015367
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ01 | RtSNewPGE | CZ01 | 0.039633
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ02 | RtSNewPGE | CZ02 | 0.28533
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ03 | RtSNewPGE | CZ03 | 1.2201
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ04 | RtSNewPGE | CZ04 | 0.60113
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ05 | RtSNewPGE | CZ05 | 0.10377
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ06 | RtSNewPGE | CZ06 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ07 | RtSNewPGE | CZ07 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ08 | RtSNewPGE | CZ08 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ09 | RtSNewPGE | CZ09 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ10 | RtSNewPGE | CZ10 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ11 | RtSNewPGE | CZ11 | 0.3246
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ12 | RtSNewPGE | CZ12 | 1.2358
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ13 | RtSNewPGE | CZ13 | 0.8523
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ14 | RtSNewPGE | CZ14 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ15 | RtSNewPGE | CZ15 | 0
ComIOUterr | RtSNewPGE | IOU | Any | PGE | RtS | New | Multiple | Any | RtSNewPGECZ16 | RtSNewPGE | CZ16 | 0.015367
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ01 | SCnNewPGE | CZ01 | 0.0603
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ02 | SCnNewPGE | CZ02 | 0.35505
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ03 | SCnNewPGE | CZ03 | 1.8681
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ04 | SCnNewPGE | CZ04 | 0.68025
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ05 | SCnNewPGE | CZ05 | 0.05165
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ06 | SCnNewPGE | CZ06 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ07 | SCnNewPGE | CZ07 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ08 | SCnNewPGE | CZ08 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ09 | SCnNewPGE | CZ09 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ10 | SCnNewPGE | CZ10 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ11 | SCnNewPGE | CZ11 | 0.6836
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ12 | SCnNewPGE | CZ12 | 2.5873
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ13 | SCnNewPGE | CZ13 | 1.5846
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ14 | SCnNewPGE | CZ14 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ15 | SCnNewPGE | CZ15 | 0
ComIOUterr | SCnNewPGE | IOU | Any | PGE | SCn | New | Multiple | Any | SCnNewPGECZ16 | SCnNewPGE | CZ16 | 0.07795
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ01 | SUnNewPGE | CZ01 | 0.0603
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ02 | SUnNewPGE | CZ02 | 0.35505
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ03 | SUnNewPGE | CZ03 | 1.8681
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ04 | SUnNewPGE | CZ04 | 0.68025
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ05 | SUnNewPGE | CZ05 | 0.05165
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ06 | SUnNewPGE | CZ06 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ07 | SUnNewPGE | CZ07 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ08 | SUnNewPGE | CZ08 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ09 | SUnNewPGE | CZ09 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ10 | SUnNewPGE | CZ10 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ11 | SUnNewPGE | CZ11 | 0.6836
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ12 | SUnNewPGE | CZ12 | 2.5873
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ13 | SUnNewPGE | CZ13 | 1.5846
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ14 | SUnNewPGE | CZ14 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ15 | SUnNewPGE | CZ15 | 0
ComIOUterr | SUnNewPGE | IOU | Any | PGE | SUn | New | Multiple | Any | SUnNewPGECZ16 | SUnNewPGE | CZ16 | 0.07795
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ01 | WRfNewPGE | CZ01 | 0.00644
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ02 | WRfNewPGE | CZ02 | 0.03398
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ03 | WRfNewPGE | CZ03 | 0.36751
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ04 | WRfNewPGE | CZ04 | 0.06702
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ05 | WRfNewPGE | CZ05 | 0.0394
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ06 | WRfNewPGE | CZ06 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ07 | WRfNewPGE | CZ07 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ08 | WRfNewPGE | CZ08 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ09 | WRfNewPGE | CZ09 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ10 | WRfNewPGE | CZ10 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ11 | WRfNewPGE | CZ11 | 0.09113
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ12 | WRfNewPGE | CZ12 | 0.52793
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ13 | WRfNewPGE | CZ13 | 0.55314
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ14 | WRfNewPGE | CZ14 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ15 | WRfNewPGE | CZ15 | 0
ComIOUterr | WRfNewPGE | IOU | Any | PGE | WRf | New | Multiple | Any | WRfNewPGECZ16 | WRfNewPGE | CZ16 | 0.00082
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ01 | AsmExSCE | CZ01 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ02 | AsmExSCE | CZ02 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ03 | AsmExSCE | CZ03 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ04 | AsmExSCE | CZ04 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ05 | AsmExSCE | CZ05 | 0.43187
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ06 | AsmExSCE | CZ06 | 36.3075
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ07 | AsmExSCE | CZ07 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ08 | AsmExSCE | CZ08 | 52.9964
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ09 | AsmExSCE | CZ09 | 24.7926
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ10 | AsmExSCE | CZ10 | 27.1921
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ11 | AsmExSCE | CZ11 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ12 | AsmExSCE | CZ12 | 0
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ13 | AsmExSCE | CZ13 | 3.4588
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ14 | AsmExSCE | CZ14 | 6.3093
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ15 | AsmExSCE | CZ15 | 9.843
ComIOUterr | AsmExSCE | IOU | SCE | SCE | Asm | Ex | Multiple | Any | AsmExSCECZ16 | AsmExSCE | CZ16 | 3.6908
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ01 | EPrExSCE | CZ01 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ02 | EPrExSCE | CZ02 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ03 | EPrExSCE | CZ03 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ04 | EPrExSCE | CZ04 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ05 | EPrExSCE | CZ05 | 0.0665
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ06 | EPrExSCE | CZ06 | 11.7851
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ07 | EPrExSCE | CZ07 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ08 | EPrExSCE | CZ08 | 20.5217
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ09 | EPrExSCE | CZ09 | 10.7985
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ10 | EPrExSCE | CZ10 | 13.2453
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ11 | EPrExSCE | CZ11 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ12 | EPrExSCE | CZ12 | 0
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ13 | EPrExSCE | CZ13 | 2.689
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ14 | EPrExSCE | CZ14 | 3.4831
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ15 | EPrExSCE | CZ15 | 1.1804
ComIOUterr | EPrExSCE | IOU | SCE | SCE | EPr | Ex | Multiple | Any | EPrExSCECZ16 | EPrExSCE | CZ16 | 1.618
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ01 | ESeExSCE | CZ01 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ02 | ESeExSCE | CZ02 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ03 | ESeExSCE | CZ03 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ04 | ESeExSCE | CZ04 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ05 | ESeExSCE | CZ05 | 0.0665
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ06 | ESeExSCE | CZ06 | 11.7851
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ07 | ESeExSCE | CZ07 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ08 | ESeExSCE | CZ08 | 20.5217
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ09 | ESeExSCE | CZ09 | 10.7985
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ10 | ESeExSCE | CZ10 | 13.2453
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ11 | ESeExSCE | CZ11 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ12 | ESeExSCE | CZ12 | 0
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ13 | ESeExSCE | CZ13 | 2.689
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ14 | ESeExSCE | CZ14 | 3.4831
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ15 | ESeExSCE | CZ15 | 1.1804
ComIOUterr | ESeExSCE | IOU | SCE | SCE | ESe | Ex | Multiple | Any | ESeExSCECZ16 | ESeExSCE | CZ16 | 1.618
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ01 | ECCExSCE | CZ01 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ02 | ECCExSCE | CZ02 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ03 | ECCExSCE | CZ03 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ04 | ECCExSCE | CZ04 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ05 | ECCExSCE | CZ05 | 0.0152
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ06 | ECCExSCE | CZ06 | 12.7884
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ07 | ECCExSCE | CZ07 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ08 | ECCExSCE | CZ08 | 20.6788
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ09 | ECCExSCE | CZ09 | 4.5456
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ10 | ECCExSCE | CZ10 | 5.9322
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ11 | ECCExSCE | CZ11 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ12 | ECCExSCE | CZ12 | 0
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ13 | ECCExSCE | CZ13 | 1.1944
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ14 | ECCExSCE | CZ14 | 2.0935
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ15 | ECCExSCE | CZ15 | 1.7264
ComIOUterr | ECCExSCE | IOU | SCE | SCE | ECC | Ex | Multiple | Any | ECCExSCECZ16 | ECCExSCE | CZ16 | 3.8559
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ01 | EUnExSCE | CZ01 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ02 | EUnExSCE | CZ02 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ03 | EUnExSCE | CZ03 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ04 | EUnExSCE | CZ04 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ05 | EUnExSCE | CZ05 | 0.0152
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ06 | EUnExSCE | CZ06 | 12.7884
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ07 | EUnExSCE | CZ07 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ08 | EUnExSCE | CZ08 | 20.6788
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ09 | EUnExSCE | CZ09 | 4.5456
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ10 | EUnExSCE | CZ10 | 5.9322
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ11 | EUnExSCE | CZ11 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ12 | EUnExSCE | CZ12 | 0
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ13 | EUnExSCE | CZ13 | 1.1944
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ14 | EUnExSCE | CZ14 | 2.0935
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ15 | EUnExSCE | CZ15 | 1.7264
ComIOUterr | EUnExSCE | IOU | SCE | SCE | EUn | Ex | Multiple | Any | EUnExSCECZ16 | EUnExSCE | CZ16 | 3.8559
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ01 | ERCExSCE | CZ01 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ02 | ERCExSCE | CZ02 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ03 | ERCExSCE | CZ03 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ04 | ERCExSCE | CZ04 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ05 | ERCExSCE | CZ05 | 0.0665
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ06 | ERCExSCE | CZ06 | 11.7851
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ07 | ERCExSCE | CZ07 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ08 | ERCExSCE | CZ08 | 20.5217
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ09 | ERCExSCE | CZ09 | 10.7985
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ10 | ERCExSCE | CZ10 | 13.2453
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ11 | ERCExSCE | CZ11 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ12 | ERCExSCE | CZ12 | 0
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ13 | ERCExSCE | CZ13 | 2.689
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ14 | ERCExSCE | CZ14 | 3.4831
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ15 | ERCExSCE | CZ15 | 1.1804
ComIOUterr | ERCExSCE | IOU | SCE | SCE | ERC | Ex | Multiple | Any | ERCExSCECZ16 | ERCExSCE | CZ16 | 1.618
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ01 | GroExSCE | CZ01 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ02 | GroExSCE | CZ02 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ03 | GroExSCE | CZ03 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ04 | GroExSCE | CZ04 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ05 | GroExSCE | CZ05 | 0.4567
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ06 | GroExSCE | CZ06 | 22.7954
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ07 | GroExSCE | CZ07 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ08 | GroExSCE | CZ08 | 33.4574
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ09 | GroExSCE | CZ09 | 15.4115
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ10 | GroExSCE | CZ10 | 23.7779
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ11 | GroExSCE | CZ11 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ12 | GroExSCE | CZ12 | 0
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ13 | GroExSCE | CZ13 | 3.4644
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ14 | GroExSCE | CZ14 | 5.7258
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ15 | GroExSCE | CZ15 | 3.3432
ComIOUterr | GroExSCE | IOU | SCE | SCE | Gro | Ex | Multiple | Any | GroExSCECZ16 | GroExSCE | CZ16 | 2.2903
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ01 | HspExSCE | CZ01 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ02 | HspExSCE | CZ02 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ03 | HspExSCE | CZ03 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ04 | HspExSCE | CZ04 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ05 | HspExSCE | CZ05 | 0.95435
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ06 | HspExSCE | CZ06 | 14.2056
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ07 | HspExSCE | CZ07 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ08 | HspExSCE | CZ08 | 15.1282
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ09 | HspExSCE | CZ09 | 7.5672
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ10 | HspExSCE | CZ10 | 7.9053
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ11 | HspExSCE | CZ11 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ12 | HspExSCE | CZ12 | 0
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ13 | HspExSCE | CZ13 | 1.5183
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ14 | HspExSCE | CZ14 | 1.4169
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ15 | HspExSCE | CZ15 | 1.6376
ComIOUterr | HspExSCE | IOU | SCE | SCE | Hsp | Ex | Multiple | Any | HspExSCECZ16 | HspExSCE | CZ16 | 1.0455
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ01 | NrsExSCE | CZ01 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ02 | NrsExSCE | CZ02 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ03 | NrsExSCE | CZ03 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ04 | NrsExSCE | CZ04 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ05 | NrsExSCE | CZ05 | 0.95435
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ06 | NrsExSCE | CZ06 | 14.2056
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ07 | NrsExSCE | CZ07 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ08 | NrsExSCE | CZ08 | 15.1282
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ09 | NrsExSCE | CZ09 | 7.5672
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ10 | NrsExSCE | CZ10 | 7.9053
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ11 | NrsExSCE | CZ11 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ12 | NrsExSCE | CZ12 | 0
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ13 | NrsExSCE | CZ13 | 1.5183
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ14 | NrsExSCE | CZ14 | 1.4169
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ15 | NrsExSCE | CZ15 | 1.6376
ComIOUterr | NrsExSCE | IOU | SCE | SCE | Nrs | Ex | Multiple | Any | NrsExSCECZ16 | NrsExSCE | CZ16 | 1.0455
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ01 | HtlExSCE | CZ01 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ02 | HtlExSCE | CZ02 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ03 | HtlExSCE | CZ03 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ04 | HtlExSCE | CZ04 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ05 | HtlExSCE | CZ05 | 0.15065
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ06 | HtlExSCE | CZ06 | 17.6298
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ07 | HtlExSCE | CZ07 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ08 | HtlExSCE | CZ08 | 11.3624
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ09 | HtlExSCE | CZ09 | 8.2035
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ10 | HtlExSCE | CZ10 | 2.7843
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ11 | HtlExSCE | CZ11 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ12 | HtlExSCE | CZ12 | 0
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ13 | HtlExSCE | CZ13 | 0.5345
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ14 | HtlExSCE | CZ14 | 1.3728
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ15 | HtlExSCE | CZ15 | 7.1212
ComIOUterr | HtlExSCE | IOU | SCE | SCE | Htl | Ex | Multiple | Any | HtlExSCECZ16 | HtlExSCE | CZ16 | 1.87
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ01 | MtlExSCE | CZ01 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ02 | MtlExSCE | CZ02 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ03 | MtlExSCE | CZ03 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ04 | MtlExSCE | CZ04 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ05 | MtlExSCE | CZ05 | 0.15065
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ06 | MtlExSCE | CZ06 | 17.6298
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ07 | MtlExSCE | CZ07 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ08 | MtlExSCE | CZ08 | 11.3624
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ09 | MtlExSCE | CZ09 | 8.2035
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ10 | MtlExSCE | CZ10 | 2.7843
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ11 | MtlExSCE | CZ11 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ12 | MtlExSCE | CZ12 | 0
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ13 | MtlExSCE | CZ13 | 0.5345
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ14 | MtlExSCE | CZ14 | 1.3728
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ15 | MtlExSCE | CZ15 | 7.1212
ComIOUterr | MtlExSCE | IOU | SCE | SCE | Mtl | Ex | Multiple | Any | MtlExSCECZ16 | MtlExSCE | CZ16 | 1.87
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ01 | MBTExSCE | CZ01 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ02 | MBTExSCE | CZ02 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ03 | MBTExSCE | CZ03 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ04 | MBTExSCE | CZ04 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ05 | MBTExSCE | CZ05 | 0.43187
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ06 | MBTExSCE | CZ06 | 36.3075
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ07 | MBTExSCE | CZ07 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ08 | MBTExSCE | CZ08 | 52.9964
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ09 | MBTExSCE | CZ09 | 24.7926
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ10 | MBTExSCE | CZ10 | 27.1921
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ11 | MBTExSCE | CZ11 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ12 | MBTExSCE | CZ12 | 0
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ13 | MBTExSCE | CZ13 | 3.4588
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ14 | MBTExSCE | CZ14 | 6.3093
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ15 | MBTExSCE | CZ15 | 9.843
ComIOUterr | MBTExSCE | IOU | SCE | SCE | MBT | Ex | Multiple | Any | MBTExSCECZ16 | MBTExSCE | CZ16 | 3.6908
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ01 | MLIExSCE | CZ01 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ02 | MLIExSCE | CZ02 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ03 | MLIExSCE | CZ03 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ04 | MLIExSCE | CZ04 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ05 | MLIExSCE | CZ05 | 0.43187
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ06 | MLIExSCE | CZ06 | 36.3075
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ07 | MLIExSCE | CZ07 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ08 | MLIExSCE | CZ08 | 52.9964
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ09 | MLIExSCE | CZ09 | 24.7926
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ10 | MLIExSCE | CZ10 | 27.1921
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ11 | MLIExSCE | CZ11 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ12 | MLIExSCE | CZ12 | 0
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ13 | MLIExSCE | CZ13 | 3.4588
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ14 | MLIExSCE | CZ14 | 6.3093
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ15 | MLIExSCE | CZ15 | 9.843
ComIOUterr | MLIExSCE | IOU | SCE | SCE | MLI | Ex | Multiple | Any | MLIExSCECZ16 | MLIExSCE | CZ16 | 3.6908
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ01 | OfLExSCE | CZ01 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ02 | OfLExSCE | CZ02 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ03 | OfLExSCE | CZ03 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ04 | OfLExSCE | CZ04 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ05 | OfLExSCE | CZ05 | 1.3083
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ06 | OfLExSCE | CZ06 | 117.1113
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ07 | OfLExSCE | CZ07 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ08 | OfLExSCE | CZ08 | 142.3205
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ09 | OfLExSCE | CZ09 | 85.6962
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ10 | OfLExSCE | CZ10 | 32.2181
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ11 | OfLExSCE | CZ11 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ12 | OfLExSCE | CZ12 | 0
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ13 | OfLExSCE | CZ13 | 3.6548
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ14 | OfLExSCE | CZ14 | 7.4876
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ15 | OfLExSCE | CZ15 | 8.8041
ComIOUterr | OfLExSCE | IOU | SCE | SCE | OfL | Ex | Multiple | Any | OfLExSCECZ16 | OfLExSCE | CZ16 | 3.4486
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ01 | OfSExSCE | CZ01 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ02 | OfSExSCE | CZ02 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ03 | OfSExSCE | CZ03 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ04 | OfSExSCE | CZ04 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ05 | OfSExSCE | CZ05 | 0.3105
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ06 | OfSExSCE | CZ06 | 26.9101
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ07 | OfSExSCE | CZ07 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ08 | OfSExSCE | CZ08 | 32.4968
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ09 | OfSExSCE | CZ09 | 17.1719
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ10 | OfSExSCE | CZ10 | 24.8649
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ11 | OfSExSCE | CZ11 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ12 | OfSExSCE | CZ12 | 0
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ13 | OfSExSCE | CZ13 | 5.7207
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ14 | OfSExSCE | CZ14 | 3.5403
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ15 | OfSExSCE | CZ15 | 6.7948
ComIOUterr | OfSExSCE | IOU | SCE | SCE | OfS | Ex | Multiple | Any | OfSExSCECZ16 | OfSExSCE | CZ16 | 2.0179
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ01 | RSDExSCE | CZ01 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ02 | RSDExSCE | CZ02 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ03 | RSDExSCE | CZ03 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ04 | RSDExSCE | CZ04 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ05 | RSDExSCE | CZ05 | 0.13278
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ06 | RSDExSCE | CZ06 | 9.1684
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ07 | RSDExSCE | CZ07 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ08 | RSDExSCE | CZ08 | 10.5495
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ09 | RSDExSCE | CZ09 | 5.8953
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ10 | RSDExSCE | CZ10 | 9.0972
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ11 | RSDExSCE | CZ11 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ12 | RSDExSCE | CZ12 | 0
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ13 | RSDExSCE | CZ13 | 0.73034
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ14 | RSDExSCE | CZ14 | 1.9086
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ15 | RSDExSCE | CZ15 | 1.7798
ComIOUterr | RSDExSCE | IOU | SCE | SCE | RSD | Ex | Multiple | Any | RSDExSCECZ16 | RSDExSCE | CZ16 | 0.73716
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ01 | RFFExSCE | CZ01 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ02 | RFFExSCE | CZ02 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ03 | RFFExSCE | CZ03 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ04 | RFFExSCE | CZ04 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ05 | RFFExSCE | CZ05 | 0.13278
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ06 | RFFExSCE | CZ06 | 9.1684
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ07 | RFFExSCE | CZ07 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ08 | RFFExSCE | CZ08 | 10.5495
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ09 | RFFExSCE | CZ09 | 5.8953
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ10 | RFFExSCE | CZ10 | 9.0972
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ11 | RFFExSCE | CZ11 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ12 | RFFExSCE | CZ12 | 0
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ13 | RFFExSCE | CZ13 | 0.73034
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ14 | RFFExSCE | CZ14 | 1.9086
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ15 | RFFExSCE | CZ15 | 1.7798
ComIOUterr | RFFExSCE | IOU | SCE | SCE | RFF | Ex | Multiple | Any | RFFExSCECZ16 | RFFExSCE | CZ16 | 0.73716
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ01 | Rt3ExSCE | CZ01 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ02 | Rt3ExSCE | CZ02 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ03 | Rt3ExSCE | CZ03 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ04 | Rt3ExSCE | CZ04 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ05 | Rt3ExSCE | CZ05 | 0.63007
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ06 | Rt3ExSCE | CZ06 | 35.1278
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ07 | Rt3ExSCE | CZ07 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ08 | Rt3ExSCE | CZ08 | 39.9233
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ09 | Rt3ExSCE | CZ09 | 21.4588
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ10 | Rt3ExSCE | CZ10 | 30.9056
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ11 | Rt3ExSCE | CZ11 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ12 | Rt3ExSCE | CZ12 | 0
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ13 | Rt3ExSCE | CZ13 | 4.0005
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ14 | Rt3ExSCE | CZ14 | 5.8068
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ15 | Rt3ExSCE | CZ15 | 4.3153
ComIOUterr | Rt3ExSCE | IOU | SCE | SCE | Rt3 | Ex | Multiple | Any | Rt3ExSCECZ16 | Rt3ExSCE | CZ16 | 1.1979
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ01 | RtLExSCE | CZ01 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ02 | RtLExSCE | CZ02 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ03 | RtLExSCE | CZ03 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ04 | RtLExSCE | CZ04 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ05 | RtLExSCE | CZ05 | 0.63007
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ06 | RtLExSCE | CZ06 | 35.1278
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ07 | RtLExSCE | CZ07 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ08 | RtLExSCE | CZ08 | 39.9233
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ09 | RtLExSCE | CZ09 | 21.4588
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ10 | RtLExSCE | CZ10 | 30.9056
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ11 | RtLExSCE | CZ11 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ12 | RtLExSCE | CZ12 | 0
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ13 | RtLExSCE | CZ13 | 4.0005
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ14 | RtLExSCE | CZ14 | 5.8068
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ15 | RtLExSCE | CZ15 | 4.3153
ComIOUterr | RtLExSCE | IOU | SCE | SCE | RtL | Ex | Multiple | Any | RtLExSCECZ16 | RtLExSCE | CZ16 | 1.1979
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ01 | RtSExSCE | CZ01 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ02 | RtSExSCE | CZ02 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ03 | RtSExSCE | CZ03 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ04 | RtSExSCE | CZ04 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ05 | RtSExSCE | CZ05 | 0.63007
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ06 | RtSExSCE | CZ06 | 35.1278
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ07 | RtSExSCE | CZ07 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ08 | RtSExSCE | CZ08 | 39.9233
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ09 | RtSExSCE | CZ09 | 21.4588
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ10 | RtSExSCE | CZ10 | 30.9056
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ11 | RtSExSCE | CZ11 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ12 | RtSExSCE | CZ12 | 0
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ13 | RtSExSCE | CZ13 | 4.0005
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ14 | RtSExSCE | CZ14 | 5.8068
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ15 | RtSExSCE | CZ15 | 4.3153
ComIOUterr | RtSExSCE | IOU | SCE | SCE | RtS | Ex | Multiple | Any | RtSExSCECZ16 | RtSExSCE | CZ16 | 1.1979
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ01 | SCnExSCE | CZ01 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ02 | SCnExSCE | CZ02 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ03 | SCnExSCE | CZ03 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ04 | SCnExSCE | CZ04 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ05 | SCnExSCE | CZ05 | 0.03265
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ06 | SCnExSCE | CZ06 | 27.9838
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ07 | SCnExSCE | CZ07 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ08 | SCnExSCE | CZ08 | 84.5766
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ09 | SCnExSCE | CZ09 | 22.022
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ10 | SCnExSCE | CZ10 | 67.8886
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ11 | SCnExSCE | CZ11 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ12 | SCnExSCE | CZ12 | 0
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ13 | SCnExSCE | CZ13 | 3.2924
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ14 | SCnExSCE | CZ14 | 1.6308
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ15 | SCnExSCE | CZ15 | 1.2471
ComIOUterr | SCnExSCE | IOU | SCE | SCE | SCn | Ex | Multiple | Any | SCnExSCECZ16 | SCnExSCE | CZ16 | 1.2978
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ01 | SUnExSCE | CZ01 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ02 | SUnExSCE | CZ02 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ03 | SUnExSCE | CZ03 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ04 | SUnExSCE | CZ04 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ05 | SUnExSCE | CZ05 | 0.03265
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ06 | SUnExSCE | CZ06 | 27.9838
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ07 | SUnExSCE | CZ07 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ08 | SUnExSCE | CZ08 | 84.5766
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ09 | SUnExSCE | CZ09 | 22.022
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ10 | SUnExSCE | CZ10 | 67.8886
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ11 | SUnExSCE | CZ11 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ12 | SUnExSCE | CZ12 | 0
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ13 | SUnExSCE | CZ13 | 3.2924
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ14 | SUnExSCE | CZ14 | 1.6308
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ15 | SUnExSCE | CZ15 | 1.2471
ComIOUterr | SUnExSCE | IOU | SCE | SCE | SUn | Ex | Multiple | Any | SUnExSCECZ16 | SUnExSCE | CZ16 | 1.2978
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ01 | WRfExSCE | CZ01 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ02 | WRfExSCE | CZ02 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ03 | WRfExSCE | CZ03 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ04 | WRfExSCE | CZ04 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ05 | WRfExSCE | CZ05 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ06 | WRfExSCE | CZ06 | 4.3608
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ07 | WRfExSCE | CZ07 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ08 | WRfExSCE | CZ08 | 5.8136
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ09 | WRfExSCE | CZ09 | 1.7034
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ10 | WRfExSCE | CZ10 | 3.2777
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ11 | WRfExSCE | CZ11 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ12 | WRfExSCE | CZ12 | 0
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ13 | WRfExSCE | CZ13 | 2.8029
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ14 | WRfExSCE | CZ14 | 0.04439
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ15 | WRfExSCE | CZ15 | 0.21278
ComIOUterr | WRfExSCE | IOU | SCE | SCE | WRf | Ex | Multiple | Any | WRfExSCECZ16 | WRfExSCE | CZ16 | 0.0587
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ01 | AsmNewSCE | CZ01 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ02 | AsmNewSCE | CZ02 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ03 | AsmNewSCE | CZ03 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ04 | AsmNewSCE | CZ04 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ05 | AsmNewSCE | CZ05 | 0.017567
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ06 | AsmNewSCE | CZ06 | 1.4671
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ07 | AsmNewSCE | CZ07 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ08 | AsmNewSCE | CZ08 | 2.1348
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ09 | AsmNewSCE | CZ09 | 0.9664
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ10 | AsmNewSCE | CZ10 | 2.9381
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ11 | AsmNewSCE | CZ11 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ12 | AsmNewSCE | CZ12 | 0
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ13 | AsmNewSCE | CZ13 | 0.223
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ14 | AsmNewSCE | CZ14 | 0.48587
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ15 | AsmNewSCE | CZ15 | 1.0635
ComIOUterr | AsmNewSCE | IOU | Any | SCE | Asm | New | Multiple | Any | AsmNewSCECZ16 | AsmNewSCE | CZ16 | 0.306
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ01 | EPrNewSCE | CZ01 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ02 | EPrNewSCE | CZ02 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ03 | EPrNewSCE | CZ03 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ04 | EPrNewSCE | CZ04 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ05 | EPrNewSCE | CZ05 | 0.0011333
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ06 | EPrNewSCE | CZ06 | 0.20437
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ07 | EPrNewSCE | CZ07 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ08 | EPrNewSCE | CZ08 | 0.3627
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ09 | EPrNewSCE | CZ09 | 0.20407
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ10 | EPrNewSCE | CZ10 | 0.5695
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ11 | EPrNewSCE | CZ11 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ12 | EPrNewSCE | CZ12 | 0
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ13 | EPrNewSCE | CZ13 | 0.12477
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ14 | EPrNewSCE | CZ14 | 0.12883
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ15 | EPrNewSCE | CZ15 | 0.050767
ComIOUterr | EPrNewSCE | IOU | Any | SCE | EPr | New | Multiple | Any | EPrNewSCECZ16 | EPrNewSCE | CZ16 | 0.0672
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ01 | ESeNewSCE | CZ01 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ02 | ESeNewSCE | CZ02 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ03 | ESeNewSCE | CZ03 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ04 | ESeNewSCE | CZ04 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ05 | ESeNewSCE | CZ05 | 0.0011333
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ06 | ESeNewSCE | CZ06 | 0.20437
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ07 | ESeNewSCE | CZ07 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ08 | ESeNewSCE | CZ08 | 0.3627
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ09 | ESeNewSCE | CZ09 | 0.20407
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ10 | ESeNewSCE | CZ10 | 0.5695
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ11 | ESeNewSCE | CZ11 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ12 | ESeNewSCE | CZ12 | 0
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ13 | ESeNewSCE | CZ13 | 0.12477
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ14 | ESeNewSCE | CZ14 | 0.12883
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ15 | ESeNewSCE | CZ15 | 0.050767
ComIOUterr | ESeNewSCE | IOU | Any | SCE | ESe | New | Multiple | Any | ESeNewSCECZ16 | ESeNewSCE | CZ16 | 0.0672
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ01 | ECCNewSCE | CZ01 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ02 | ECCNewSCE | CZ02 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ03 | ECCNewSCE | CZ03 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ04 | ECCNewSCE | CZ04 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ05 | ECCNewSCE | CZ05 | 0.0005
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ06 | ECCNewSCE | CZ06 | 0.43465
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ07 | ECCNewSCE | CZ07 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ08 | ECCNewSCE | CZ08 | 0.6893
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ09 | ECCNewSCE | CZ09 | 0.17615
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ10 | ECCNewSCE | CZ10 | 0.42155
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ11 | ECCNewSCE | CZ11 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ12 | ECCNewSCE | CZ12 | 0
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ13 | ECCNewSCE | CZ13 | 0.1116
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ14 | ECCNewSCE | CZ14 | 0.1407
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ15 | ECCNewSCE | CZ15 | 0.12265
ComIOUterr | ECCNewSCE | IOU | Any | SCE | ECC | New | Multiple | Any | ECCNewSCECZ16 | ECCNewSCE | CZ16 | 0.2769
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ01 | EUnNewSCE | CZ01 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ02 | EUnNewSCE | CZ02 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ03 | EUnNewSCE | CZ03 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ04 | EUnNewSCE | CZ04 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ05 | EUnNewSCE | CZ05 | 0.0005
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ06 | EUnNewSCE | CZ06 | 0.43465
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ07 | EUnNewSCE | CZ07 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ08 | EUnNewSCE | CZ08 | 0.6893
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ09 | EUnNewSCE | CZ09 | 0.17615
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ10 | EUnNewSCE | CZ10 | 0.42155
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ11 | EUnNewSCE | CZ11 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ12 | EUnNewSCE | CZ12 | 0
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ13 | EUnNewSCE | CZ13 | 0.1116
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ14 | EUnNewSCE | CZ14 | 0.1407
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ15 | EUnNewSCE | CZ15 | 0.12265
ComIOUterr | EUnNewSCE | IOU | Any | SCE | EUn | New | Multiple | Any | EUnNewSCECZ16 | EUnNewSCE | CZ16 | 0.2769
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ01 | ERCNewSCE | CZ01 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ02 | ERCNewSCE | CZ02 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ03 | ERCNewSCE | CZ03 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ04 | ERCNewSCE | CZ04 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ05 | ERCNewSCE | CZ05 | 0.0011333
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ06 | ERCNewSCE | CZ06 | 0.20437
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ07 | ERCNewSCE | CZ07 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ08 | ERCNewSCE | CZ08 | 0.3627
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ09 | ERCNewSCE | CZ09 | 0.20407
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ10 | ERCNewSCE | CZ10 | 0.5695
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ11 | ERCNewSCE | CZ11 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ12 | ERCNewSCE | CZ12 | 0
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ13 | ERCNewSCE | CZ13 | 0.12477
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ14 | ERCNewSCE | CZ14 | 0.12883
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ15 | ERCNewSCE | CZ15 | 0.050767
ComIOUterr | ERCNewSCE | IOU | Any | SCE | ERC | New | Multiple | Any | ERCNewSCECZ16 | ERCNewSCE | CZ16 | 0.0672
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ01 | GroNewSCE | CZ01 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ02 | GroNewSCE | CZ02 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ03 | GroNewSCE | CZ03 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ04 | GroNewSCE | CZ04 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ05 | GroNewSCE | CZ05 | 0.02
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ06 | GroNewSCE | CZ06 | 1.0043
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ07 | GroNewSCE | CZ07 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ08 | GroNewSCE | CZ08 | 1.4806
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ09 | GroNewSCE | CZ09 | 0.6988
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ10 | GroNewSCE | CZ10 | 2.0009
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ11 | GroNewSCE | CZ11 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ12 | GroNewSCE | CZ12 | 0
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ13 | GroNewSCE | CZ13 | 0.2498
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ14 | GroNewSCE | CZ14 | 0.4414
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ15 | GroNewSCE | CZ15 | 0.2813
ComIOUterr | GroNewSCE | IOU | Any | SCE | Gro | New | Multiple | Any | GroNewSCECZ16 | GroNewSCE | CZ16 | 0.1751
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ01 | HspNewSCE | CZ01 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ02 | HspNewSCE | CZ02 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ03 | HspNewSCE | CZ03 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ04 | HspNewSCE | CZ04 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ05 | HspNewSCE | CZ05 | 0.02495
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ06 | HspNewSCE | CZ06 | 0.39225
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ07 | HspNewSCE | CZ07 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ08 | HspNewSCE | CZ08 | 0.42465
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ09 | HspNewSCE | CZ09 | 0.2704
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ10 | HspNewSCE | CZ10 | 0.46295
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ11 | HspNewSCE | CZ11 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ12 | HspNewSCE | CZ12 | 0
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ13 | HspNewSCE | CZ13 | 0.0707
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ14 | HspNewSCE | CZ14 | 0.0741
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ15 | HspNewSCE | CZ15 | 0.0959
ComIOUterr | HspNewSCE | IOU | Any | SCE | Hsp | New | Multiple | Any | HspNewSCECZ16 | HspNewSCE | CZ16 | 0.05715
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ01 | NrsNewSCE | CZ01 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ02 | NrsNewSCE | CZ02 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ03 | NrsNewSCE | CZ03 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ04 | NrsNewSCE | CZ04 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ05 | NrsNewSCE | CZ05 | 0.02495
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ06 | NrsNewSCE | CZ06 | 0.39225
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ07 | NrsNewSCE | CZ07 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ08 | NrsNewSCE | CZ08 | 0.42465
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ09 | NrsNewSCE | CZ09 | 0.2704
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ10 | NrsNewSCE | CZ10 | 0.46295
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ11 | NrsNewSCE | CZ11 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ12 | NrsNewSCE | CZ12 | 0
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ13 | NrsNewSCE | CZ13 | 0.0707
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ14 | NrsNewSCE | CZ14 | 0.0741
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ15 | NrsNewSCE | CZ15 | 0.0959
ComIOUterr | NrsNewSCE | IOU | Any | SCE | Nrs | New | Multiple | Any | NrsNewSCECZ16 | NrsNewSCE | CZ16 | 0.05715
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ01 | HtlNewSCE | CZ01 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ02 | HtlNewSCE | CZ02 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ03 | HtlNewSCE | CZ03 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ04 | HtlNewSCE | CZ04 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ05 | HtlNewSCE | CZ05 | 0.00345
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ06 | HtlNewSCE | CZ06 | 0.4795
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ07 | HtlNewSCE | CZ07 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ08 | HtlNewSCE | CZ08 | 0.30255
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ09 | HtlNewSCE | CZ09 | 0.30105
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ10 | HtlNewSCE | CZ10 | 0.21475
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ11 | HtlNewSCE | CZ11 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ12 | HtlNewSCE | CZ12 | 0
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ13 | HtlNewSCE | CZ13 | 0.02975
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ14 | HtlNewSCE | CZ14 | 0.0971
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ15 | HtlNewSCE | CZ15 | 0.5492
ComIOUterr | HtlNewSCE | IOU | Any | SCE | Htl | New | Multiple | Any | HtlNewSCECZ16 | HtlNewSCE | CZ16 | 0.1157
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ01 | MtlNewSCE | CZ01 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ02 | MtlNewSCE | CZ02 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ03 | MtlNewSCE | CZ03 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ04 | MtlNewSCE | CZ04 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ05 | MtlNewSCE | CZ05 | 0.00345
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ06 | MtlNewSCE | CZ06 | 0.4795
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ07 | MtlNewSCE | CZ07 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ08 | MtlNewSCE | CZ08 | 0.30255
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ09 | MtlNewSCE | CZ09 | 0.30105
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ10 | MtlNewSCE | CZ10 | 0.21475
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ11 | MtlNewSCE | CZ11 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ12 | MtlNewSCE | CZ12 | 0
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ13 | MtlNewSCE | CZ13 | 0.02975
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ14 | MtlNewSCE | CZ14 | 0.0971
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ15 | MtlNewSCE | CZ15 | 0.5492
ComIOUterr | MtlNewSCE | IOU | Any | SCE | Mtl | New | Multiple | Any | MtlNewSCECZ16 | MtlNewSCE | CZ16 | 0.1157
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ01 | MBTNewSCE | CZ01 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ02 | MBTNewSCE | CZ02 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ03 | MBTNewSCE | CZ03 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ04 | MBTNewSCE | CZ04 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ05 | MBTNewSCE | CZ05 | 0.017567
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ06 | MBTNewSCE | CZ06 | 1.4671
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ07 | MBTNewSCE | CZ07 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ08 | MBTNewSCE | CZ08 | 2.1348
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ09 | MBTNewSCE | CZ09 | 0.9664
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ10 | MBTNewSCE | CZ10 | 2.9381
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ11 | MBTNewSCE | CZ11 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ12 | MBTNewSCE | CZ12 | 0
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ13 | MBTNewSCE | CZ13 | 0.223
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ14 | MBTNewSCE | CZ14 | 0.48587
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ15 | MBTNewSCE | CZ15 | 1.0635
ComIOUterr | MBTNewSCE | IOU | Any | SCE | MBT | New | Multiple | Any | MBTNewSCECZ16 | MBTNewSCE | CZ16 | 0.306
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ01 | MLINewSCE | CZ01 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ02 | MLINewSCE | CZ02 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ03 | MLINewSCE | CZ03 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ04 | MLINewSCE | CZ04 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ05 | MLINewSCE | CZ05 | 0.017567
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ06 | MLINewSCE | CZ06 | 1.4671
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ07 | MLINewSCE | CZ07 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ08 | MLINewSCE | CZ08 | 2.1348
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ09 | MLINewSCE | CZ09 | 0.9664
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ10 | MLINewSCE | CZ10 | 2.9381
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ11 | MLINewSCE | CZ11 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ12 | MLINewSCE | CZ12 | 0
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ13 | MLINewSCE | CZ13 | 0.223
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ14 | MLINewSCE | CZ14 | 0.48587
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ15 | MLINewSCE | CZ15 | 1.0635
ComIOUterr | MLINewSCE | IOU | Any | SCE | MLI | New | Multiple | Any | MLINewSCECZ16 | MLINewSCE | CZ16 | 0.306
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ01 | OfLNewSCE | CZ01 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ02 | OfLNewSCE | CZ02 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ03 | OfLNewSCE | CZ03 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ04 | OfLNewSCE | CZ04 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ05 | OfLNewSCE | CZ05 | 0.021
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ06 | OfLNewSCE | CZ06 | 2.16
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ07 | OfLNewSCE | CZ07 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ08 | OfLNewSCE | CZ08 | 2.6911
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ09 | OfLNewSCE | CZ09 | 2.3895
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ10 | OfLNewSCE | CZ10 | 2.1266
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ11 | OfLNewSCE | CZ11 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ12 | OfLNewSCE | CZ12 | 0
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ13 | OfLNewSCE | CZ13 | 0.1959
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ14 | OfLNewSCE | CZ14 | 0.3814
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ15 | OfLNewSCE | CZ15 | 0.5811
ComIOUterr | OfLNewSCE | IOU | Any | SCE | OfL | New | Multiple | Any | OfLNewSCECZ16 | OfLNewSCE | CZ16 | 0.1713
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ01 | OfSNewSCE | CZ01 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ02 | OfSNewSCE | CZ02 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ03 | OfSNewSCE | CZ03 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ04 | OfSNewSCE | CZ04 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ05 | OfSNewSCE | CZ05 | 0.012
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ06 | OfSNewSCE | CZ06 | 1.0387
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ07 | OfSNewSCE | CZ07 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ08 | OfSNewSCE | CZ08 | 1.2538
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ09 | OfSNewSCE | CZ09 | 0.6559
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ10 | OfSNewSCE | CZ10 | 1.5809
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ11 | OfSNewSCE | CZ11 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ12 | OfSNewSCE | CZ12 | 0
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ13 | OfSNewSCE | CZ13 | 0.2368
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ14 | OfSNewSCE | CZ14 | 0.203
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ15 | OfSNewSCE | CZ15 | 0.432
ComIOUterr | OfSNewSCE | IOU | Any | SCE | OfS | New | Multiple | Any | OfSNewSCECZ16 | OfSNewSCE | CZ16 | 0.1026
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ01 | RSDNewSCE | CZ01 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ02 | RSDNewSCE | CZ02 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ03 | RSDNewSCE | CZ03 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ04 | RSDNewSCE | CZ04 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ05 | RSDNewSCE | CZ05 | 0.007195
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ06 | RSDNewSCE | CZ06 | 0.48923
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ07 | RSDNewSCE | CZ07 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ08 | RSDNewSCE | CZ08 | 0.55199
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ09 | RSDNewSCE | CZ09 | 0.27653
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ10 | RSDNewSCE | CZ10 | 0.64264
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ11 | RSDNewSCE | CZ11 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ12 | RSDNewSCE | CZ12 | 0
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ13 | RSDNewSCE | CZ13 | 0.043635
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ14 | RSDNewSCE | CZ14 | 0.1231
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ15 | RSDNewSCE | CZ15 | 0.12574
ComIOUterr | RSDNewSCE | IOU | Any | SCE | RSD | New | Multiple | Any | RSDNewSCECZ16 | RSDNewSCE | CZ16 | 0.04724
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ01 | RFFNewSCE | CZ01 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ02 | RFFNewSCE | CZ02 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ03 | RFFNewSCE | CZ03 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ04 | RFFNewSCE | CZ04 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ05 | RFFNewSCE | CZ05 | 0.007195
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ06 | RFFNewSCE | CZ06 | 0.48923
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ07 | RFFNewSCE | CZ07 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ08 | RFFNewSCE | CZ08 | 0.55199
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ09 | RFFNewSCE | CZ09 | 0.27653
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ10 | RFFNewSCE | CZ10 | 0.64264
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ11 | RFFNewSCE | CZ11 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ12 | RFFNewSCE | CZ12 | 0
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ13 | RFFNewSCE | CZ13 | 0.043635
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ14 | RFFNewSCE | CZ14 | 0.1231
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ15 | RFFNewSCE | CZ15 | 0.12574
ComIOUterr | RFFNewSCE | IOU | Any | SCE | RFF | New | Multiple | Any | RFFNewSCECZ16 | RFFNewSCE | CZ16 | 0.04724
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ01 | Rt3NewSCE | CZ01 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ02 | Rt3NewSCE | CZ02 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ03 | Rt3NewSCE | CZ03 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ04 | Rt3NewSCE | CZ04 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ05 | Rt3NewSCE | CZ05 | 0.0288
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ06 | Rt3NewSCE | CZ06 | 1.611
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ07 | Rt3NewSCE | CZ07 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ08 | Rt3NewSCE | CZ08 | 1.8454
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ09 | Rt3NewSCE | CZ09 | 1.0207
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ10 | Rt3NewSCE | CZ10 | 2.7777
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ11 | Rt3NewSCE | CZ11 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ12 | Rt3NewSCE | CZ12 | 0
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ13 | Rt3NewSCE | CZ13 | 0.30547
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ14 | Rt3NewSCE | CZ14 | 0.43163
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ15 | Rt3NewSCE | CZ15 | 0.38783
ComIOUterr | Rt3NewSCE | IOU | Any | SCE | Rt3 | New | Multiple | Any | Rt3NewSCECZ16 | Rt3NewSCE | CZ16 | 0.092833
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ01 | RtLNewSCE | CZ01 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ02 | RtLNewSCE | CZ02 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ03 | RtLNewSCE | CZ03 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ04 | RtLNewSCE | CZ04 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ05 | RtLNewSCE | CZ05 | 0.0288
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ06 | RtLNewSCE | CZ06 | 1.611
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ07 | RtLNewSCE | CZ07 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ08 | RtLNewSCE | CZ08 | 1.8454
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ09 | RtLNewSCE | CZ09 | 1.0207
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ10 | RtLNewSCE | CZ10 | 2.7777
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ11 | RtLNewSCE | CZ11 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ12 | RtLNewSCE | CZ12 | 0
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ13 | RtLNewSCE | CZ13 | 0.30547
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ14 | RtLNewSCE | CZ14 | 0.43163
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ15 | RtLNewSCE | CZ15 | 0.38783
ComIOUterr | RtLNewSCE | IOU | Any | SCE | RtL | New | Multiple | Any | RtLNewSCECZ16 | RtLNewSCE | CZ16 | 0.092833
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ01 | RtSNewSCE | CZ01 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ02 | RtSNewSCE | CZ02 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ03 | RtSNewSCE | CZ03 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ04 | RtSNewSCE | CZ04 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ05 | RtSNewSCE | CZ05 | 0.0288
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ06 | RtSNewSCE | CZ06 | 1.611
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ07 | RtSNewSCE | CZ07 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ08 | RtSNewSCE | CZ08 | 1.8454
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ09 | RtSNewSCE | CZ09 | 1.0207
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ10 | RtSNewSCE | CZ10 | 2.7777
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ11 | RtSNewSCE | CZ11 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ12 | RtSNewSCE | CZ12 | 0
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ13 | RtSNewSCE | CZ13 | 0.30547
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ14 | RtSNewSCE | CZ14 | 0.43163
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ15 | RtSNewSCE | CZ15 | 0.38783
ComIOUterr | RtSNewSCE | IOU | Any | SCE | RtS | New | Multiple | Any | RtSNewSCECZ16 | RtSNewSCE | CZ16 | 0.092833
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ01 | SCnNewSCE | CZ01 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ02 | SCnNewSCE | CZ02 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ03 | SCnNewSCE | CZ03 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ04 | SCnNewSCE | CZ04 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ05 | SCnNewSCE | CZ05 | 0.0013
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ06 | SCnNewSCE | CZ06 | 1.1548
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ07 | SCnNewSCE | CZ07 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ08 | SCnNewSCE | CZ08 | 3.4362
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ09 | SCnNewSCE | CZ09 | 1.0423
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ10 | SCnNewSCE | CZ10 | 11.1073
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ11 | SCnNewSCE | CZ11 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ12 | SCnNewSCE | CZ12 | 0
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ13 | SCnNewSCE | CZ13 | 0.376
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ14 | SCnNewSCE | CZ14 | 0.21515
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ15 | SCnNewSCE | CZ15 | 0.20405
ComIOUterr | SCnNewSCE | IOU | Any | SCE | SCn | New | Multiple | Any | SCnNewSCECZ16 | SCnNewSCE | CZ16 | 0.20215
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ01 | SUnNewSCE | CZ01 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ02 | SUnNewSCE | CZ02 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ03 | SUnNewSCE | CZ03 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ04 | SUnNewSCE | CZ04 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ05 | SUnNewSCE | CZ05 | 0.0013
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ06 | SUnNewSCE | CZ06 | 1.1548
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ07 | SUnNewSCE | CZ07 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ08 | SUnNewSCE | CZ08 | 3.4362
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ09 | SUnNewSCE | CZ09 | 1.0423
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ10 | SUnNewSCE | CZ10 | 11.1073
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ11 | SUnNewSCE | CZ11 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ12 | SUnNewSCE | CZ12 | 0
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ13 | SUnNewSCE | CZ13 | 0.376
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ14 | SUnNewSCE | CZ14 | 0.21515
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ15 | SUnNewSCE | CZ15 | 0.20405
ComIOUterr | SUnNewSCE | IOU | Any | SCE | SUn | New | Multiple | Any | SUnNewSCECZ16 | SUnNewSCE | CZ16 | 0.20215
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ01 | WRfNewSCE | CZ01 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ02 | WRfNewSCE | CZ02 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ03 | WRfNewSCE | CZ03 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ04 | WRfNewSCE | CZ04 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ05 | WRfNewSCE | CZ05 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ06 | WRfNewSCE | CZ06 | 0.21323
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ07 | WRfNewSCE | CZ07 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ08 | WRfNewSCE | CZ08 | 0.28524
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ09 | WRfNewSCE | CZ09 | 0.09214
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ10 | WRfNewSCE | CZ10 | 0.21974
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ11 | WRfNewSCE | CZ11 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ12 | WRfNewSCE | CZ12 | 0
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ13 | WRfNewSCE | CZ13 | 0.29843
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ14 | WRfNewSCE | CZ14 | 0.0029
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ15 | WRfNewSCE | CZ15 | 0.01426
ComIOUterr | WRfNewSCE | IOU | Any | SCE | WRf | New | Multiple | Any | WRfNewSCECZ16 | WRfNewSCE | CZ16 | 0.00608
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ01 | AsmExSDG | CZ01 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ02 | AsmExSDG | CZ02 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ03 | AsmExSDG | CZ03 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ04 | AsmExSDG | CZ04 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ05 | AsmExSDG | CZ05 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ06 | AsmExSDG | CZ06 | 0.86807
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ07 | AsmExSDG | CZ07 | 16.8129
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ08 | AsmExSDG | CZ08 | 0.53257
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ09 | AsmExSDG | CZ09 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ10 | AsmExSDG | CZ10 | 8.0789
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ11 | AsmExSDG | CZ11 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ12 | AsmExSDG | CZ12 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ13 | AsmExSDG | CZ13 | 0
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ14 | AsmExSDG | CZ14 | 0.25297
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ15 | AsmExSDG | CZ15 | 0.082567
ComIOUterr | AsmExSDG | IOU | SDG | SDG | Asm | Ex | Multiple | Any | AsmExSDGCZ16 | AsmExSDG | CZ16 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ01 | EPrExSDG | CZ01 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ02 | EPrExSDG | CZ02 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ03 | EPrExSDG | CZ03 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ04 | EPrExSDG | CZ04 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ05 | EPrExSDG | CZ05 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ06 | EPrExSDG | CZ06 | 0.68783
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ07 | EPrExSDG | CZ07 | 7.8963
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ08 | EPrExSDG | CZ08 | 0.77677
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ09 | EPrExSDG | CZ09 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ10 | EPrExSDG | CZ10 | 4.5999
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ11 | EPrExSDG | CZ11 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ12 | EPrExSDG | CZ12 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ13 | EPrExSDG | CZ13 | 0
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ14 | EPrExSDG | CZ14 | 0.12563
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ15 | EPrExSDG | CZ15 | 0.033933
ComIOUterr | EPrExSDG | IOU | SDG | SDG | EPr | Ex | Multiple | Any | EPrExSDGCZ16 | EPrExSDG | CZ16 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ01 | ESeExSDG | CZ01 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ02 | ESeExSDG | CZ02 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ03 | ESeExSDG | CZ03 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ04 | ESeExSDG | CZ04 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ05 | ESeExSDG | CZ05 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ06 | ESeExSDG | CZ06 | 0.68783
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ07 | ESeExSDG | CZ07 | 7.8963
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ08 | ESeExSDG | CZ08 | 0.77677
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ09 | ESeExSDG | CZ09 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ10 | ESeExSDG | CZ10 | 4.5999
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ11 | ESeExSDG | CZ11 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ12 | ESeExSDG | CZ12 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ13 | ESeExSDG | CZ13 | 0
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ14 | ESeExSDG | CZ14 | 0.12563
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ15 | ESeExSDG | CZ15 | 0.033933
ComIOUterr | ESeExSDG | IOU | SDG | SDG | ESe | Ex | Multiple | Any | ESeExSDGCZ16 | ESeExSDG | CZ16 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ01 | ECCExSDG | CZ01 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ02 | ECCExSDG | CZ02 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ03 | ECCExSDG | CZ03 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ04 | ECCExSDG | CZ04 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ05 | ECCExSDG | CZ05 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ06 | ECCExSDG | CZ06 | 0.07403
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ07 | ECCExSDG | CZ07 | 10.616
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ08 | ECCExSDG | CZ08 | 0.1267
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ09 | ECCExSDG | CZ09 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ10 | ECCExSDG | CZ10 | 3.3455
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ11 | ECCExSDG | CZ11 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ12 | ECCExSDG | CZ12 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ13 | ECCExSDG | CZ13 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ14 | ECCExSDG | CZ14 | 0.07403
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ15 | ECCExSDG | CZ15 | 0
ComIOUterr | ECCExSDG | IOU | SDG | SDG | ECC | Ex | Multiple | Any | ECCExSDGCZ16 | ECCExSDG | CZ16 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ01 | EUnExSDG | CZ01 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ02 | EUnExSDG | CZ02 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ03 | EUnExSDG | CZ03 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ04 | EUnExSDG | CZ04 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ05 | EUnExSDG | CZ05 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ06 | EUnExSDG | CZ06 | 0.07403
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ07 | EUnExSDG | CZ07 | 10.616
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ08 | EUnExSDG | CZ08 | 0.1267
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ09 | EUnExSDG | CZ09 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ10 | EUnExSDG | CZ10 | 3.3455
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ11 | EUnExSDG | CZ11 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ12 | EUnExSDG | CZ12 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ13 | EUnExSDG | CZ13 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ14 | EUnExSDG | CZ14 | 0.07403
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ15 | EUnExSDG | CZ15 | 0
ComIOUterr | EUnExSDG | IOU | SDG | SDG | EUn | Ex | Multiple | Any | EUnExSDGCZ16 | EUnExSDG | CZ16 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ01 | ERCExSDG | CZ01 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ02 | ERCExSDG | CZ02 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ03 | ERCExSDG | CZ03 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ04 | ERCExSDG | CZ04 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ05 | ERCExSDG | CZ05 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ06 | ERCExSDG | CZ06 | 0.68783
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ07 | ERCExSDG | CZ07 | 7.8963
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ08 | ERCExSDG | CZ08 | 0.77677
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ09 | ERCExSDG | CZ09 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ10 | ERCExSDG | CZ10 | 4.5999
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ11 | ERCExSDG | CZ11 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ12 | ERCExSDG | CZ12 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ13 | ERCExSDG | CZ13 | 0
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ14 | ERCExSDG | CZ14 | 0.12563
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ15 | ERCExSDG | CZ15 | 0.033933
ComIOUterr | ERCExSDG | IOU | SDG | SDG | ERC | Ex | Multiple | Any | ERCExSDGCZ16 | ERCExSDG | CZ16 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ01 | GroExSDG | CZ01 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ02 | GroExSDG | CZ02 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ03 | GroExSDG | CZ03 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ04 | GroExSDG | CZ04 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ05 | GroExSDG | CZ05 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ06 | GroExSDG | CZ06 | 1.7436
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ07 | GroExSDG | CZ07 | 18.7949
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ08 | GroExSDG | CZ08 | 0.7221
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ09 | GroExSDG | CZ09 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ10 | GroExSDG | CZ10 | 7.9489
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ11 | GroExSDG | CZ11 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ12 | GroExSDG | CZ12 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ13 | GroExSDG | CZ13 | 0
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ14 | GroExSDG | CZ14 | 0.11154
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ15 | GroExSDG | CZ15 | 0.03229
ComIOUterr | GroExSDG | IOU | SDG | SDG | Gro | Ex | Multiple | Any | GroExSDGCZ16 | GroExSDG | CZ16 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ01 | HspExSDG | CZ01 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ02 | HspExSDG | CZ02 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ03 | HspExSDG | CZ03 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ04 | HspExSDG | CZ04 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ05 | HspExSDG | CZ05 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ06 | HspExSDG | CZ06 | 0.37263
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ07 | HspExSDG | CZ07 | 12.0169
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ08 | HspExSDG | CZ08 | 0.6753
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ09 | HspExSDG | CZ09 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ10 | HspExSDG | CZ10 | 2.1354
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ11 | HspExSDG | CZ11 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ12 | HspExSDG | CZ12 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ13 | HspExSDG | CZ13 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ14 | HspExSDG | CZ14 | 0.00913
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ15 | HspExSDG | CZ15 | 0
ComIOUterr | HspExSDG | IOU | SDG | SDG | Hsp | Ex | Multiple | Any | HspExSDGCZ16 | HspExSDG | CZ16 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ01 | NrsExSDG | CZ01 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ02 | NrsExSDG | CZ02 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ03 | NrsExSDG | CZ03 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ04 | NrsExSDG | CZ04 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ05 | NrsExSDG | CZ05 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ06 | NrsExSDG | CZ06 | 0.37263
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ07 | NrsExSDG | CZ07 | 12.0169
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ08 | NrsExSDG | CZ08 | 0.6753
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ09 | NrsExSDG | CZ09 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ10 | NrsExSDG | CZ10 | 2.1354
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ11 | NrsExSDG | CZ11 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ12 | NrsExSDG | CZ12 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ13 | NrsExSDG | CZ13 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ14 | NrsExSDG | CZ14 | 0.00913
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ15 | NrsExSDG | CZ15 | 0
ComIOUterr | NrsExSDG | IOU | SDG | SDG | Nrs | Ex | Multiple | Any | NrsExSDGCZ16 | NrsExSDG | CZ16 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ01 | HtlExSDG | CZ01 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ02 | HtlExSDG | CZ02 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ03 | HtlExSDG | CZ03 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ04 | HtlExSDG | CZ04 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ05 | HtlExSDG | CZ05 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ06 | HtlExSDG | CZ06 | 0.96965
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ07 | HtlExSDG | CZ07 | 16.8006
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ08 | HtlExSDG | CZ08 | 0.06245
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ09 | HtlExSDG | CZ09 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ10 | HtlExSDG | CZ10 | 1.905
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ11 | HtlExSDG | CZ11 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ12 | HtlExSDG | CZ12 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ13 | HtlExSDG | CZ13 | 0
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ14 | HtlExSDG | CZ14 | 0.1895
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ15 | HtlExSDG | CZ15 | 0.22975
ComIOUterr | HtlExSDG | IOU | SDG | SDG | Htl | Ex | Multiple | Any | HtlExSDGCZ16 | HtlExSDG | CZ16 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ01 | MtlExSDG | CZ01 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ02 | MtlExSDG | CZ02 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ03 | MtlExSDG | CZ03 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ04 | MtlExSDG | CZ04 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ05 | MtlExSDG | CZ05 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ06 | MtlExSDG | CZ06 | 0.96965
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ07 | MtlExSDG | CZ07 | 16.8006
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ08 | MtlExSDG | CZ08 | 0.06245
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ09 | MtlExSDG | CZ09 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ10 | MtlExSDG | CZ10 | 1.905
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ11 | MtlExSDG | CZ11 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ12 | MtlExSDG | CZ12 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ13 | MtlExSDG | CZ13 | 0
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ14 | MtlExSDG | CZ14 | 0.1895
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ15 | MtlExSDG | CZ15 | 0.22975
ComIOUterr | MtlExSDG | IOU | SDG | SDG | Mtl | Ex | Multiple | Any | MtlExSDGCZ16 | MtlExSDG | CZ16 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ01 | MBTExSDG | CZ01 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ02 | MBTExSDG | CZ02 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ03 | MBTExSDG | CZ03 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ04 | MBTExSDG | CZ04 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ05 | MBTExSDG | CZ05 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ06 | MBTExSDG | CZ06 | 0.86807
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ07 | MBTExSDG | CZ07 | 16.8129
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ08 | MBTExSDG | CZ08 | 0.53257
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ09 | MBTExSDG | CZ09 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ10 | MBTExSDG | CZ10 | 8.0789
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ11 | MBTExSDG | CZ11 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ12 | MBTExSDG | CZ12 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ13 | MBTExSDG | CZ13 | 0
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ14 | MBTExSDG | CZ14 | 0.25297
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ15 | MBTExSDG | CZ15 | 0.082567
ComIOUterr | MBTExSDG | IOU | SDG | SDG | MBT | Ex | Multiple | Any | MBTExSDGCZ16 | MBTExSDG | CZ16 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ01 | MLIExSDG | CZ01 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ02 | MLIExSDG | CZ02 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ03 | MLIExSDG | CZ03 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ04 | MLIExSDG | CZ04 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ05 | MLIExSDG | CZ05 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ06 | MLIExSDG | CZ06 | 0.86807
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ07 | MLIExSDG | CZ07 | 16.8129
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ08 | MLIExSDG | CZ08 | 0.53257
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ09 | MLIExSDG | CZ09 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ10 | MLIExSDG | CZ10 | 8.0789
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ11 | MLIExSDG | CZ11 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ12 | MLIExSDG | CZ12 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ13 | MLIExSDG | CZ13 | 0
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ14 | MLIExSDG | CZ14 | 0.25297
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ15 | MLIExSDG | CZ15 | 0.082567
ComIOUterr | MLIExSDG | IOU | SDG | SDG | MLI | Ex | Multiple | Any | MLIExSDGCZ16 | MLIExSDG | CZ16 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ01 | OfLExSDG | CZ01 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ02 | OfLExSDG | CZ02 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ03 | OfLExSDG | CZ03 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ04 | OfLExSDG | CZ04 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ05 | OfLExSDG | CZ05 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ06 | OfLExSDG | CZ06 | 2.1485
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ07 | OfLExSDG | CZ07 | 77.1268
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ08 | OfLExSDG | CZ08 | 2.0099
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ09 | OfLExSDG | CZ09 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ10 | OfLExSDG | CZ10 | 17.1679
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ11 | OfLExSDG | CZ11 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ12 | OfLExSDG | CZ12 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ13 | OfLExSDG | CZ13 | 0
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ14 | OfLExSDG | CZ14 | 0.4158
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ15 | OfLExSDG | CZ15 | 0.1288
ComIOUterr | OfLExSDG | IOU | SDG | SDG | OfL | Ex | Multiple | Any | OfLExSDGCZ16 | OfLExSDG | CZ16 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ01 | OfSExSDG | CZ01 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ02 | OfSExSDG | CZ02 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ03 | OfSExSDG | CZ03 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ04 | OfSExSDG | CZ04 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ05 | OfSExSDG | CZ05 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ06 | OfSExSDG | CZ06 | 1.1441
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ07 | OfSExSDG | CZ07 | 41.0718
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ08 | OfSExSDG | CZ08 | 1.0703
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ09 | OfSExSDG | CZ09 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ10 | OfSExSDG | CZ10 | 9.1423
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ11 | OfSExSDG | CZ11 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ12 | OfSExSDG | CZ12 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ13 | OfSExSDG | CZ13 | 0
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ14 | OfSExSDG | CZ14 | 0.2216
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ15 | OfSExSDG | CZ15 | 0.0685
ComIOUterr | OfSExSDG | IOU | SDG | SDG | OfS | Ex | Multiple | Any | OfSExSDGCZ16 | OfSExSDG | CZ16 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ01 | RSDExSDG | CZ01 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ02 | RSDExSDG | CZ02 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ03 | RSDExSDG | CZ03 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ04 | RSDExSDG | CZ04 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ05 | RSDExSDG | CZ05 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ06 | RSDExSDG | CZ06 | 0.33992
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ07 | RSDExSDG | CZ07 | 5.2133
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ08 | RSDExSDG | CZ08 | 0.22835
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ09 | RSDExSDG | CZ09 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ10 | RSDExSDG | CZ10 | 1.6327
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ11 | RSDExSDG | CZ11 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ12 | RSDExSDG | CZ12 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ13 | RSDExSDG | CZ13 | 0
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ14 | RSDExSDG | CZ14 | 0.015615
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ15 | RSDExSDG | CZ15 | 0.00744
ComIOUterr | RSDExSDG | IOU | SDG | SDG | RSD | Ex | Multiple | Any | RSDExSDGCZ16 | RSDExSDG | CZ16 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ01 | RFFExSDG | CZ01 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ02 | RFFExSDG | CZ02 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ03 | RFFExSDG | CZ03 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ04 | RFFExSDG | CZ04 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ05 | RFFExSDG | CZ05 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ06 | RFFExSDG | CZ06 | 0.33992
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ07 | RFFExSDG | CZ07 | 5.2133
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ08 | RFFExSDG | CZ08 | 0.22835
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ09 | RFFExSDG | CZ09 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ10 | RFFExSDG | CZ10 | 1.6327
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ11 | RFFExSDG | CZ11 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ12 | RFFExSDG | CZ12 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ13 | RFFExSDG | CZ13 | 0
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ14 | RFFExSDG | CZ14 | 0.015615
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ15 | RFFExSDG | CZ15 | 0.00744
ComIOUterr | RFFExSDG | IOU | SDG | SDG | RFF | Ex | Multiple | Any | RFFExSDGCZ16 | RFFExSDG | CZ16 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ01 | Rt3ExSDG | CZ01 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ02 | Rt3ExSDG | CZ02 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ03 | Rt3ExSDG | CZ03 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ04 | Rt3ExSDG | CZ04 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ05 | Rt3ExSDG | CZ05 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ06 | Rt3ExSDG | CZ06 | 1.1075
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ07 | Rt3ExSDG | CZ07 | 21.5899
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ08 | Rt3ExSDG | CZ08 | 1.9857
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ09 | Rt3ExSDG | CZ09 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ10 | Rt3ExSDG | CZ10 | 8.0409
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ11 | Rt3ExSDG | CZ11 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ12 | Rt3ExSDG | CZ12 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ13 | Rt3ExSDG | CZ13 | 0
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ14 | Rt3ExSDG | CZ14 | 0.029467
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ15 | Rt3ExSDG | CZ15 | 0.0098333
ComIOUterr | Rt3ExSDG | IOU | SDG | SDG | Rt3 | Ex | Multiple | Any | Rt3ExSDGCZ16 | Rt3ExSDG | CZ16 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ01 | RtLExSDG | CZ01 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ02 | RtLExSDG | CZ02 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ03 | RtLExSDG | CZ03 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ04 | RtLExSDG | CZ04 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ05 | RtLExSDG | CZ05 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ06 | RtLExSDG | CZ06 | 1.1075
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ07 | RtLExSDG | CZ07 | 21.5899
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ08 | RtLExSDG | CZ08 | 1.9857
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ09 | RtLExSDG | CZ09 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ10 | RtLExSDG | CZ10 | 8.0409
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ11 | RtLExSDG | CZ11 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ12 | RtLExSDG | CZ12 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ13 | RtLExSDG | CZ13 | 0
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ14 | RtLExSDG | CZ14 | 0.029467
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ15 | RtLExSDG | CZ15 | 0.0098333
ComIOUterr | RtLExSDG | IOU | SDG | SDG | RtL | Ex | Multiple | Any | RtLExSDGCZ16 | RtLExSDG | CZ16 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ01 | RtSExSDG | CZ01 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ02 | RtSExSDG | CZ02 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ03 | RtSExSDG | CZ03 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ04 | RtSExSDG | CZ04 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ05 | RtSExSDG | CZ05 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ06 | RtSExSDG | CZ06 | 1.1075
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ07 | RtSExSDG | CZ07 | 21.5899
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ08 | RtSExSDG | CZ08 | 1.9857
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ09 | RtSExSDG | CZ09 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ10 | RtSExSDG | CZ10 | 8.0409
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ11 | RtSExSDG | CZ11 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ12 | RtSExSDG | CZ12 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ13 | RtSExSDG | CZ13 | 0
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ14 | RtSExSDG | CZ14 | 0.029467
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ15 | RtSExSDG | CZ15 | 0.0098333
ComIOUterr | RtSExSDG | IOU | SDG | SDG | RtS | Ex | Multiple | Any | RtSExSDGCZ16 | RtSExSDG | CZ16 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ01 | SCnExSDG | CZ01 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ02 | SCnExSDG | CZ02 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ03 | SCnExSDG | CZ03 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ04 | SCnExSDG | CZ04 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ05 | SCnExSDG | CZ05 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ06 | SCnExSDG | CZ06 | 0.84245
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ07 | SCnExSDG | CZ07 | 21.9203
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ08 | SCnExSDG | CZ08 | 0.5115
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ09 | SCnExSDG | CZ09 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ10 | SCnExSDG | CZ10 | 10.0091
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ11 | SCnExSDG | CZ11 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ12 | SCnExSDG | CZ12 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ13 | SCnExSDG | CZ13 | 0
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ14 | SCnExSDG | CZ14 | 0.09695
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ15 | SCnExSDG | CZ15 | 0.04675
ComIOUterr | SCnExSDG | IOU | SDG | SDG | SCn | Ex | Multiple | Any | SCnExSDGCZ16 | SCnExSDG | CZ16 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ01 | SUnExSDG | CZ01 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ02 | SUnExSDG | CZ02 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ03 | SUnExSDG | CZ03 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ04 | SUnExSDG | CZ04 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ05 | SUnExSDG | CZ05 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ06 | SUnExSDG | CZ06 | 0.84245
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ07 | SUnExSDG | CZ07 | 21.9203
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ08 | SUnExSDG | CZ08 | 0.5115
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ09 | SUnExSDG | CZ09 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ10 | SUnExSDG | CZ10 | 10.0091
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ11 | SUnExSDG | CZ11 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ12 | SUnExSDG | CZ12 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ13 | SUnExSDG | CZ13 | 0
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ14 | SUnExSDG | CZ14 | 0.09695
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ15 | SUnExSDG | CZ15 | 0.04675
ComIOUterr | SUnExSDG | IOU | SDG | SDG | SUn | Ex | Multiple | Any | SUnExSDGCZ16 | SUnExSDG | CZ16 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ01 | WRfExSDG | CZ01 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ02 | WRfExSDG | CZ02 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ03 | WRfExSDG | CZ03 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ04 | WRfExSDG | CZ04 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ05 | WRfExSDG | CZ05 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ06 | WRfExSDG | CZ06 | 0.00653
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ07 | WRfExSDG | CZ07 | 0.50888
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ08 | WRfExSDG | CZ08 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ09 | WRfExSDG | CZ09 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ10 | WRfExSDG | CZ10 | 0.14488
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ11 | WRfExSDG | CZ11 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ12 | WRfExSDG | CZ12 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ13 | WRfExSDG | CZ13 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ14 | WRfExSDG | CZ14 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ15 | WRfExSDG | CZ15 | 0
ComIOUterr | WRfExSDG | IOU | SDG | SDG | WRf | Ex | Multiple | Any | WRfExSDGCZ16 | WRfExSDG | CZ16 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ01 | AsmNewSDG | CZ01 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ02 | AsmNewSDG | CZ02 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ03 | AsmNewSDG | CZ03 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ04 | AsmNewSDG | CZ04 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ05 | AsmNewSDG | CZ05 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ06 | AsmNewSDG | CZ06 | 0.058967
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ07 | AsmNewSDG | CZ07 | 1.1418
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ08 | AsmNewSDG | CZ08 | 0.036167
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ09 | AsmNewSDG | CZ09 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ10 | AsmNewSDG | CZ10 | 0.54867
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ11 | AsmNewSDG | CZ11 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ12 | AsmNewSDG | CZ12 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ13 | AsmNewSDG | CZ13 | 0
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ14 | AsmNewSDG | CZ14 | 0.017167
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ15 | AsmNewSDG | CZ15 | 0.0056
ComIOUterr | AsmNewSDG | IOU | Any | SDG | Asm | New | Multiple | Any | AsmNewSDGCZ16 | AsmNewSDG | CZ16 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ01 | EPrNewSDG | CZ01 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ02 | EPrNewSDG | CZ02 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ03 | EPrNewSDG | CZ03 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ04 | EPrNewSDG | CZ04 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ05 | EPrNewSDG | CZ05 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ06 | EPrNewSDG | CZ06 | 0.016867
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ07 | EPrNewSDG | CZ07 | 0.19347
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ08 | EPrNewSDG | CZ08 | 0.019033
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ09 | EPrNewSDG | CZ09 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ10 | EPrNewSDG | CZ10 | 0.1127
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ11 | EPrNewSDG | CZ11 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ12 | EPrNewSDG | CZ12 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ13 | EPrNewSDG | CZ13 | 0
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ14 | EPrNewSDG | CZ14 | 0.0030667
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ15 | EPrNewSDG | CZ15 | 0.00083333
ComIOUterr | EPrNewSDG | IOU | Any | SDG | EPr | New | Multiple | Any | EPrNewSDGCZ16 | EPrNewSDG | CZ16 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ01 | ESeNewSDG | CZ01 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ02 | ESeNewSDG | CZ02 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ03 | ESeNewSDG | CZ03 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ04 | ESeNewSDG | CZ04 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ05 | ESeNewSDG | CZ05 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ06 | ESeNewSDG | CZ06 | 0.016867
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ07 | ESeNewSDG | CZ07 | 0.19347
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ08 | ESeNewSDG | CZ08 | 0.019033
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ09 | ESeNewSDG | CZ09 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ10 | ESeNewSDG | CZ10 | 0.1127
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ11 | ESeNewSDG | CZ11 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ12 | ESeNewSDG | CZ12 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ13 | ESeNewSDG | CZ13 | 0
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ14 | ESeNewSDG | CZ14 | 0.0030667
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ15 | ESeNewSDG | CZ15 | 0.00083333
ComIOUterr | ESeNewSDG | IOU | Any | SDG | ESe | New | Multiple | Any | ESeNewSDGCZ16 | ESeNewSDG | CZ16 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ01 | ECCNewSDG | CZ01 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ02 | ECCNewSDG | CZ02 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ03 | ECCNewSDG | CZ03 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ04 | ECCNewSDG | CZ04 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ05 | ECCNewSDG | CZ05 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ06 | ECCNewSDG | CZ06 | 0.003295
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ07 | ECCNewSDG | CZ07 | 0.47262
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ08 | ECCNewSDG | CZ08 | 0.00564
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ09 | ECCNewSDG | CZ09 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ10 | ECCNewSDG | CZ10 | 0.14894
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ11 | ECCNewSDG | CZ11 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ12 | ECCNewSDG | CZ12 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ13 | ECCNewSDG | CZ13 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ14 | ECCNewSDG | CZ14 | 0.003295
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ15 | ECCNewSDG | CZ15 | 0
ComIOUterr | ECCNewSDG | IOU | Any | SDG | ECC | New | Multiple | Any | ECCNewSDGCZ16 | ECCNewSDG | CZ16 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ01 | EUnNewSDG | CZ01 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ02 | EUnNewSDG | CZ02 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ03 | EUnNewSDG | CZ03 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ04 | EUnNewSDG | CZ04 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ05 | EUnNewSDG | CZ05 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ06 | EUnNewSDG | CZ06 | 0.003295
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ07 | EUnNewSDG | CZ07 | 0.47262
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ08 | EUnNewSDG | CZ08 | 0.00564
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ09 | EUnNewSDG | CZ09 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ10 | EUnNewSDG | CZ10 | 0.14894
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ11 | EUnNewSDG | CZ11 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ12 | EUnNewSDG | CZ12 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ13 | EUnNewSDG | CZ13 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ14 | EUnNewSDG | CZ14 | 0.003295
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ15 | EUnNewSDG | CZ15 | 0
ComIOUterr | EUnNewSDG | IOU | Any | SDG | EUn | New | Multiple | Any | EUnNewSDGCZ16 | EUnNewSDG | CZ16 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ01 | ERCNewSDG | CZ01 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ02 | ERCNewSDG | CZ02 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ03 | ERCNewSDG | CZ03 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ04 | ERCNewSDG | CZ04 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ05 | ERCNewSDG | CZ05 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ06 | ERCNewSDG | CZ06 | 0.016867
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ07 | ERCNewSDG | CZ07 | 0.19347
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ08 | ERCNewSDG | CZ08 | 0.019033
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ09 | ERCNewSDG | CZ09 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ10 | ERCNewSDG | CZ10 | 0.1127
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ11 | ERCNewSDG | CZ11 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ12 | ERCNewSDG | CZ12 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ13 | ERCNewSDG | CZ13 | 0
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ14 | ERCNewSDG | CZ14 | 0.0030667
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ15 | ERCNewSDG | CZ15 | 0.00083333
ComIOUterr | ERCNewSDG | IOU | Any | SDG | ERC | New | Multiple | Any | ERCNewSDGCZ16 | ERCNewSDG | CZ16 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ01 | GroNewSDG | CZ01 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ02 | GroNewSDG | CZ02 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ03 | GroNewSDG | CZ03 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ04 | GroNewSDG | CZ04 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ05 | GroNewSDG | CZ05 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ06 | GroNewSDG | CZ06 | 0.10694
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ07 | GroNewSDG | CZ07 | 1.1527
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ08 | GroNewSDG | CZ08 | 0.04429
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ09 | GroNewSDG | CZ09 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ10 | GroNewSDG | CZ10 | 0.48752
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ11 | GroNewSDG | CZ11 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ12 | GroNewSDG | CZ12 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ13 | GroNewSDG | CZ13 | 0
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ14 | GroNewSDG | CZ14 | 0.00684
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ15 | GroNewSDG | CZ15 | 0.00198
ComIOUterr | GroNewSDG | IOU | Any | SDG | Gro | New | Multiple | Any | GroNewSDGCZ16 | GroNewSDG | CZ16 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ01 | HspNewSDG | CZ01 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ02 | HspNewSDG | CZ02 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ03 | HspNewSDG | CZ03 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ04 | HspNewSDG | CZ04 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ05 | HspNewSDG | CZ05 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ06 | HspNewSDG | CZ06 | 0.010345
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ07 | HspNewSDG | CZ07 | 0.33361
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ08 | HspNewSDG | CZ08 | 0.01875
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ09 | HspNewSDG | CZ09 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ10 | HspNewSDG | CZ10 | 0.059285
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ11 | HspNewSDG | CZ11 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ12 | HspNewSDG | CZ12 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ13 | HspNewSDG | CZ13 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ14 | HspNewSDG | CZ14 | 0.000255
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ15 | HspNewSDG | CZ15 | 0
ComIOUterr | HspNewSDG | IOU | Any | SDG | Hsp | New | Multiple | Any | HspNewSDGCZ16 | HspNewSDG | CZ16 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ01 | NrsNewSDG | CZ01 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ02 | NrsNewSDG | CZ02 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ03 | NrsNewSDG | CZ03 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ04 | NrsNewSDG | CZ04 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ05 | NrsNewSDG | CZ05 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ06 | NrsNewSDG | CZ06 | 0.010345
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ07 | NrsNewSDG | CZ07 | 0.33361
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ08 | NrsNewSDG | CZ08 | 0.01875
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ09 | NrsNewSDG | CZ09 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ10 | NrsNewSDG | CZ10 | 0.059285
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ11 | NrsNewSDG | CZ11 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ12 | NrsNewSDG | CZ12 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ13 | NrsNewSDG | CZ13 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ14 | NrsNewSDG | CZ14 | 0.000255
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ15 | NrsNewSDG | CZ15 | 0
ComIOUterr | NrsNewSDG | IOU | Any | SDG | Nrs | New | Multiple | Any | NrsNewSDGCZ16 | NrsNewSDG | CZ16 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ01 | HtlNewSDG | CZ01 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ02 | HtlNewSDG | CZ02 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ03 | HtlNewSDG | CZ03 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ04 | HtlNewSDG | CZ04 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ05 | HtlNewSDG | CZ05 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ06 | HtlNewSDG | CZ06 | 0.07455
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ07 | HtlNewSDG | CZ07 | 1.292
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ08 | HtlNewSDG | CZ08 | 0.0048
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ09 | HtlNewSDG | CZ09 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ10 | HtlNewSDG | CZ10 | 0.1465
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ11 | HtlNewSDG | CZ11 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ12 | HtlNewSDG | CZ12 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ13 | HtlNewSDG | CZ13 | 0
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ14 | HtlNewSDG | CZ14 | 0.01455
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ15 | HtlNewSDG | CZ15 | 0.01765
ComIOUterr | HtlNewSDG | IOU | Any | SDG | Htl | New | Multiple | Any | HtlNewSDGCZ16 | HtlNewSDG | CZ16 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ01 | MtlNewSDG | CZ01 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ02 | MtlNewSDG | CZ02 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ03 | MtlNewSDG | CZ03 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ04 | MtlNewSDG | CZ04 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ05 | MtlNewSDG | CZ05 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ06 | MtlNewSDG | CZ06 | 0.07455
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ07 | MtlNewSDG | CZ07 | 1.292
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ08 | MtlNewSDG | CZ08 | 0.0048
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ09 | MtlNewSDG | CZ09 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ10 | MtlNewSDG | CZ10 | 0.1465
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ11 | MtlNewSDG | CZ11 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ12 | MtlNewSDG | CZ12 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ13 | MtlNewSDG | CZ13 | 0
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ14 | MtlNewSDG | CZ14 | 0.01455
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ15 | MtlNewSDG | CZ15 | 0.01765
ComIOUterr | MtlNewSDG | IOU | Any | SDG | Mtl | New | Multiple | Any | MtlNewSDGCZ16 | MtlNewSDG | CZ16 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ01 | MBTNewSDG | CZ01 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ02 | MBTNewSDG | CZ02 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ03 | MBTNewSDG | CZ03 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ04 | MBTNewSDG | CZ04 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ05 | MBTNewSDG | CZ05 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ06 | MBTNewSDG | CZ06 | 0.058967
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ07 | MBTNewSDG | CZ07 | 1.1418
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ08 | MBTNewSDG | CZ08 | 0.036167
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ09 | MBTNewSDG | CZ09 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ10 | MBTNewSDG | CZ10 | 0.54867
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ11 | MBTNewSDG | CZ11 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ12 | MBTNewSDG | CZ12 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ13 | MBTNewSDG | CZ13 | 0
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ14 | MBTNewSDG | CZ14 | 0.017167
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ15 | MBTNewSDG | CZ15 | 0.0056
ComIOUterr | MBTNewSDG | IOU | Any | SDG | MBT | New | Multiple | Any | MBTNewSDGCZ16 | MBTNewSDG | CZ16 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ01 | MLINewSDG | CZ01 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ02 | MLINewSDG | CZ02 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ03 | MLINewSDG | CZ03 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ04 | MLINewSDG | CZ04 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ05 | MLINewSDG | CZ05 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ06 | MLINewSDG | CZ06 | 0.058967
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ07 | MLINewSDG | CZ07 | 1.1418
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ08 | MLINewSDG | CZ08 | 0.036167
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ09 | MLINewSDG | CZ09 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ10 | MLINewSDG | CZ10 | 0.54867
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ11 | MLINewSDG | CZ11 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ12 | MLINewSDG | CZ12 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ13 | MLINewSDG | CZ13 | 0
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ14 | MLINewSDG | CZ14 | 0.017167
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ15 | MLINewSDG | CZ15 | 0.0056
ComIOUterr | MLINewSDG | IOU | Any | SDG | MLI | New | Multiple | Any | MLINewSDGCZ16 | MLINewSDG | CZ16 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ01 | OfLNewSDG | CZ01 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ02 | OfLNewSDG | CZ02 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ03 | OfLNewSDG | CZ03 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ04 | OfLNewSDG | CZ04 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ05 | OfLNewSDG | CZ05 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ06 | OfLNewSDG | CZ06 | 0.0817
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ07 | OfLNewSDG | CZ07 | 2.934
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ08 | OfLNewSDG | CZ08 | 0.0765
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ09 | OfLNewSDG | CZ09 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ10 | OfLNewSDG | CZ10 | 0.6531
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ11 | OfLNewSDG | CZ11 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ12 | OfLNewSDG | CZ12 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ13 | OfLNewSDG | CZ13 | 0
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ14 | OfLNewSDG | CZ14 | 0.0158
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ15 | OfLNewSDG | CZ15 | 0.0049
ComIOUterr | OfLNewSDG | IOU | Any | SDG | OfL | New | Multiple | Any | OfLNewSDGCZ16 | OfLNewSDG | CZ16 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ01 | OfSNewSDG | CZ01 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ02 | OfSNewSDG | CZ02 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ03 | OfSNewSDG | CZ03 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ04 | OfSNewSDG | CZ04 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ05 | OfSNewSDG | CZ05 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ06 | OfSNewSDG | CZ06 | 0.0375
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ07 | OfSNewSDG | CZ07 | 1.3449
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ08 | OfSNewSDG | CZ08 | 0.035
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ09 | OfSNewSDG | CZ09 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ10 | OfSNewSDG | CZ10 | 0.2994
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ11 | OfSNewSDG | CZ11 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ12 | OfSNewSDG | CZ12 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ13 | OfSNewSDG | CZ13 | 0
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ14 | OfSNewSDG | CZ14 | 0.0073
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ15 | OfSNewSDG | CZ15 | 0.0022
ComIOUterr | OfSNewSDG | IOU | Any | SDG | OfS | New | Multiple | Any | OfSNewSDGCZ16 | OfSNewSDG | CZ16 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ01 | RSDNewSDG | CZ01 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ02 | RSDNewSDG | CZ02 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ03 | RSDNewSDG | CZ03 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ04 | RSDNewSDG | CZ04 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ05 | RSDNewSDG | CZ05 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ06 | RSDNewSDG | CZ06 | 0.013085
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ07 | RSDNewSDG | CZ07 | 0.20067
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ08 | RSDNewSDG | CZ08 | 0.00879
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ09 | RSDNewSDG | CZ09 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ10 | RSDNewSDG | CZ10 | 0.062845
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ11 | RSDNewSDG | CZ11 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ12 | RSDNewSDG | CZ12 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ13 | RSDNewSDG | CZ13 | 0
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ14 | RSDNewSDG | CZ14 | 0.0006
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ15 | RSDNewSDG | CZ15 | 0.000285
ComIOUterr | RSDNewSDG | IOU | Any | SDG | RSD | New | Multiple | Any | RSDNewSDGCZ16 | RSDNewSDG | CZ16 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ01 | RFFNewSDG | CZ01 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ02 | RFFNewSDG | CZ02 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ03 | RFFNewSDG | CZ03 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ04 | RFFNewSDG | CZ04 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ05 | RFFNewSDG | CZ05 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ06 | RFFNewSDG | CZ06 | 0.013085
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ07 | RFFNewSDG | CZ07 | 0.20067
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ08 | RFFNewSDG | CZ08 | 0.00879
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ09 | RFFNewSDG | CZ09 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ10 | RFFNewSDG | CZ10 | 0.062845
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ11 | RFFNewSDG | CZ11 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ12 | RFFNewSDG | CZ12 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ13 | RFFNewSDG | CZ13 | 0
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ14 | RFFNewSDG | CZ14 | 0.0006
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ15 | RFFNewSDG | CZ15 | 0.000285
ComIOUterr | RFFNewSDG | IOU | Any | SDG | RFF | New | Multiple | Any | RFFNewSDGCZ16 | RFFNewSDG | CZ16 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ01 | Rt3NewSDG | CZ01 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ02 | Rt3NewSDG | CZ02 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ03 | Rt3NewSDG | CZ03 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ04 | Rt3NewSDG | CZ04 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ05 | Rt3NewSDG | CZ05 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ06 | Rt3NewSDG | CZ06 | 0.057567
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ07 | Rt3NewSDG | CZ07 | 1.1219
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ08 | Rt3NewSDG | CZ08 | 0.1032
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ09 | Rt3NewSDG | CZ09 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ10 | Rt3NewSDG | CZ10 | 0.41783
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ11 | Rt3NewSDG | CZ11 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ12 | Rt3NewSDG | CZ12 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ13 | Rt3NewSDG | CZ13 | 0
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ14 | Rt3NewSDG | CZ14 | 0.0015333
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ15 | Rt3NewSDG | CZ15 | 0.0005
ComIOUterr | Rt3NewSDG | IOU | Any | SDG | Rt3 | New | Multiple | Any | Rt3NewSDGCZ16 | Rt3NewSDG | CZ16 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ01 | RtLNewSDG | CZ01 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ02 | RtLNewSDG | CZ02 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ03 | RtLNewSDG | CZ03 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ04 | RtLNewSDG | CZ04 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ05 | RtLNewSDG | CZ05 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ06 | RtLNewSDG | CZ06 | 0.057567
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ07 | RtLNewSDG | CZ07 | 1.1219
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ08 | RtLNewSDG | CZ08 | 0.1032
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ09 | RtLNewSDG | CZ09 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ10 | RtLNewSDG | CZ10 | 0.41783
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ11 | RtLNewSDG | CZ11 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ12 | RtLNewSDG | CZ12 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ13 | RtLNewSDG | CZ13 | 0
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ14 | RtLNewSDG | CZ14 | 0.0015333
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ15 | RtLNewSDG | CZ15 | 0.0005
ComIOUterr | RtLNewSDG | IOU | Any | SDG | RtL | New | Multiple | Any | RtLNewSDGCZ16 | RtLNewSDG | CZ16 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ01 | RtSNewSDG | CZ01 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ02 | RtSNewSDG | CZ02 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ03 | RtSNewSDG | CZ03 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ04 | RtSNewSDG | CZ04 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ05 | RtSNewSDG | CZ05 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ06 | RtSNewSDG | CZ06 | 0.057567
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ07 | RtSNewSDG | CZ07 | 1.1219
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ08 | RtSNewSDG | CZ08 | 0.1032
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ09 | RtSNewSDG | CZ09 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ10 | RtSNewSDG | CZ10 | 0.41783
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ11 | RtSNewSDG | CZ11 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ12 | RtSNewSDG | CZ12 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ13 | RtSNewSDG | CZ13 | 0
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ14 | RtSNewSDG | CZ14 | 0.0015333
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ15 | RtSNewSDG | CZ15 | 0.0005
ComIOUterr | RtSNewSDG | IOU | Any | SDG | RtS | New | Multiple | Any | RtSNewSDGCZ16 | RtSNewSDG | CZ16 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ01 | SCnNewSDG | CZ01 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ02 | SCnNewSDG | CZ02 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ03 | SCnNewSDG | CZ03 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ04 | SCnNewSDG | CZ04 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ05 | SCnNewSDG | CZ05 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ06 | SCnNewSDG | CZ06 | 0.03995
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ07 | SCnNewSDG | CZ07 | 1.0393
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ08 | SCnNewSDG | CZ08 | 0.02425
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ09 | SCnNewSDG | CZ09 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ10 | SCnNewSDG | CZ10 | 0.47455
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ11 | SCnNewSDG | CZ11 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ12 | SCnNewSDG | CZ12 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ13 | SCnNewSDG | CZ13 | 0
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ14 | SCnNewSDG | CZ14 | 0.0046
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ15 | SCnNewSDG | CZ15 | 0.0022
ComIOUterr | SCnNewSDG | IOU | Any | SDG | SCn | New | Multiple | Any | SCnNewSDGCZ16 | SCnNewSDG | CZ16 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ01 | SUnNewSDG | CZ01 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ02 | SUnNewSDG | CZ02 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ03 | SUnNewSDG | CZ03 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ04 | SUnNewSDG | CZ04 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ05 | SUnNewSDG | CZ05 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ06 | SUnNewSDG | CZ06 | 0.03995
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ07 | SUnNewSDG | CZ07 | 1.0393
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ08 | SUnNewSDG | CZ08 | 0.02425
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ09 | SUnNewSDG | CZ09 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ10 | SUnNewSDG | CZ10 | 0.47455
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ11 | SUnNewSDG | CZ11 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ12 | SUnNewSDG | CZ12 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ13 | SUnNewSDG | CZ13 | 0
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ14 | SUnNewSDG | CZ14 | 0.0046
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ15 | SUnNewSDG | CZ15 | 0.0022
ComIOUterr | SUnNewSDG | IOU | Any | SDG | SUn | New | Multiple | Any | SUnNewSDGCZ16 | SUnNewSDG | CZ16 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ01 | WRfNewSDG | CZ01 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ02 | WRfNewSDG | CZ02 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ03 | WRfNewSDG | CZ03 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ04 | WRfNewSDG | CZ04 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ05 | WRfNewSDG | CZ05 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ06 | WRfNewSDG | CZ06 | 0.00038
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ07 | WRfNewSDG | CZ07 | 0.02993
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ08 | WRfNewSDG | CZ08 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ09 | WRfNewSDG | CZ09 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ10 | WRfNewSDG | CZ10 | 0.00852
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ11 | WRfNewSDG | CZ11 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ12 | WRfNewSDG | CZ12 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ13 | WRfNewSDG | CZ13 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ14 | WRfNewSDG | CZ14 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ15 | WRfNewSDG | CZ15 | 0
ComIOUterr | WRfNewSDG | IOU | Any | SDG | WRf | New | Multiple | Any | WRfNewSDGCZ16 | WRfNewSDG | CZ16 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ01 | AsmExSCG | CZ01 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ02 | AsmExSCG | CZ02 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ03 | AsmExSCG | CZ03 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ04 | AsmExSCG | CZ04 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ05 | AsmExSCG | CZ05 | 0.43187
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ06 | AsmExSCG | CZ06 | 39.668
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ07 | AsmExSCG | CZ07 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ08 | AsmExSCG | CZ08 | 59.7461
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ09 | AsmExSCG | CZ09 | 51.1175
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ10 | AsmExSCG | CZ10 | 27.1921
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ11 | AsmExSCG | CZ11 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ12 | AsmExSCG | CZ12 | 0
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ13 | AsmExSCG | CZ13 | 3.4588
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ14 | AsmExSCG | CZ14 | 6.3093
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ15 | AsmExSCG | CZ15 | 9.843
ComIOUterr | AsmExSCG | IOU | SCG | SCG | Asm | Ex | Multiple | Any | AsmExSCGCZ16 | AsmExSCG | CZ16 | 3.6908
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ01 | EPrExSCG | CZ01 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ02 | EPrExSCG | CZ02 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ03 | EPrExSCG | CZ03 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ04 | EPrExSCG | CZ04 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ05 | EPrExSCG | CZ05 | 0.0665
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ06 | EPrExSCG | CZ06 | 13.2872
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ07 | EPrExSCG | CZ07 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ08 | EPrExSCG | CZ08 | 23.5388
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ09 | EPrExSCG | CZ09 | 22.0797
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ10 | EPrExSCG | CZ10 | 13.2453
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ11 | EPrExSCG | CZ11 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ12 | EPrExSCG | CZ12 | 0
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ13 | EPrExSCG | CZ13 | 2.689
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ14 | EPrExSCG | CZ14 | 3.4831
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ15 | EPrExSCG | CZ15 | 1.1804
ComIOUterr | EPrExSCG | IOU | SCG | SCG | EPr | Ex | Multiple | Any | EPrExSCGCZ16 | EPrExSCG | CZ16 | 1.618
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ01 | ESeExSCG | CZ01 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ02 | ESeExSCG | CZ02 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ03 | ESeExSCG | CZ03 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ04 | ESeExSCG | CZ04 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ05 | ESeExSCG | CZ05 | 0.0665
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ06 | ESeExSCG | CZ06 | 13.2872
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ07 | ESeExSCG | CZ07 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ08 | ESeExSCG | CZ08 | 23.5388
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ09 | ESeExSCG | CZ09 | 22.0797
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ10 | ESeExSCG | CZ10 | 13.2453
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ11 | ESeExSCG | CZ11 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ12 | ESeExSCG | CZ12 | 0
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ13 | ESeExSCG | CZ13 | 2.689
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ14 | ESeExSCG | CZ14 | 3.4831
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ15 | ESeExSCG | CZ15 | 1.1804
ComIOUterr | ESeExSCG | IOU | SCG | SCG | ESe | Ex | Multiple | Any | ESeExSCGCZ16 | ESeExSCG | CZ16 | 1.618
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ01 | ECCExSCG | CZ01 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ02 | ECCExSCG | CZ02 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ03 | ECCExSCG | CZ03 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ04 | ECCExSCG | CZ04 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ05 | ECCExSCG | CZ05 | 0.0152
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ06 | ECCExSCG | CZ06 | 14.9507
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ07 | ECCExSCG | CZ07 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ08 | ECCExSCG | CZ08 | 25.0218
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ09 | ECCExSCG | CZ09 | 21.2062
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ10 | ECCExSCG | CZ10 | 5.9322
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ11 | ECCExSCG | CZ11 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ12 | ECCExSCG | CZ12 | 0
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ13 | ECCExSCG | CZ13 | 1.1944
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ14 | ECCExSCG | CZ14 | 2.0935
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ15 | ECCExSCG | CZ15 | 1.7264
ComIOUterr | ECCExSCG | IOU | SCG | SCG | ECC | Ex | Multiple | Any | ECCExSCGCZ16 | ECCExSCG | CZ16 | 3.8559
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ01 | EUnExSCG | CZ01 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ02 | EUnExSCG | CZ02 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ03 | EUnExSCG | CZ03 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ04 | EUnExSCG | CZ04 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ05 | EUnExSCG | CZ05 | 0.0152
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ06 | EUnExSCG | CZ06 | 14.9507
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ07 | EUnExSCG | CZ07 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ08 | EUnExSCG | CZ08 | 25.0218
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ09 | EUnExSCG | CZ09 | 21.2062
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ10 | EUnExSCG | CZ10 | 5.9322
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ11 | EUnExSCG | CZ11 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ12 | EUnExSCG | CZ12 | 0
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ13 | EUnExSCG | CZ13 | 1.1944
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ14 | EUnExSCG | CZ14 | 2.0935
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ15 | EUnExSCG | CZ15 | 1.7264
ComIOUterr | EUnExSCG | IOU | SCG | SCG | EUn | Ex | Multiple | Any | EUnExSCGCZ16 | EUnExSCG | CZ16 | 3.8559
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ01 | ERCExSCG | CZ01 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ02 | ERCExSCG | CZ02 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ03 | ERCExSCG | CZ03 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ04 | ERCExSCG | CZ04 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ05 | ERCExSCG | CZ05 | 0.0665
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ06 | ERCExSCG | CZ06 | 13.2872
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ07 | ERCExSCG | CZ07 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ08 | ERCExSCG | CZ08 | 23.5388
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ09 | ERCExSCG | CZ09 | 22.0797
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ10 | ERCExSCG | CZ10 | 13.2453
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ11 | ERCExSCG | CZ11 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ12 | ERCExSCG | CZ12 | 0
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ13 | ERCExSCG | CZ13 | 2.689
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ14 | ERCExSCG | CZ14 | 3.4831
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ15 | ERCExSCG | CZ15 | 1.1804
ComIOUterr | ERCExSCG | IOU | SCG | SCG | ERC | Ex | Multiple | Any | ERCExSCGCZ16 | ERCExSCG | CZ16 | 1.618
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ01 | GroExSCG | CZ01 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ02 | GroExSCG | CZ02 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ03 | GroExSCG | CZ03 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ04 | GroExSCG | CZ04 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ05 | GroExSCG | CZ05 | 0.4567
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ06 | GroExSCG | CZ06 | 25.274
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ07 | GroExSCG | CZ07 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ08 | GroExSCG | CZ08 | 38.4356
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ09 | GroExSCG | CZ09 | 35.6266
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ10 | GroExSCG | CZ10 | 23.7779
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ11 | GroExSCG | CZ11 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ12 | GroExSCG | CZ12 | 0
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ13 | GroExSCG | CZ13 | 3.4644
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ14 | GroExSCG | CZ14 | 5.7258
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ15 | GroExSCG | CZ15 | 3.3432
ComIOUterr | GroExSCG | IOU | SCG | SCG | Gro | Ex | Multiple | Any | GroExSCGCZ16 | GroExSCG | CZ16 | 2.2903
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ01 | HspExSCG | CZ01 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ02 | HspExSCG | CZ02 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ03 | HspExSCG | CZ03 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ04 | HspExSCG | CZ04 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ05 | HspExSCG | CZ05 | 0.95435
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ06 | HspExSCG | CZ06 | 15.9869
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ07 | HspExSCG | CZ07 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ08 | HspExSCG | CZ08 | 18.7061
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ09 | HspExSCG | CZ09 | 21.6804
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ10 | HspExSCG | CZ10 | 7.9053
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ11 | HspExSCG | CZ11 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ12 | HspExSCG | CZ12 | 0
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ13 | HspExSCG | CZ13 | 1.5183
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ14 | HspExSCG | CZ14 | 1.4169
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ15 | HspExSCG | CZ15 | 1.6376
ComIOUterr | HspExSCG | IOU | SCG | SCG | Hsp | Ex | Multiple | Any | HspExSCGCZ16 | HspExSCG | CZ16 | 1.0455
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ01 | NrsExSCG | CZ01 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ02 | NrsExSCG | CZ02 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ03 | NrsExSCG | CZ03 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ04 | NrsExSCG | CZ04 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ05 | NrsExSCG | CZ05 | 0.95435
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ06 | NrsExSCG | CZ06 | 15.9869
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ07 | NrsExSCG | CZ07 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ08 | NrsExSCG | CZ08 | 18.7061
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ09 | NrsExSCG | CZ09 | 21.6804
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ10 | NrsExSCG | CZ10 | 7.9053
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ11 | NrsExSCG | CZ11 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ12 | NrsExSCG | CZ12 | 0
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ13 | NrsExSCG | CZ13 | 1.5183
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ14 | NrsExSCG | CZ14 | 1.4169
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ15 | NrsExSCG | CZ15 | 1.6376
ComIOUterr | NrsExSCG | IOU | SCG | SCG | Nrs | Ex | Multiple | Any | NrsExSCGCZ16 | NrsExSCG | CZ16 | 1.0455
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ01 | HtlExSCG | CZ01 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ02 | HtlExSCG | CZ02 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ03 | HtlExSCG | CZ03 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ04 | HtlExSCG | CZ04 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ05 | HtlExSCG | CZ05 | 0.15065
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ06 | HtlExSCG | CZ06 | 19.3526
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ07 | HtlExSCG | CZ07 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ08 | HtlExSCG | CZ08 | 14.8227
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ09 | HtlExSCG | CZ09 | 20.7798
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ10 | HtlExSCG | CZ10 | 2.7843
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ11 | HtlExSCG | CZ11 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ12 | HtlExSCG | CZ12 | 0
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ13 | HtlExSCG | CZ13 | 0.5345
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ14 | HtlExSCG | CZ14 | 1.3728
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ15 | HtlExSCG | CZ15 | 7.1212
ComIOUterr | HtlExSCG | IOU | SCG | SCG | Htl | Ex | Multiple | Any | HtlExSCGCZ16 | HtlExSCG | CZ16 | 1.87
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ01 | MtlExSCG | CZ01 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ02 | MtlExSCG | CZ02 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ03 | MtlExSCG | CZ03 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ04 | MtlExSCG | CZ04 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ05 | MtlExSCG | CZ05 | 0.15065
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ06 | MtlExSCG | CZ06 | 19.3526
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ07 | MtlExSCG | CZ07 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ08 | MtlExSCG | CZ08 | 14.8227
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ09 | MtlExSCG | CZ09 | 20.7798
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ10 | MtlExSCG | CZ10 | 2.7843
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ11 | MtlExSCG | CZ11 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ12 | MtlExSCG | CZ12 | 0
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ13 | MtlExSCG | CZ13 | 0.5345
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ14 | MtlExSCG | CZ14 | 1.3728
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ15 | MtlExSCG | CZ15 | 7.1212
ComIOUterr | MtlExSCG | IOU | SCG | SCG | Mtl | Ex | Multiple | Any | MtlExSCGCZ16 | MtlExSCG | CZ16 | 1.87
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ01 | MBTExSCG | CZ01 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ02 | MBTExSCG | CZ02 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ03 | MBTExSCG | CZ03 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ04 | MBTExSCG | CZ04 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ05 | MBTExSCG | CZ05 | 0.43187
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ06 | MBTExSCG | CZ06 | 39.668
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ07 | MBTExSCG | CZ07 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ08 | MBTExSCG | CZ08 | 59.7461
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ09 | MBTExSCG | CZ09 | 51.1175
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ10 | MBTExSCG | CZ10 | 27.1921
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ11 | MBTExSCG | CZ11 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ12 | MBTExSCG | CZ12 | 0
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ13 | MBTExSCG | CZ13 | 3.4588
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ14 | MBTExSCG | CZ14 | 6.3093
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ15 | MBTExSCG | CZ15 | 9.843
ComIOUterr | MBTExSCG | IOU | SCG | SCG | MBT | Ex | Multiple | Any | MBTExSCGCZ16 | MBTExSCG | CZ16 | 3.6908
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ01 | MLIExSCG | CZ01 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ02 | MLIExSCG | CZ02 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ03 | MLIExSCG | CZ03 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ04 | MLIExSCG | CZ04 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ05 | MLIExSCG | CZ05 | 0.43187
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ06 | MLIExSCG | CZ06 | 39.668
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ07 | MLIExSCG | CZ07 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ08 | MLIExSCG | CZ08 | 59.7461
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ09 | MLIExSCG | CZ09 | 51.1175
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ10 | MLIExSCG | CZ10 | 27.1921
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ11 | MLIExSCG | CZ11 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ12 | MLIExSCG | CZ12 | 0
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ13 | MLIExSCG | CZ13 | 3.4588
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ14 | MLIExSCG | CZ14 | 6.3093
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ15 | MLIExSCG | CZ15 | 9.843
ComIOUterr | MLIExSCG | IOU | SCG | SCG | MLI | Ex | Multiple | Any | MLIExSCGCZ16 | MLIExSCG | CZ16 | 3.6908
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ01 | OfLExSCG | CZ01 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ02 | OfLExSCG | CZ02 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ03 | OfLExSCG | CZ03 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ04 | OfLExSCG | CZ04 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ05 | OfLExSCG | CZ05 | 1.3083
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ06 | OfLExSCG | CZ06 | 137.4656
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ07 | OfLExSCG | CZ07 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ08 | OfLExSCG | CZ08 | 183.2024
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ09 | OfLExSCG | CZ09 | 238.1117
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ10 | OfLExSCG | CZ10 | 32.2181
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ11 | OfLExSCG | CZ11 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ12 | OfLExSCG | CZ12 | 0
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ13 | OfLExSCG | CZ13 | 3.6548
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ14 | OfLExSCG | CZ14 | 7.4876
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ15 | OfLExSCG | CZ15 | 8.8041
ComIOUterr | OfLExSCG | IOU | SCG | SCG | OfL | Ex | Multiple | Any | OfLExSCGCZ16 | OfLExSCG | CZ16 | 3.4486
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ01 | OfSExSCG | CZ01 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ02 | OfSExSCG | CZ02 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ03 | OfSExSCG | CZ03 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ04 | OfSExSCG | CZ04 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ05 | OfSExSCG | CZ05 | 0.3105
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ06 | OfSExSCG | CZ06 | 30.2259
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ07 | OfSExSCG | CZ07 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ08 | OfSExSCG | CZ08 | 39.1569
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ09 | OfSExSCG | CZ09 | 42.7612
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ10 | OfSExSCG | CZ10 | 24.8649
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ11 | OfSExSCG | CZ11 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ12 | OfSExSCG | CZ12 | 0
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ13 | OfSExSCG | CZ13 | 5.7207
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ14 | OfSExSCG | CZ14 | 3.5403
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ15 | OfSExSCG | CZ15 | 6.7948
ComIOUterr | OfSExSCG | IOU | SCG | SCG | OfS | Ex | Multiple | Any | OfSExSCGCZ16 | OfSExSCG | CZ16 | 2.0179
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ01 | RSDExSCG | CZ01 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ02 | RSDExSCG | CZ02 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ03 | RSDExSCG | CZ03 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ04 | RSDExSCG | CZ04 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ05 | RSDExSCG | CZ05 | 0.13278
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ06 | RSDExSCG | CZ06 | 10.2066
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ07 | RSDExSCG | CZ07 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ08 | RSDExSCG | CZ08 | 12.6349
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ09 | RSDExSCG | CZ09 | 14.0831
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ10 | RSDExSCG | CZ10 | 9.0972
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ11 | RSDExSCG | CZ11 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ12 | RSDExSCG | CZ12 | 0
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ13 | RSDExSCG | CZ13 | 0.73034
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ14 | RSDExSCG | CZ14 | 1.9086
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ15 | RSDExSCG | CZ15 | 1.7798
ComIOUterr | RSDExSCG | IOU | SCG | SCG | RSD | Ex | Multiple | Any | RSDExSCGCZ16 | RSDExSCG | CZ16 | 0.73716
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ01 | RFFExSCG | CZ01 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ02 | RFFExSCG | CZ02 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ03 | RFFExSCG | CZ03 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ04 | RFFExSCG | CZ04 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ05 | RFFExSCG | CZ05 | 0.13278
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ06 | RFFExSCG | CZ06 | 10.2066
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ07 | RFFExSCG | CZ07 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ08 | RFFExSCG | CZ08 | 12.6349
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ09 | RFFExSCG | CZ09 | 14.0831
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ10 | RFFExSCG | CZ10 | 9.0972
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ11 | RFFExSCG | CZ11 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ12 | RFFExSCG | CZ12 | 0
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ13 | RFFExSCG | CZ13 | 0.73034
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ14 | RFFExSCG | CZ14 | 1.9086
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ15 | RFFExSCG | CZ15 | 1.7798
ComIOUterr | RFFExSCG | IOU | SCG | SCG | RFF | Ex | Multiple | Any | RFFExSCGCZ16 | RFFExSCG | CZ16 | 0.73716
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ01 | Rt3ExSCG | CZ01 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ02 | Rt3ExSCG | CZ02 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ03 | Rt3ExSCG | CZ03 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ04 | Rt3ExSCG | CZ04 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ05 | Rt3ExSCG | CZ05 | 0.63007
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ06 | Rt3ExSCG | CZ06 | 38.5094
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ07 | Rt3ExSCG | CZ07 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ08 | Rt3ExSCG | CZ08 | 46.7153
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ09 | Rt3ExSCG | CZ09 | 48.7408
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ10 | Rt3ExSCG | CZ10 | 30.9056
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ11 | Rt3ExSCG | CZ11 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ12 | Rt3ExSCG | CZ12 | 0
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ13 | Rt3ExSCG | CZ13 | 4.0005
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ14 | Rt3ExSCG | CZ14 | 5.8068
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ15 | Rt3ExSCG | CZ15 | 4.3153
ComIOUterr | Rt3ExSCG | IOU | SCG | SCG | Rt3 | Ex | Multiple | Any | Rt3ExSCGCZ16 | Rt3ExSCG | CZ16 | 1.1979
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ01 | RtLExSCG | CZ01 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ02 | RtLExSCG | CZ02 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ03 | RtLExSCG | CZ03 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ04 | RtLExSCG | CZ04 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ05 | RtLExSCG | CZ05 | 0.63007
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ06 | RtLExSCG | CZ06 | 38.5094
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ07 | RtLExSCG | CZ07 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ08 | RtLExSCG | CZ08 | 46.7153
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ09 | RtLExSCG | CZ09 | 48.7408
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ10 | RtLExSCG | CZ10 | 30.9056
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ11 | RtLExSCG | CZ11 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ12 | RtLExSCG | CZ12 | 0
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ13 | RtLExSCG | CZ13 | 4.0005
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ14 | RtLExSCG | CZ14 | 5.8068
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ15 | RtLExSCG | CZ15 | 4.3153
ComIOUterr | RtLExSCG | IOU | SCG | SCG | RtL | Ex | Multiple | Any | RtLExSCGCZ16 | RtLExSCG | CZ16 | 1.1979
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ01 | RtSExSCG | CZ01 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ02 | RtSExSCG | CZ02 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ03 | RtSExSCG | CZ03 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ04 | RtSExSCG | CZ04 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ05 | RtSExSCG | CZ05 | 0.63007
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ06 | RtSExSCG | CZ06 | 38.5094
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ07 | RtSExSCG | CZ07 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ08 | RtSExSCG | CZ08 | 46.7153
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ09 | RtSExSCG | CZ09 | 48.7408
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ10 | RtSExSCG | CZ10 | 30.9056
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ11 | RtSExSCG | CZ11 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ12 | RtSExSCG | CZ12 | 0
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ13 | RtSExSCG | CZ13 | 4.0005
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ14 | RtSExSCG | CZ14 | 5.8068
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ15 | RtSExSCG | CZ15 | 4.3153
ComIOUterr | RtSExSCG | IOU | SCG | SCG | RtS | Ex | Multiple | Any | RtSExSCGCZ16 | RtSExSCG | CZ16 | 1.1979
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ01 | SCnExSCG | CZ01 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ02 | SCnExSCG | CZ02 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ03 | SCnExSCG | CZ03 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ04 | SCnExSCG | CZ04 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ05 | SCnExSCG | CZ05 | 0.03265
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ06 | SCnExSCG | CZ06 | 33.0727
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ07 | SCnExSCG | CZ07 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ08 | SCnExSCG | CZ08 | 94.7981
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ09 | SCnExSCG | CZ09 | 61.569
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ10 | SCnExSCG | CZ10 | 67.8886
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ11 | SCnExSCG | CZ11 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ12 | SCnExSCG | CZ12 | 0
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ13 | SCnExSCG | CZ13 | 3.2924
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ14 | SCnExSCG | CZ14 | 1.6308
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ15 | SCnExSCG | CZ15 | 1.2471
ComIOUterr | SCnExSCG | IOU | SCG | SCG | SCn | Ex | Multiple | Any | SCnExSCGCZ16 | SCnExSCG | CZ16 | 1.2978
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ01 | SUnExSCG | CZ01 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ02 | SUnExSCG | CZ02 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ03 | SUnExSCG | CZ03 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ04 | SUnExSCG | CZ04 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ05 | SUnExSCG | CZ05 | 0.03265
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ06 | SUnExSCG | CZ06 | 33.0727
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ07 | SUnExSCG | CZ07 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ08 | SUnExSCG | CZ08 | 94.7981
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ09 | SUnExSCG | CZ09 | 61.569
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ10 | SUnExSCG | CZ10 | 67.8886
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ11 | SUnExSCG | CZ11 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ12 | SUnExSCG | CZ12 | 0
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ13 | SUnExSCG | CZ13 | 3.2924
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ14 | SUnExSCG | CZ14 | 1.6308
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ15 | SUnExSCG | CZ15 | 1.2471
ComIOUterr | SUnExSCG | IOU | SCG | SCG | SUn | Ex | Multiple | Any | SUnExSCGCZ16 | SUnExSCG | CZ16 | 1.2978
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ01 | WRfExSCG | CZ01 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ02 | WRfExSCG | CZ02 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ03 | WRfExSCG | CZ03 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ04 | WRfExSCG | CZ04 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ05 | WRfExSCG | CZ05 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ06 | WRfExSCG | CZ06 | 4.7559
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ07 | WRfExSCG | CZ07 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ08 | WRfExSCG | CZ08 | 6.6073
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ09 | WRfExSCG | CZ09 | 4.6003
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ10 | WRfExSCG | CZ10 | 3.2777
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ11 | WRfExSCG | CZ11 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ12 | WRfExSCG | CZ12 | 0
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ13 | WRfExSCG | CZ13 | 2.8029
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ14 | WRfExSCG | CZ14 | 0.04439
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ15 | WRfExSCG | CZ15 | 0.21278
ComIOUterr | WRfExSCG | IOU | SCG | SCG | WRf | Ex | Multiple | Any | WRfExSCGCZ16 | WRfExSCG | CZ16 | 0.0587
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ01 | AsmNewSCG | CZ01 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ02 | AsmNewSCG | CZ02 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ03 | AsmNewSCG | CZ03 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ04 | AsmNewSCG | CZ04 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ05 | AsmNewSCG | CZ05 | 0.017567
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ06 | AsmNewSCG | CZ06 | 1.5975
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ07 | AsmNewSCG | CZ07 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ08 | AsmNewSCG | CZ08 | 2.3968
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ09 | AsmNewSCG | CZ09 | 1.99
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ10 | AsmNewSCG | CZ10 | 2.9381
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ11 | AsmNewSCG | CZ11 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ12 | AsmNewSCG | CZ12 | 0
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ13 | AsmNewSCG | CZ13 | 0.223
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ14 | AsmNewSCG | CZ14 | 0.48587
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ15 | AsmNewSCG | CZ15 | 1.0635
ComIOUterr | AsmNewSCG | IOU | Any | SCG | Asm | New | Multiple | Any | AsmNewSCGCZ16 | AsmNewSCG | CZ16 | 0.306
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ01 | EPrNewSCG | CZ01 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ02 | EPrNewSCG | CZ02 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ03 | EPrNewSCG | CZ03 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ04 | EPrNewSCG | CZ04 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ05 | EPrNewSCG | CZ05 | 0.0011333
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ06 | EPrNewSCG | CZ06 | 0.22457
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ07 | EPrNewSCG | CZ07 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ08 | EPrNewSCG | CZ08 | 0.4033
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ09 | EPrNewSCG | CZ09 | 0.35527
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ10 | EPrNewSCG | CZ10 | 0.5695
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ11 | EPrNewSCG | CZ11 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ12 | EPrNewSCG | CZ12 | 0
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ13 | EPrNewSCG | CZ13 | 0.12477
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ14 | EPrNewSCG | CZ14 | 0.12883
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ15 | EPrNewSCG | CZ15 | 0.050767
ComIOUterr | EPrNewSCG | IOU | Any | SCG | EPr | New | Multiple | Any | EPrNewSCGCZ16 | EPrNewSCG | CZ16 | 0.0672
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ01 | ESeNewSCG | CZ01 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ02 | ESeNewSCG | CZ02 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ03 | ESeNewSCG | CZ03 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ04 | ESeNewSCG | CZ04 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ05 | ESeNewSCG | CZ05 | 0.0011333
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ06 | ESeNewSCG | CZ06 | 0.22457
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ07 | ESeNewSCG | CZ07 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ08 | ESeNewSCG | CZ08 | 0.4033
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ09 | ESeNewSCG | CZ09 | 0.35527
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ10 | ESeNewSCG | CZ10 | 0.5695
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ11 | ESeNewSCG | CZ11 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ12 | ESeNewSCG | CZ12 | 0
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ13 | ESeNewSCG | CZ13 | 0.12477
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ14 | ESeNewSCG | CZ14 | 0.12883
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ15 | ESeNewSCG | CZ15 | 0.050767
ComIOUterr | ESeNewSCG | IOU | Any | SCG | ESe | New | Multiple | Any | ESeNewSCGCZ16 | ESeNewSCG | CZ16 | 0.0672
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ01 | ECCNewSCG | CZ01 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ02 | ECCNewSCG | CZ02 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ03 | ECCNewSCG | CZ03 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ04 | ECCNewSCG | CZ04 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ05 | ECCNewSCG | CZ05 | 0.0005
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ06 | ECCNewSCG | CZ06 | 0.47035
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ07 | ECCNewSCG | CZ07 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ08 | ECCNewSCG | CZ08 | 0.76105
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ09 | ECCNewSCG | CZ09 | 0.4744
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ10 | ECCNewSCG | CZ10 | 0.42155
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ11 | ECCNewSCG | CZ11 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ12 | ECCNewSCG | CZ12 | 0
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ13 | ECCNewSCG | CZ13 | 0.1116
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ14 | ECCNewSCG | CZ14 | 0.1407
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ15 | ECCNewSCG | CZ15 | 0.12265
ComIOUterr | ECCNewSCG | IOU | Any | SCG | ECC | New | Multiple | Any | ECCNewSCGCZ16 | ECCNewSCG | CZ16 | 0.2769
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ01 | EUnNewSCG | CZ01 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ02 | EUnNewSCG | CZ02 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ03 | EUnNewSCG | CZ03 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ04 | EUnNewSCG | CZ04 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ05 | EUnNewSCG | CZ05 | 0.0005
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ06 | EUnNewSCG | CZ06 | 0.47035
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ07 | EUnNewSCG | CZ07 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ08 | EUnNewSCG | CZ08 | 0.76105
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ09 | EUnNewSCG | CZ09 | 0.4744
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ10 | EUnNewSCG | CZ10 | 0.42155
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ11 | EUnNewSCG | CZ11 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ12 | EUnNewSCG | CZ12 | 0
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ13 | EUnNewSCG | CZ13 | 0.1116
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ14 | EUnNewSCG | CZ14 | 0.1407
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ15 | EUnNewSCG | CZ15 | 0.12265
ComIOUterr | EUnNewSCG | IOU | Any | SCG | EUn | New | Multiple | Any | EUnNewSCGCZ16 | EUnNewSCG | CZ16 | 0.2769
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ01 | ERCNewSCG | CZ01 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ02 | ERCNewSCG | CZ02 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ03 | ERCNewSCG | CZ03 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ04 | ERCNewSCG | CZ04 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ05 | ERCNewSCG | CZ05 | 0.0011333
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ06 | ERCNewSCG | CZ06 | 0.22457
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ07 | ERCNewSCG | CZ07 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ08 | ERCNewSCG | CZ08 | 0.4033
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ09 | ERCNewSCG | CZ09 | 0.35527
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ10 | ERCNewSCG | CZ10 | 0.5695
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ11 | ERCNewSCG | CZ11 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ12 | ERCNewSCG | CZ12 | 0
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ13 | ERCNewSCG | CZ13 | 0.12477
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ14 | ERCNewSCG | CZ14 | 0.12883
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ15 | ERCNewSCG | CZ15 | 0.050767
ComIOUterr | ERCNewSCG | IOU | Any | SCG | ERC | New | Multiple | Any | ERCNewSCGCZ16 | ERCNewSCG | CZ16 | 0.0672
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ01 | GroNewSCG | CZ01 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ02 | GroNewSCG | CZ02 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ03 | GroNewSCG | CZ03 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ04 | GroNewSCG | CZ04 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ05 | GroNewSCG | CZ05 | 0.02
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ06 | GroNewSCG | CZ06 | 1.1204
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ07 | GroNewSCG | CZ07 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ08 | GroNewSCG | CZ08 | 1.7137
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ09 | GroNewSCG | CZ09 | 1.6596
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ10 | GroNewSCG | CZ10 | 2.0009
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ11 | GroNewSCG | CZ11 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ12 | GroNewSCG | CZ12 | 0
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ13 | GroNewSCG | CZ13 | 0.2498
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ14 | GroNewSCG | CZ14 | 0.4414
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ15 | GroNewSCG | CZ15 | 0.2813
ComIOUterr | GroNewSCG | IOU | Any | SCG | Gro | New | Multiple | Any | GroNewSCGCZ16 | GroNewSCG | CZ16 | 0.1751
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ01 | HspNewSCG | CZ01 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ02 | HspNewSCG | CZ02 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ03 | HspNewSCG | CZ03 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ04 | HspNewSCG | CZ04 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ05 | HspNewSCG | CZ05 | 0.02495
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ06 | HspNewSCG | CZ06 | 0.45235
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ07 | HspNewSCG | CZ07 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ08 | HspNewSCG | CZ08 | 0.54535
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ09 | HspNewSCG | CZ09 | 0.7459
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ10 | HspNewSCG | CZ10 | 0.46295
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ11 | HspNewSCG | CZ11 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ12 | HspNewSCG | CZ12 | 0
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ13 | HspNewSCG | CZ13 | 0.0707
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ14 | HspNewSCG | CZ14 | 0.0741
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ15 | HspNewSCG | CZ15 | 0.0959
ComIOUterr | HspNewSCG | IOU | Any | SCG | Hsp | New | Multiple | Any | HspNewSCGCZ16 | HspNewSCG | CZ16 | 0.05715
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ01 | NrsNewSCG | CZ01 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ02 | NrsNewSCG | CZ02 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ03 | NrsNewSCG | CZ03 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ04 | NrsNewSCG | CZ04 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ05 | NrsNewSCG | CZ05 | 0.02495
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ06 | NrsNewSCG | CZ06 | 0.45235
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ07 | NrsNewSCG | CZ07 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ08 | NrsNewSCG | CZ08 | 0.54535
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ09 | NrsNewSCG | CZ09 | 0.7459
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ10 | NrsNewSCG | CZ10 | 0.46295
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ11 | NrsNewSCG | CZ11 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ12 | NrsNewSCG | CZ12 | 0
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ13 | NrsNewSCG | CZ13 | 0.0707
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ14 | NrsNewSCG | CZ14 | 0.0741
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ15 | NrsNewSCG | CZ15 | 0.0959
ComIOUterr | NrsNewSCG | IOU | Any | SCG | Nrs | New | Multiple | Any | NrsNewSCGCZ16 | NrsNewSCG | CZ16 | 0.05715
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ01 | HtlNewSCG | CZ01 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ02 | HtlNewSCG | CZ02 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ03 | HtlNewSCG | CZ03 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ04 | HtlNewSCG | CZ04 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ05 | HtlNewSCG | CZ05 | 0.00345
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ06 | HtlNewSCG | CZ06 | 0.56415
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ07 | HtlNewSCG | CZ07 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ08 | HtlNewSCG | CZ08 | 0.4726
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ09 | HtlNewSCG | CZ09 | 0.86075
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ10 | HtlNewSCG | CZ10 | 0.21475
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ11 | HtlNewSCG | CZ11 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ12 | HtlNewSCG | CZ12 | 0
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ13 | HtlNewSCG | CZ13 | 0.02975
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ14 | HtlNewSCG | CZ14 | 0.0971
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ15 | HtlNewSCG | CZ15 | 0.5492
ComIOUterr | HtlNewSCG | IOU | Any | SCG | Htl | New | Multiple | Any | HtlNewSCGCZ16 | HtlNewSCG | CZ16 | 0.1157
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ01 | MtlNewSCG | CZ01 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ02 | MtlNewSCG | CZ02 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ03 | MtlNewSCG | CZ03 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ04 | MtlNewSCG | CZ04 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ05 | MtlNewSCG | CZ05 | 0.00345
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ06 | MtlNewSCG | CZ06 | 0.56415
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ07 | MtlNewSCG | CZ07 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ08 | MtlNewSCG | CZ08 | 0.4726
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ09 | MtlNewSCG | CZ09 | 0.86075
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ10 | MtlNewSCG | CZ10 | 0.21475
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ11 | MtlNewSCG | CZ11 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ12 | MtlNewSCG | CZ12 | 0
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ13 | MtlNewSCG | CZ13 | 0.02975
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ14 | MtlNewSCG | CZ14 | 0.0971
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ15 | MtlNewSCG | CZ15 | 0.5492
ComIOUterr | MtlNewSCG | IOU | Any | SCG | Mtl | New | Multiple | Any | MtlNewSCGCZ16 | MtlNewSCG | CZ16 | 0.1157
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ01 | MBTNewSCG | CZ01 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ02 | MBTNewSCG | CZ02 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ03 | MBTNewSCG | CZ03 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ04 | MBTNewSCG | CZ04 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ05 | MBTNewSCG | CZ05 | 0.017567
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ06 | MBTNewSCG | CZ06 | 1.5975
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ07 | MBTNewSCG | CZ07 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ08 | MBTNewSCG | CZ08 | 2.3968
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ09 | MBTNewSCG | CZ09 | 1.99
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ10 | MBTNewSCG | CZ10 | 2.9381
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ11 | MBTNewSCG | CZ11 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ12 | MBTNewSCG | CZ12 | 0
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ13 | MBTNewSCG | CZ13 | 0.223
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ14 | MBTNewSCG | CZ14 | 0.48587
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ15 | MBTNewSCG | CZ15 | 1.0635
ComIOUterr | MBTNewSCG | IOU | Any | SCG | MBT | New | Multiple | Any | MBTNewSCGCZ16 | MBTNewSCG | CZ16 | 0.306
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ01 | MLINewSCG | CZ01 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ02 | MLINewSCG | CZ02 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ03 | MLINewSCG | CZ03 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ04 | MLINewSCG | CZ04 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ05 | MLINewSCG | CZ05 | 0.017567
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ06 | MLINewSCG | CZ06 | 1.5975
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ07 | MLINewSCG | CZ07 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ08 | MLINewSCG | CZ08 | 2.3968
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ09 | MLINewSCG | CZ09 | 1.99
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ10 | MLINewSCG | CZ10 | 2.9381
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ11 | MLINewSCG | CZ11 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ12 | MLINewSCG | CZ12 | 0
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ13 | MLINewSCG | CZ13 | 0.223
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ14 | MLINewSCG | CZ14 | 0.48587
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ15 | MLINewSCG | CZ15 | 1.0635
ComIOUterr | MLINewSCG | IOU | Any | SCG | MLI | New | Multiple | Any | MLINewSCGCZ16 | MLINewSCG | CZ16 | 0.306
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ01 | OfLNewSCG | CZ01 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ02 | OfLNewSCG | CZ02 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ03 | OfLNewSCG | CZ03 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ04 | OfLNewSCG | CZ04 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ05 | OfLNewSCG | CZ05 | 0.021
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ06 | OfLNewSCG | CZ06 | 2.8514
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ07 | OfLNewSCG | CZ07 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ08 | OfLNewSCG | CZ08 | 4.0797
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ09 | OfLNewSCG | CZ09 | 5.9253
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ10 | OfLNewSCG | CZ10 | 2.1266
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ11 | OfLNewSCG | CZ11 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ12 | OfLNewSCG | CZ12 | 0
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ13 | OfLNewSCG | CZ13 | 0.1959
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ14 | OfLNewSCG | CZ14 | 0.3814
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ15 | OfLNewSCG | CZ15 | 0.5811
ComIOUterr | OfLNewSCG | IOU | Any | SCG | OfL | New | Multiple | Any | OfLNewSCGCZ16 | OfLNewSCG | CZ16 | 0.1713
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ01 | OfSNewSCG | CZ01 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ02 | OfSNewSCG | CZ02 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ03 | OfSNewSCG | CZ03 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ04 | OfSNewSCG | CZ04 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ05 | OfSNewSCG | CZ05 | 0.012
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ06 | OfSNewSCG | CZ06 | 1.1343
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ07 | OfSNewSCG | CZ07 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ08 | OfSNewSCG | CZ08 | 1.4458
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ09 | OfSNewSCG | CZ09 | 1.4484
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ10 | OfSNewSCG | CZ10 | 1.5809
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ11 | OfSNewSCG | CZ11 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ12 | OfSNewSCG | CZ12 | 0
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ13 | OfSNewSCG | CZ13 | 0.2368
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ14 | OfSNewSCG | CZ14 | 0.203
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ15 | OfSNewSCG | CZ15 | 0.432
ComIOUterr | OfSNewSCG | IOU | Any | SCG | OfS | New | Multiple | Any | OfSNewSCGCZ16 | OfSNewSCG | CZ16 | 0.1026
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ01 | RSDNewSCG | CZ01 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ02 | RSDNewSCG | CZ02 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ03 | RSDNewSCG | CZ03 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ04 | RSDNewSCG | CZ04 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ05 | RSDNewSCG | CZ05 | 0.007195
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ06 | RSDNewSCG | CZ06 | 0.53298
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ07 | RSDNewSCG | CZ07 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ08 | RSDNewSCG | CZ08 | 0.63989
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ09 | RSDNewSCG | CZ09 | 0.54983
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ10 | RSDNewSCG | CZ10 | 0.64264
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ11 | RSDNewSCG | CZ11 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ12 | RSDNewSCG | CZ12 | 0
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ13 | RSDNewSCG | CZ13 | 0.043635
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ14 | RSDNewSCG | CZ14 | 0.1231
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ15 | RSDNewSCG | CZ15 | 0.12574
ComIOUterr | RSDNewSCG | IOU | Any | SCG | RSD | New | Multiple | Any | RSDNewSCGCZ16 | RSDNewSCG | CZ16 | 0.04724
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ01 | RFFNewSCG | CZ01 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ02 | RFFNewSCG | CZ02 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ03 | RFFNewSCG | CZ03 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ04 | RFFNewSCG | CZ04 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ05 | RFFNewSCG | CZ05 | 0.007195
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ06 | RFFNewSCG | CZ06 | 0.53298
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ07 | RFFNewSCG | CZ07 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ08 | RFFNewSCG | CZ08 | 0.63989
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ09 | RFFNewSCG | CZ09 | 0.54983
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ10 | RFFNewSCG | CZ10 | 0.64264
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ11 | RFFNewSCG | CZ11 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ12 | RFFNewSCG | CZ12 | 0
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ13 | RFFNewSCG | CZ13 | 0.043635
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ14 | RFFNewSCG | CZ14 | 0.1231
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ15 | RFFNewSCG | CZ15 | 0.12574
ComIOUterr | RFFNewSCG | IOU | Any | SCG | RFF | New | Multiple | Any | RFFNewSCGCZ16 | RFFNewSCG | CZ16 | 0.04724
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ01 | Rt3NewSCG | CZ01 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ02 | Rt3NewSCG | CZ02 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ03 | Rt3NewSCG | CZ03 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ04 | Rt3NewSCG | CZ04 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ05 | Rt3NewSCG | CZ05 | 0.0288
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ06 | Rt3NewSCG | CZ06 | 1.7774
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ07 | Rt3NewSCG | CZ07 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ08 | Rt3NewSCG | CZ08 | 2.1797
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ09 | Rt3NewSCG | CZ09 | 2.3601
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ10 | Rt3NewSCG | CZ10 | 2.7777
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ11 | Rt3NewSCG | CZ11 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ12 | Rt3NewSCG | CZ12 | 0
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ13 | Rt3NewSCG | CZ13 | 0.30547
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ14 | Rt3NewSCG | CZ14 | 0.43163
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ15 | Rt3NewSCG | CZ15 | 0.38783
ComIOUterr | Rt3NewSCG | IOU | Any | SCG | Rt3 | New | Multiple | Any | Rt3NewSCGCZ16 | Rt3NewSCG | CZ16 | 0.092833
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ01 | RtLNewSCG | CZ01 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ02 | RtLNewSCG | CZ02 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ03 | RtLNewSCG | CZ03 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ04 | RtLNewSCG | CZ04 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ05 | RtLNewSCG | CZ05 | 0.0288
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ06 | RtLNewSCG | CZ06 | 1.7774
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ07 | RtLNewSCG | CZ07 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ08 | RtLNewSCG | CZ08 | 2.1797
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ09 | RtLNewSCG | CZ09 | 2.3601
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ10 | RtLNewSCG | CZ10 | 2.7777
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ11 | RtLNewSCG | CZ11 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ12 | RtLNewSCG | CZ12 | 0
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ13 | RtLNewSCG | CZ13 | 0.30547
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ14 | RtLNewSCG | CZ14 | 0.43163
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ15 | RtLNewSCG | CZ15 | 0.38783
ComIOUterr | RtLNewSCG | IOU | Any | SCG | RtL | New | Multiple | Any | RtLNewSCGCZ16 | RtLNewSCG | CZ16 | 0.092833
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ01 | RtSNewSCG | CZ01 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ02 | RtSNewSCG | CZ02 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ03 | RtSNewSCG | CZ03 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ04 | RtSNewSCG | CZ04 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ05 | RtSNewSCG | CZ05 | 0.0288
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ06 | RtSNewSCG | CZ06 | 1.7774
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ07 | RtSNewSCG | CZ07 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ08 | RtSNewSCG | CZ08 | 2.1797
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ09 | RtSNewSCG | CZ09 | 2.3601
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ10 | RtSNewSCG | CZ10 | 2.7777
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ11 | RtSNewSCG | CZ11 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ12 | RtSNewSCG | CZ12 | 0
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ13 | RtSNewSCG | CZ13 | 0.30547
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ14 | RtSNewSCG | CZ14 | 0.43163
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ15 | RtSNewSCG | CZ15 | 0.38783
ComIOUterr | RtSNewSCG | IOU | Any | SCG | RtS | New | Multiple | Any | RtSNewSCGCZ16 | RtSNewSCG | CZ16 | 0.092833
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ01 | SCnNewSCG | CZ01 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ02 | SCnNewSCG | CZ02 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ03 | SCnNewSCG | CZ03 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ04 | SCnNewSCG | CZ04 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ05 | SCnNewSCG | CZ05 | 0.0013
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ06 | SCnNewSCG | CZ06 | 1.3821
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ07 | SCnNewSCG | CZ07 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ08 | SCnNewSCG | CZ08 | 3.8928
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ09 | SCnNewSCG | CZ09 | 2.7921
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ10 | SCnNewSCG | CZ10 | 11.1073
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ11 | SCnNewSCG | CZ11 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ12 | SCnNewSCG | CZ12 | 0
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ13 | SCnNewSCG | CZ13 | 0.376
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ14 | SCnNewSCG | CZ14 | 0.21515
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ15 | SCnNewSCG | CZ15 | 0.20405
ComIOUterr | SCnNewSCG | IOU | Any | SCG | SCn | New | Multiple | Any | SCnNewSCGCZ16 | SCnNewSCG | CZ16 | 0.20215
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ01 | SUnNewSCG | CZ01 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ02 | SUnNewSCG | CZ02 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ03 | SUnNewSCG | CZ03 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ04 | SUnNewSCG | CZ04 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ05 | SUnNewSCG | CZ05 | 0.0013
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ06 | SUnNewSCG | CZ06 | 1.3821
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ07 | SUnNewSCG | CZ07 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ08 | SUnNewSCG | CZ08 | 3.8928
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ09 | SUnNewSCG | CZ09 | 2.7921
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ10 | SUnNewSCG | CZ10 | 11.1073
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ11 | SUnNewSCG | CZ11 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ12 | SUnNewSCG | CZ12 | 0
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ13 | SUnNewSCG | CZ13 | 0.376
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ14 | SUnNewSCG | CZ14 | 0.21515
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ15 | SUnNewSCG | CZ15 | 0.20405
ComIOUterr | SUnNewSCG | IOU | Any | SCG | SUn | New | Multiple | Any | SUnNewSCGCZ16 | SUnNewSCG | CZ16 | 0.20215
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ01 | WRfNewSCG | CZ01 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ02 | WRfNewSCG | CZ02 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ03 | WRfNewSCG | CZ03 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ04 | WRfNewSCG | CZ04 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ05 | WRfNewSCG | CZ05 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ06 | WRfNewSCG | CZ06 | 0.23303
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ07 | WRfNewSCG | CZ07 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ08 | WRfNewSCG | CZ08 | 0.325
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ09 | WRfNewSCG | CZ09 | 0.23693
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ10 | WRfNewSCG | CZ10 | 0.21974
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ11 | WRfNewSCG | CZ11 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ12 | WRfNewSCG | CZ12 | 0
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ13 | WRfNewSCG | CZ13 | 0.29843
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ14 | WRfNewSCG | CZ14 | 0.0029
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ15 | WRfNewSCG | CZ15 | 0.01426
ComIOUterr | WRfNewSCG | IOU | Any | SCG | WRf | New | Multiple | Any | WRfNewSCGCZ16 | WRfNewSCG | CZ16 | 0.00608

## ECC Scheduling (hidden)
Space Name | Parent Floor | Activity Decsiption | Occupnacy Schedule
EL8 West Perim Spc (T.W13) | EL8 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch | EL4 Occ-C3 Sch | S1 Sys1 (PVVT) Cooling and Heating Schedule
EL8 West Perim Spc (G.W1) | EL8 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch | EL4 Occ-1 Sch
EL8 South Perim Spc (T.S14) | EL8 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch | EL1 Occ-1 Sch
EL8 South Perim Spc (G.S2) | EL8 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL8 North Perim Spc (T.N16) | EL8 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL8 North Perim Spc (G.N4) | EL8 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL8 East Perim Spc (T.E15) | EL8 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL8 East Perim Spc (G.E3) | EL8 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL8 Core Spc (T.C17) | EL8 Top Flr | Computer (Instruc/PC Lab) | EL4 Occ-1 Sch
EL8 Core Spc (G.C5) | EL8 Ground Flr | Computer (Instruc/PC Lab) | EL4 Occ-1 Sch
EL6 West Perim Spc (G.W2) | EL6 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL6 North Perim Spc (G.N1) | EL6 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL6 East Perim Spc (G.E3) | EL6 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL5 North Perim Spc (G.N1) | EL5 Ground Flr | Comm/Ind Work (Gen, Low) | EL1 Occ-1 Sch
EL4 West Perim Spc (T.W16) | EL4 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 West Perim Spc (G.W4) | EL4 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 South Perim Spc (T.S13) | EL4 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 South Perim Spc (G.S1) | EL4 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 North Perim Spc (T.N15) | EL4 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 North Perim Spc (G.N3) | EL4 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 East Perim Spc (T.E14) | EL4 Top Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 East Perim Spc (G.E2) | EL4 Ground Flr | Classroom / Lecture (86%) | EL4 Occ-C3 Sch
EL4 Core Spc (T.C17) | EL4 Top Flr | Computer (Instruc/PC Lab) | EL4 Occ-1 Sch
EL4 Core Spc (G.C5) | EL4 Ground Flr | Computer (Instruc/PC Lab) | EL4 Occ-1 Sch
EL2 West Perim Spc (G.W1) | EL2 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL2 South Perim Spc (G.S2) | EL2 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL2 North Perim Spc (G.N3) | EL2 Ground Flr | Classroom / Lecture | EL1 Occ-1 Sch
EL1 West Perim Spc (G.W1) | EL1 Ground Flr | Comm/Ind Work (Gen, Low) | EL1 Occ-1 Sch

## ESe Scheduling
Sapce Name | Parent Floor | Activity Description | Occupancy Schedule
E1 West Perim Spc (G.W1) | E1 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch | E1 Occ-1 Sch | E1 s2 WD | 2-4pm
E2 West Perim Spc (G.W1) | E2 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch | E4 Occ-C1 Sch | e1 s2 Sat | noon-4PM
E2 South Perim Spc (G.S2) | E2 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch | E17 Occ-1 Sch
E2 North Perim Spc (G.N3) | E2 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch |  | E4 S2 wd | 6-7am | 2-7pm |  | 3-7PM
E4 South Perim Spc (G.S1) | E4 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch |  | E4 S2 Sat | noon-5PM
E4 East Perim Spc (G.E2) | E4 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch |  | E17 s2 WD | 7-8am | nooon-1 | 4-6pm
E4 North Perim Spc (G.N3) | E4 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch |  | E17 S2 SAT | NOON-5pm
E4 West Perim Spc (G.W4) | E4 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E4 Core Spc (G.C5) | E4 Ground Flr | Computer (Instruc/PC Lab) | E1 Occ-1 Sch
E4 Core Spc (G.C6) | E4 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E5 North Perim Spc (G.N1) | E5 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E6 North Perim Spc (G.N1) | E6 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E6 West Perim Spc (G.W2) | E6 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E6 East Perim Spc (G.E3) | E6 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E8 West Perim Spc (G.W1) | E8 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E8 South Perim Spc (G.S2) | E8 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E8 East Perim Spc (G.E3) | E8 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E8 North Perim Spc (G.N4) | E8 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E8 Core Spc (G.C5) | E8 Ground Flr | Computer (Instruc/PC Lab) | E1 Occ-1 Sch
E8 Core Spc (G.C6) | E8 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E9 East Perim Spc (G.E1) | E9 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E10 East Perim Spc (G.E1) | E10 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E10 North Perim Spc (G.N2) | E10 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E10 South Perim Spc (G.S3) | E10 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch | [7 empty] | Setbacks
E12 North Perim Spc (G.N1) | E12 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch | [6 empty] | WD | 5-7PM
E12 West Perim Spc (G.W2) | E12 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch | [6 empty] | Sat | 1PM to after
E12 South Perim Spc (G.S3) | E12 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E12 East Perim Spc (G.E4) | E12 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E12 Core Spc (G.C5) | E12 Ground Flr | Computer (Instruc/PC Lab) | E1 Occ-1 Sch
E12 Core Spc (G.C6) | E12 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E13 South Perim Spc (G.S1) | E13 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E14 South Perim Spc (G.S1) | E14 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E14 East Perim Spc (G.E2) | E14 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E14 West Perim Spc (G.W3) | E14 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E16 East Perim Spc (G.E1) | E16 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E16 North Perim Spc (G.N2) | E16 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E16 West Perim Spc (G.W3) | E16 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E16 South Perim Spc (G.S4) | E16 Ground Flr | Classroom / Lecture (93%) | E4 Occ-C1 Sch
E16 Core Spc (G.C5) | E16 Ground Flr | Computer (Instruc/PC Lab) | E1 Occ-1 Sch
E16 Core Spc (G.C6) | E16 Ground Flr | Classroom / Lecture | E1 Occ-1 Sch
E17 West Perim Spc (G.W1) | E17 Ground Flr | Exercising Center / Gym | E17 Occ-1 Sch

## ESe Area
|  |  | Space Type | [12 empty] | Area |  | Total Area | 149994.4
E1 West Perim Spc (G.W1) | E1 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E1 Space Polygon 1 | V1 of Floor Polygon | 3750.9 | 48761.2 | Classroom Area | 94502
E2 West Perim Spc (G.W1) | E2 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 29.96 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E2 Space Polygon 1 | - undefined - | 1651.5 | 14863.7 | %classroom | 63%
E2 South Perim Spc (G.S2) | E2 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E2 Space Polygon 2 | V1 of Floor Polygon | 2080.7 | 18726.5
E2 North Perim Spc (G.N3) | E2 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 69.45 | 83.7 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E2 Space Polygon 3 | V3 of Floor Polygon | 2080.7 | 18726.5
E3 SW Perim Spc (G.SW1) | E3 Ground Flr | Conditioned | Dining Area | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E3 Space Polygon 1 | V1 of Floor Polygon | 5622.6 | 73093.2
E3 NE Perim Spc (G.NE2) | E3 Ground Flr | Conditioned | Kitchen and Food Prep | No | 70 | 98.25 | 83.95 | 0 | 180 | 13 | 1 | 1 | Use a POLYGON | E3 Space Polygon 2 | V3 of Floor Polygon | 2625.5 | 34132
E4 South Perim Spc (G.S1) | E4 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 1 | V1 of Floor Polygon | 4131 | 37179
E4 East Perim Spc (G.E2) | E4 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 0 | 0 | -90 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 2 | V2 of Floor Polygon | 1615.5 | 14539.5
E4 North Perim Spc (G.N3) | E4 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 83.85 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 3 | V3 of Floor Polygon | 4131 | 37179
E4 West Perim Spc (G.W4) | E4 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 83.85 | 0 | 90 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 4 | V4 of Floor Polygon | 1615.5 | 14539.5
E4 Core Spc (G.C5) | E4 Ground Flr | Conditioned | Computer (Instruc/PC Lab) | No | 70 | 30 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 5 | - undefined - | 770.6 | 6935.3
E4 Core Spc (G.C6) | E4 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 62.31 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E4 Space Polygon 6 | - undefined - | 1798.1 | 16182.5
E5 North Perim Spc (G.N1) | E5 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E5 Space Polygon 1 | V1 of Floor Polygon | 3750.9 | 48761.2
E6 North Perim Spc (G.N1) | E6 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 29.96 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E6 Space Polygon 1 | - undefined - | 1651.5 | 14863.7
E6 West Perim Spc (G.W2) | E6 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E6 Space Polygon 2 | V1 of Floor Polygon | 2080.7 | 18726.5
E6 East Perim Spc (G.E3) | E6 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 69.45 | 83.7 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E6 Space Polygon 3 | V3 of Floor Polygon | 2080.7 | 18726.5
E7 NW Perim Spc (G.NW1) | E7 Ground Flr | Conditioned | Dining Area | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E7 Space Polygon 1 | V1 of Floor Polygon | 5622.6 | 73093.2
E7 SE Perim Spc (G.SE2) | E7 Ground Flr | Conditioned | Kitchen and Food Prep | No | 70 | 98.25 | 83.95 | 0 | 180 | 13 | 1 | 1 | Use a POLYGON | E7 Space Polygon 2 | V3 of Floor Polygon | 2625.5 | 34132
E8 West Perim Spc (G.W1) | E8 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 1 | V1 of Floor Polygon | 4131 | 37179
E8 South Perim Spc (G.S2) | E8 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 0 | 0 | -90 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 2 | V2 of Floor Polygon | 1615.5 | 14539.5
E8 East Perim Spc (G.E3) | E8 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 83.85 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 3 | V3 of Floor Polygon | 4131 | 37179
E8 North Perim Spc (G.N4) | E8 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 83.85 | 0 | 90 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 4 | V4 of Floor Polygon | 1615.5 | 14539.5
E8 Core Spc (G.C5) | E8 Ground Flr | Conditioned | Computer (Instruc/PC Lab) | No | 70 | 30 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 5 | - undefined - | 770.6 | 6935.3
E8 Core Spc (G.C6) | E8 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 62.31 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E8 Space Polygon 6 | - undefined - | 1798.1 | 16182.5
E9 East Perim Spc (G.E1) | E9 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E9 Space Polygon 1 | V1 of Floor Polygon | 3750.9 | 48761.2
E10 East Perim Spc (G.E1) | E10 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 29.96 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E10 Space Polygon 1 | - undefined - | 1651.5 | 14863.7
E10 North Perim Spc (G.N2) | E10 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E10 Space Polygon 2 | V1 of Floor Polygon | 2080.7 | 18726.5
E10 South Perim Spc (G.S3) | E10 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 69.45 | 83.7 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E10 Space Polygon 3 | V3 of Floor Polygon | 2080.7 | 18726.5
E11 NE Perim Spc (G.NE1) | E11 Ground Flr | Conditioned | Dining Area | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E11 Space Polygon 1 | V1 of Floor Polygon | 5622.6 | 73093.2
E11 SW Perim Spc (G.SW2) | E11 Ground Flr | Conditioned | Kitchen and Food Prep | No | 70 | 98.25 | 83.95 | 0 | 180 | 13 | 1 | 1 | Use a POLYGON | E11 Space Polygon 2 | V3 of Floor Polygon | 2625.5 | 34132
E12 North Perim Spc (G.N1) | E12 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 1 | V1 of Floor Polygon | 4131 | 37179
E12 West Perim Spc (G.W2) | E12 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 0 | 0 | -90 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 2 | V2 of Floor Polygon | 1615.5 | 14539.5
E12 South Perim Spc (G.S3) | E12 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 83.85 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 3 | V3 of Floor Polygon | 4131 | 37179
E12 East Perim Spc (G.E4) | E12 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 83.85 | 0 | 90 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 4 | V4 of Floor Polygon | 1615.5 | 14539.5
E12 Core Spc (G.C5) | E12 Ground Flr | Conditioned | Computer (Instruc/PC Lab) | No | 70 | 30 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 5 | - undefined - | 770.6 | 6935.3
E12 Core Spc (G.C6) | E12 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 62.31 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E12 Space Polygon 6 | - undefined - | 1798.1 | 16182.5
E13 South Perim Spc (G.S1) | E13 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E13 Space Polygon 1 | V1 of Floor Polygon | 3750.9 | 48761.2
E14 South Perim Spc (G.S1) | E14 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 29.96 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E14 Space Polygon 1 | - undefined - | 1651.5 | 14863.7
E14 East Perim Spc (G.E2) | E14 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E14 Space Polygon 2 | V1 of Floor Polygon | 2080.7 | 18726.5
E14 West Perim Spc (G.W3) | E14 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 69.45 | 83.7 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E14 Space Polygon 3 | V3 of Floor Polygon | 2080.7 | 18726.5
E15 SE Perim Spc (G.SE1) | E15 Ground Flr | Conditioned | Dining Area | No | 70 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | Use a POLYGON | E15 Space Polygon 1 | V1 of Floor Polygon | 5622.6 | 73093.2
E15 NW Perim Spc (G.NW2) | E15 Ground Flr | Conditioned | Kitchen and Food Prep | No | 70 | 98.25 | 83.95 | 0 | 180 | 13 | 1 | 1 | Use a POLYGON | E15 Space Polygon 2 | V3 of Floor Polygon | 2625.5 | 34132
E16 East Perim Spc (G.E1) | E16 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 1 | V1 of Floor Polygon | 4131 | 37179
E16 North Perim Spc (G.N2) | E16 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 0 | 0 | -90 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 2 | V2 of Floor Polygon | 1615.5 | 14539.5
E16 West Perim Spc (G.W3) | E16 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 167.7 | 83.85 | 0 | 180 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 3 | V3 of Floor Polygon | 4131 | 37179
E16 South Perim Spc (G.S4) | E16 Ground Flr | Conditioned | Classroom / Lecture (93%) | No | 70 | 0 | 83.85 | 0 | 90 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 4 | V4 of Floor Polygon | 1615.5 | 14539.5
E16 Core Spc (G.C5) | E16 Ground Flr | Conditioned | Computer (Instruc/PC Lab) | No | 70 | 30 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 5 | - undefined - | 770.6 | 6935.3
E16 Core Spc (G.C6) | E16 Ground Flr | Conditioned | Classroom / Lecture | No | 70 | 62.31 | 30 | 0 | 0 | 9 | 1 | 1 | Use a POLYGON | E16 Space Polygon 6 | - undefined - | 1798.1 | 16182.5
E17 West Perim Spc (G.W1) | E17 Ground Flr | Conditioned | Exercising Center / Gym | No | 70 | 0 | 0 | 0 | 0 | 26 | 1 | 1 | Use a POLYGON | E17 Space Polygon 1 | V1 of Floor Polygon | 22500 | 585000

## EPr Areas
|  |  | Area Type |  | Total Area | 49997
EL1 East Perim Spc (G.E1) | EL1 Ground Flr | Conditioned | Classroom / Lecture | 5750.9 | Classroom area | 31494.2
EL1 NNE Perim Spc (G.NNE2) | EL1 Ground Flr | Conditioned | Classroom / Lecture | 3321.1 | % classroom | 62.99%
EL1 SSE Perim Spc (G.SSE3) | EL1 Ground Flr | Conditioned | Classroom / Lecture | 3321.1
EL1 West Perim Spc (G.W4) | EL1 Ground Flr | Conditioned | Classroom / Lecture | 3354 | Setbacks will be same as Ese
EL2 SSW Perim Spc (G.SSW1) | EL2 Ground Flr | Conditioned | Dining Area | 3753.9
EL2 North Perim Spc (G.N2) | EL2 Ground Flr | Conditioned | Exercising Center / Gym | 3746.9
EL2 East Perim Spc (G.E3) | EL2 Ground Flr | Conditioned | Kitchen and Food Prep | 1750.6
EL3 South Perim Spc (G.S1) | EL3 Ground Flr | Conditioned | Classroom / Lecture | 5750.9
EL3 ESE Perim Spc (G.ESE2) | EL3 Ground Flr | Conditioned | Classroom / Lecture | 3321.1
EL3 WSW Perim Spc (G.WSW3) | EL3 Ground Flr | Conditioned | Classroom / Lecture | 3321.1
EL3 North Perim Spc (G.N4) | EL3 Ground Flr | Conditioned | Classroom / Lecture | 3354
EL4 WNW Perim Spc (G.WNW1) | EL4 Ground Flr | Conditioned | Dining Area | 3753.9
EL4 East Perim Spc (G.E2) | EL4 Ground Flr | Conditioned | Exercising Center / Gym | 3746.9
EL4 South Perim Spc (G.S3) | EL4 Ground Flr | Conditioned | Kitchen and Food Prep | 1750.6

## EPr-Base-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 3972 | 2972 | 7063 | 7862 | 15562 | 8806 | 2845 | 18000 | 29279 | 14216 | 4778 | 1919 | 117275
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9794 | 8685 | 9854 | 7349 | 9415 | 4901 | 2401 | 6685 | 9565 | 9829 | 8703 | 4536 | 91718
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10536 | 10599 | 12070 | 8941 | 11397 | 5201 | 0 | 6006 | 11579 | 11822 | 10727 | 4715 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357 | 13283 | 15140 | 11597 | 14261 | 7256 | 1220 | 8160 | 14521 | 14797 | 13449 | 6718 | 133759
Total | 37659 | 35540 | 44127 | 35749 | 50636 | 26165 | 6466 | 38851 | 64943 | 50664 | 37656 | 17889 | 446345
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 72882 | 65294 | 61624 | 27464 | 18180 | 4334 | 0 | 1470 | 4694 | 20760 | 55401 | 42180 | 374283
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22624 | 22983 | 26387 | 19930 | 23400 | 10984 | 471 | 11660 | 21842 | 22610 | 21049 | 10390 | 214330
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 96629 | 89400 | 89298 | 48367 | 42778 | 15887 | 471 | 13773 | 27769 | 44623 | 77573 | 53084 | 599652
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 74.98 | 51.24 | 92.38 | 147.94 | 221.03 | 187.79 | 30.69 | 230.71 | 252.03 | 168.06 | 69.18 | 101.99 | 1628
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 21.64 | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 378.12
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 55.69 | 55.69 | 55.69 | 53.38 | 0 | 55.69 | 57.41 | 55.69 | 55.69 | 55.69 | 611.98
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 60.36 | 59.47 | 60.36 | 60.36 | 60.36 | 664.7
Total | 223.43 | 199.69 | 240.84 | 296.39 | 369.48 | 333.94 | 53.96 | 379.16 | 401.32 | 316.51 | 217.63 | 250.44 | 3282.81
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 1624879 | 1297441 | 1303186 | 1146663 | 580996 | 355797 | 0 | 130155 | 399399 | 648210 | 1580740 | 1562873 | 10630339
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 80795 | 80828 | 40890 | 80251 | 38986 | 74203 | 700 | 70019 | 69920 | 71253 | 73845 | 76687 | 758378
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1705674 | 1378269 | 1344076 | 1226914 | 619982 | 430000 | 700 | 200174 | 469319 | 719463 | 1654585 | 1639561 | 11388716
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\EPr-w09-v03-Base - Baseline Design
07/18/2018 @ 06:53:33

## EPr-Post-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 3662 | 2820 | 6198 | 6884 | 13743 | 7934 | 2845 | 16402 | 26611 | 12692 | 4661 | 1804 | 106256
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9800 | 8685 | 9872 | 7373 | 9475 | 4952 | 2401 | 6753 | 9752 | 9857 | 8708 | 4539 | 92168
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10536 | 10599 | 12070 | 8941 | 11397 | 5201 | 0 | 6006 | 11579 | 11822 | 10727 | 4715 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357 | 13283 | 15140 | 11597 | 14261 | 7256 | 1220 | 8160 | 14521 | 14797 | 13449 | 6718 | 133759
Total | 37355 | 35387 | 43279 | 34794 | 48876 | 25343 | 6466 | 37321 | 62463 | 49168 | 37545 | 17776 | 435775
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 74821 | 67601 | 62620 | 25963 | 21958 | 3939 | 0 | 2032 | 4260 | 24830 | 58357 | 40340 | 386721
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22618 | 22976 | 26377 | 19923 | 23386 | 10976 | 470 | 11651 | 21825 | 22597 | 21041 | 10387 | 214230
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 98562 | 91700 | 90285 | 46859 | 46542 | 15484 | 470 | 14327 | 27318 | 48680 | 80522 | 51241 | 611990
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 76.27 | 52.59 | 94.46 | 150.06 | 223.49 | 190.65 | 30.69 | 230.71 | 253.63 | 171.59 | 70.29 | 102.46 | 1646.88
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 21.64 | 32.41 | 32.41 | 32.41 | 32.41 | 32.41 | 378.12
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 55.69 | 55.69 | 55.69 | 53.38 | 0 | 55.69 | 57.41 | 55.69 | 55.69 | 55.69 | 611.98
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 60.36 | 59.47 | 60.36 | 60.36 | 60.36 | 664.7
Total | 224.72 | 201.04 | 242.92 | 298.52 | 371.95 | 336.79 | 53.96 | 379.16 | 402.91 | 320.04 | 218.74 | 250.92 | 3301.68
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 1624879 | 1243344 | 1677938 | 1144114 | 978310 | 294433 | 0 | 119513 | 373439 | 1154304 | 1534639 | 1791144 | 11936057
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 80795 | 80813 | 721 | 80250 | 683 | 74183 | 700 | 69998 | 69906 | 690 | 73831 | 728 | 533297
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1705674 | 1324157 | 1678659 | 1224363 | 978993 | 368615 | 700 | 189511 | 443344 | 1154995 | 1608470 | 1791873 | 12469355
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\EPr-w09-v03-Post - Baseline Design
07/18/2018 @ 07:06:51

## Ese-Base-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 10931.6 | 7145.4 | 20221.9 | 22174.5 | 46342.9 | 25870.6 | 7256.6 | 57364.3 | 94352.9 | 43484.6 | 13742.2 | 5324.1 | 354211.7
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31177.7 | 27510.2 | 31197.1 | 23370.8 | 29803.4 | 14886.6 | 6211.7 | 20897.7 | 30339.7 | 31101.4 | 27556.4 | 14222.6 | 288275.3
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 112829.5 | 105203.4 | 131769.9 | 106425.6 | 151978.5 | 78051.5 | 17988.5 | 120577.6 | 201773.7 | 153270.7 | 112668.3 | 53880.3 | 1346417.3
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 252780 | 219726 | 210140 | 86632 | 51132 | 9009 | 0 | 2223 | 8814 | 54628 | 180842 | 148161 | 1224088
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 103020 | 104883 | 120497 | 90741 | 106787 | 49585 | 1089 | 52680 | 99630 | 103076 | 95846 | 46469 | 974303
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 357909 | 326718 | 333034 | 179147 | 160196 | 59625 | 1089 | 56101 | 110744 | 160076 | 278798 | 195564 | 2219002
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 208.0183 | 129.3257 | 257.3451 | 421.1173 | 647.3107 | 530.1955 | 71.0093 | 705.2978 | 729.2067 | 492.5658 | 195.377 | 284.3112 | 4671.0806
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 53.5288 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 1093.4309
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 1539.762
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 2021.1528
Total | 624.6691 | 545.9765 | 673.9959 | 837.7681 | 1063.9615 | 946.8463 | 130.6136 | 1121.9486 | 1158.509 | 909.2166 | 612.0278 | 700.962 | 9326.4873
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 5086986 | 4077057 | 4448171 | 4099921 | 2176513 | 921292 | 0 | 0 | 1197952 | 2238404 | 4931785 | 4760086 | 33938164
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 364101 | 1882 | 2019 | 2007 | 1844 | 1733 | 1648 | 534976 | 1740 | 1877 | 1970 | 1953 | 917748
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34237 | 0 | 0 | 0 | 0 | 34237
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 5451087 | 4078939 | 4450190 | 4101927 | 2178357 | 923025 | 1648 | 569213 | 1199692 | 2240281 | 4933754 | 4762039 | 34890144
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ESe-w09-v03-airAC-Base - Baseline Design
07/17/2018 @ 16:17:25

## ESe-Post-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 9601.3 | 6311.3 | 16900.6 | 18745.5 | 40013.6 | 22733.5 | 7257.5 | 52149.5 | 85547 | 37873.4 | 12768.5 | 4766 | 314667.6
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31196.2 | 27510.2 | 31202.2 | 23409.7 | 29929.5 | 15003.3 | 6213 | 21259.5 | 31520.6 | 31240.5 | 27586.3 | 14243.5 | 290314.5
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 111517.6 | 104369.3 | 128453.7 | 103035.6 | 145775.3 | 75031.2 | 17990.6 | 115724.7 | 194148.7 | 147798.5 | 111724.6 | 53343.1 | 1308912.8
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 230956 | 201727 | 187197 | 80392 | 46703 | 7737 | 0 | 1846 | 7454 | 49337 | 160073 | 130617 | 1104038
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 103012 | 104877 | 120485 | 90730 | 106767 | 49574 | 1089 | 52665 | 99603 | 103057 | 95837 | 46468 | 974165
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 336076 | 308713 | 310079 | 172896 | 155747 | 58342 | 1089 | 55709 | 109358 | 154766 | 258019 | 178019 | 2098813
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 212.265 | 130.367 | 264.073 | 428.2901 | 659.2646 | 540.4509 | 71.0132 | 705.3005 | 742.9634 | 504.643 | 199.0713 | 285.6687 | 4743.3711
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 53.5288 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 94.5366 | 1093.4309
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 1539.762
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 2021.1528
Total | 628.9158 | 547.0178 | 680.7238 | 844.941 | 1075.9154 | 957.1017 | 130.6175 | 1121.9513 | 1172.2657 | 921.2938 | 615.7222 | 702.3195 | 9398.7764
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 5086986 | 4078259 | 4536958 | 4096550 | 2146914 | 780951 | 0 | 0 | 1145239 | 1860535 | 4967726 | 4820981 | 33521098
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 364101 | 1877 | 2028 | 2006 | 1839 | 1705 | 1648 | 534968 | 1718 | 327170 | 1967 | 1953 | 1242980
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34237 | 0 | 0 | 0 | 0 | 34237
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 5451087 | 4080136 | 4538987 | 4098556 | 2148753 | 782656 | 1648 | 569205 | 1146957 | 2187705 | 4969693 | 4822934 | 34798320
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ESe-w09-v03-Post - Baseline Design
07/18/2018 @ 06:47:43

## ERC-Post-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 154.4 | 107.4 | 290.1 | 295.6 | 597.1 | 447.1 | 405.1 | 811.9 | 1187.4 | 536 | 191.3 | 93.9 | 5117.4
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 608.5 | 492.2 | 542.7 | 449.5 | 417.2 | 337 | 304.2 | 404.1 | 445.5 | 431.7 | 529.6 | 542.8 | 5505.1
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 339.5 | 366.8 | 417.6 | 296.4 | 394.4 | 210.3 | 39.1 | 200.6 | 400.6 | 409 | 371.4 | 194.4 | 3639.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 528.1 | 571.1 | 652.2 | 464.9 | 611.7 | 331.8 | 67.3 | 313 | 625.2 | 635.6 | 577.4 | 307.8 | 5685.8
Total | 1630.5 | 1537.4 | 1902.6 | 1506.4 | 2020.4 | 1326.2 | 815.6 | 1729.7 | 2658.8 | 2012.3 | 1669.7 | 1138.8 | 19948.3
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 5501.3 | 3722.1 | 3678.1 | 2739.5 | 899.5 | 283.6 | 49.3 | 49.5 | 208.9 | 1216.8 | 3930.1 | 5437.3 | 27716
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 2248.9 | 2428.1 | 2757.1 | 2000.7 | 2462.1 | 1353 | 385.2 | 1209.5 | 2284.4 | 2401.5 | 2281.9 | 1387.4 | 23199.8
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 7750.1 | 6150.2 | 6435.2 | 4740.1 | 3361.6 | 1636.6 | 434.6 | 1259.1 | 2493.3 | 3618.3 | 6212.1 | 6824.7 | 50915.8
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 4.061 | 2.972 | 4.8 | 7.842 | 11.193 | 9.384 | 6.424 | 9.814 | 12.639 | 8.672 | 3.781 | 5.597 | 87.18
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 15.771
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 0.577 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 21.723
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 0.532 | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 25.933
Total | 9.607 | 8.517 | 10.346 | 13.388 | 16.739 | 14.93 | 8.848 | 15.36 | 18.185 | 14.217 | 9.327 | 11.143 | 150.607
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 67278 | 65661 | 62014 | 57273 | 36115 | 26737 | 21568 | 8337 | 34504 | 45615 | 75616 | 78181 | 578899
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 7736 | 7878 | 7869 | 704 | 7527 | 7216 | 648 | 6817 | 6874 | 7003 | 7259 | 7520 | 75051
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 75015 | 73539 | 69883 | 57977 | 43642 | 33953 | 22216 | 15154 | 41378 | 52618 | 82875 | 85701 | 653950
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ERC-w09-v03-Test - Post - Baseline Design
07/17/2018 @ 16:49:40

## ERC-Base-AC-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 208.8 | 145.2 | 337.6 | 345.5 | 679.5 | 493.4 | 405.1 | 861.6 | 1304.6 | 611.9 | 249.5 | 111.2 | 5754
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 598.6 | 485 | 530.9 | 445.5 | 408 | 335.7 | 304.2 | 398.9 | 437.6 | 421.2 | 525.7 | 541.5 | 5432.8
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 339.5 | 366.8 | 417.6 | 296.4 | 394.4 | 210.3 | 39.1 | 200.6 | 400.6 | 409 | 371.4 | 194.4 | 3639.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 528.1 | 571.1 | 652.2 | 464.9 | 611.7 | 331.8 | 67.3 | 313 | 625.2 | 635.6 | 577.4 | 307.8 | 5685.8
Total | 1675.1 | 1568 | 1938.3 | 1552.2 | 2093.5 | 1371.2 | 815.6 | 1774.1 | 2768 | 2077.6 | 1723.9 | 1154.9 | 20512.6 | 20454.9 | 57.7
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 5633.1 | 3800.3 | 3863.5 | 2798.3 | 924.1 | 287.8 | 49.3 | 50.1 | 213.5 | 1244 | 4087.3 | 5574.5 | 28525.6
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 2252 | 2430.4 | 2759.8 | 2002.9 | 2465.8 | 1355.1 | 385.2 | 1211.3 | 2288.7 | 2405.7 | 2285 | 1388.2 | 23230
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 7885.1 | 6230.6 | 6623.3 | 4801.1 | 3389.9 | 1642.9 | 434.6 | 1261.4 | 2502.1 | 3649.6 | 6372.3 | 6962.7 | 51755.7
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 4.082 | 2.969 | 4.939 | 7.837 | 11.188 | 9.57 | 6.424 | 9.809 | 12.872 | 8.666 | 3.776 | 5.593 | 87.726
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 1.314 | 15.771
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 0.577 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 21.723
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 0.532 | 2.309 | 2.309 | 2.309 | 2.309 | 2.309 | 25.933
Total | 9.628 | 8.515 | 10.485 | 13.383 | 16.734 | 15.116 | 8.848 | 15.355 | 18.418 | 14.212 | 9.322 | 11.139 | 151.153
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 67417 | 65803 | 61939 | 57273 | 36609 | 27039 | 21568 | 8332 | 34911 | 44205 | 75615 | 78256 | 578966
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 7737 | 7878 | 7869 | 704 | 7523 | 7218 | 648 | 6817 | 6876 | 6993 | 7259 | 7520 | 75043
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 75154 | 73681 | 69808 | 57977 | 44132 | 34257 | 22216 | 15149 | 41787 | 51198 | 82875 | 85776 | 654009
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ERC-w09-v03-Test - Baseline Design
07/17/2018 @ 16:51:16

## ESe-Base-HP-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 9310.29 | 6095.89 | 17977.87 | 20322.96 | 43863.27 | 25103.23 | 9101.4 | 56763 | 91586.05 | 40427.87 | 11998.91 | 4461.8 | 337012.56
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 17858.56 | 15987.59 | 15412.82 | 6123.27 | 3371.74 | 571.05 | 0 | 122.22 | 539.4 | 3539.5 | 12938.34 | 10696.35 | 87160.84
HP Supp. | 140.58 | 163.53 | 80.52 | 1.81 | 0 | 0 | 0 | 0 | 0 | 0 | 131.58 | 345.59 | 863.62
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 32162.63 | 27125.35 | 30760.73 | 23268.99 | 29502.41 | 18676.4 | 15060.07 | 25448.55 | 30642.68 | 31040.71 | 27389.66 | 15523 | 306601.16
Pumps & Aux. | 66.29 | 59.88 | 66.29 | 64.16 | 66.29 | 64.16 | 66.29 | 66.29 | 64.16 | 66.29 | 64.16 | 66.29 | 780.56
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.29 | 28106.77 | 31954.68 | 23920.64 | 30284.67 | 14385 | 1172.32 | 16504.09 | 30670.06 | 31392.53 | 28448.3 | 13187.55 | 278113.91
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.57 | 42381.22 | 48329.86 | 36895.61 | 45481.2 | 22845.21 | 3281.53 | 25745.31 | 46346.86 | 47225.82 | 42857.28 | 21079.79 | 425036.22
Total | 130192.21 | 119920.22 | 144582.77 | 110597.44 | 152569.58 | 81645.05 | 28681.62 | 124649.47 | 199849.2 | 153692.72 | 123828.23 | 65360.38 | 1435568.38
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 103032 | 104886 | 120516 | 90759 | 106816 | 49659 | 1200 | 52755 | 99686 | 103103 | 95853 | 46484 | 974748
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 105141 | 106995 | 122912 | 92532 | 109093 | 50689 | 1200 | 53954 | 101987 | 105476 | 97962 | 47418 | 995359
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 237.1885 | 411.1644 | 654.1511 | 530.048 | 69.0397 | 706.7332 | 734.2619 | 478.9846 | 0 | 263.4531 | 4085.0244
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 392.6331 | 351.9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.2121 | 0 | 1155.7529
HP Supp. | 40.9478 | 39.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2459 | 0 | 132.8203
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 58.1602 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 1083.5128
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10.1044 | 10.1044 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 138.4546 | 153.6401 | 138.4546 | 10.1044 | 138.4546 | 1154.7115
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 71.5292 | 71.5292 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 183.5705 | 181.0367 | 183.5705 | 71.5292 | 183.5705 | 1685.0288
Total | 608.5175 | 566.4711 | 652.5166 | 826.4925 | 1069.4792 | 945.3762 | 133.2754 | 1122.0613 | 1162.2417 | 894.3127 | 638.3947 | 678.7813 | 9297.917
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 605498 | 617275 | 618289 | 612669 | 589782 | 567086 | 1679 | 534969 | 533951 | 544113 | 563292 | 585272 | 6373874
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 34237 | 34237 | 34237 | 34237 | 34237 | 34237 | 0 | 34237 | 34237 | 34237 | 34237 | 34237 | 376607
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 639735 | 651512 | 652526 | 646906 | 624019 | 601323 | 1679 | 569205 | 568188 | 578350 | 597529 | 619509 | 6750481
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ESe-w09-v03-HP-Base - Baseline Design
07/18/2018 @ 09:19:17

## ESe-Post-HP-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 8229.56 | 5442.22 | 15098.12 | 17283.59 | 38092.68 | 22232.03 | 9102.84 | 51904.23 | 83353.41 | 35421.82 | 11234.01 | 3966.65 | 301361.13
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 16490.83 | 14914.86 | 13798.06 | 5719.26 | 3099.02 | 477.42 | 0 | 108.85 | 455.53 | 3223.5 | 11596.06 | 9458.83 | 79342.2
HP Supp. | 141.76 | 162.97 | 82.52 | 1.82 | 0 | 0 | 0 | 0 | 0 | 0 | 132.97 | 349.73 | 871.77
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 32201.47 | 27125.35 | 30816.64 | 23415.09 | 29986.11 | 19024.71 | 15060.07 | 26216.77 | 32769.63 | 31634.69 | 27469.35 | 15579.44 | 311299.31
Pumps & Aux. | 66.29 | 59.88 | 66.29 | 64.16 | 66.29 | 64.16 | 66.29 | 66.29 | 64.16 | 66.29 | 64.16 | 66.29 | 780.56
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.29 | 28106.77 | 31954.68 | 23920.64 | 30284.67 | 14385 | 1172.32 | 16504.09 | 30670.06 | 31392.53 | 28448.3 | 13187.55 | 278113.91
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.57 | 42381.22 | 48329.86 | 36895.61 | 45481.2 | 22845.21 | 3281.53 | 25745.31 | 46346.86 | 47225.82 | 42857.28 | 21079.79 | 425036.22
Total | 127783.78 | 118193.27 | 140146.17 | 107300.16 | 147009.98 | 79028.52 | 28683.05 | 120545.55 | 193659.66 | 148964.67 | 121802.12 | 63688.28 | 1396804.88
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 103030 | 104884 | 120511 | 90752 | 106802 | 49648 | 1199 | 52744 | 99658 | 103087 | 95848 | 46483 | 974646
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 105139 | 106993 | 122908 | 92525 | 109079 | 50678 | 1199 | 53942 | 101959 | 105460 | 97957 | 47417 | 995256
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 244.0107 | 419.0116 | 666.7233 | 541.7092 | 68.6293 | 706.7344 | 748.9783 | 493.2787 | 0 | 264.8495 | 4153.9253
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 396.7521 | 352.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.942 | 0 | 1162.9868
HP Supp. | 41.4641 | 39.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6774 | 0 | 133.8176
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 58.1602 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 93.2139 | 1083.5128
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10.1044 | 10.1044 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 138.4546 | 153.6401 | 138.4546 | 10.1044 | 138.4546 | 1154.7115
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 71.5292 | 71.5292 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 183.5705 | 181.0367 | 183.5705 | 71.5292 | 183.5705 | 1685.0288
Total | 613.153 | 566.9054 | 659.3389 | 834.3397 | 1082.0515 | 957.0373 | 132.865 | 1122.0625 | 1176.958 | 908.6069 | 641.556 | 680.1776 | 9375.0488
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 605498 | 617274 | 618301 | 612668 | 589775 | 567072 | 1677 | 534946 | 533934 | 544109 | 563293 | 585282 | 6373828
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 34237 | 34237 | 34237 | 34237 | 34237 | 34237 | 0 | 34237 | 34237 | 34237 | 34237 | 34237 | 376607
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 639735 | 651511 | 652538 | 646905 | 624012 | 601309 | 1677 | 569182 | 568171 | 578345 | 597530 | 619519 | 6750435
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\ESe-w09-v03-HP-Post - Baseline Design
07/18/2018 @ 09:23:44

## EPr-Base-HP-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 3522.293 | 2610.16 | 6366.976 | 7258.854 | 14808.17 | 8337.807 | 2523.494 | 17423.824 | 28550.127 | 13290.866 | 4263.258 | 1729.996 | 110685.828
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 5201.172 | 4715.595 | 4473.028 | 1923.974 | 1204.911 | 282.939 | 0 | 85.281 | 290.828 | 1388.079 | 3943.918 | 3063.766 | 26573.492
HP Supp. | 24.839 | 35.459 | 14.55 | 0.186 | 0 | 0 | 0 | 0 | 0 | 0 | 28.826 | 69.353 | 173.213
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9643.234 | 8554.111 | 9705.104 | 7237.322 | 9273.107 | 4820.616 | 2354.221 | 6578.147 | 9419.632 | 9680.137 | 8571.482 | 4465.276 | 90302.398
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10535.77 | 10599.484 | 12069.701 | 8940.695 | 11397.054 | 5201.163 | 0 | 6006.177 | 11578.907 | 11821.943 | 10726.938 | 4715.188 | 103593.023
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357.074 | 13282.676 | 15139.948 | 11597.012 | 14261.103 | 7256.479 | 1219.899 | 8159.951 | 14520.823 | 14797.079 | 13448.707 | 6717.994 | 133758.75
Total | 42284.383 | 39797.488 | 47769.309 | 36958.047 | 50944.344 | 25899.004 | 6097.614 | 38253.383 | 64360.32 | 50978.105 | 40983.133 | 20761.574 | 465086.594
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22624 | 22983 | 26387 | 19930 | 23400 | 10984 | 470 | 11659 | 21842 | 22609 | 21049 | 10390 | 214329
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 23747 | 24106 | 27674 | 20903 | 24598 | 11553 | 470 | 12303 | 23075 | 23863 | 22172 | 10904 | 225368
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 69.13 | 46.23 | 86.35 | 145.9 | 221.36 | 189.56 | 27.32 | 228.41 | 249.97 | 165.12 | 63.45 | 96.01 | 1588.81
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 21.25 | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 372.36
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 55.69 | 55.69 | 55.69 | 53.38 | 0 | 55.69 | 57.41 | 55.69 | 55.69 | 55.69 | 611.98
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 60.36 | 59.47 | 60.36 | 60.36 | 60.36 | 664.7
Total | 217.1 | 194.2 | 234.32 | 293.86 | 369.33 | 335.21 | 50.21 | 376.37 | 398.77 | 313.08 | 211.42 | 243.98 | 3237.85
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 131581 | 134123 | 134333 | 133094 | 128141 | 123213 | 700 | 116246 | 116047 | 118269 | 122450 | 127200 | 1385396
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 11414 | 11414 | 11414 | 11414 | 11414 | 11414 | 0 | 11414 | 11414 | 11414 | 11414 | 11414 | 125552
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 142995 | 145537 | 145747 | 144508 | 139555 | 134627 | 700 | 127660 | 127460 | 129683 | 133863 | 138613 | 1510948
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\EPr-w09-v03-Base-HP - Baseline Design
07/18/2018 @ 09:29:51

## EPr-Post-HP-09
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 3187.798 | 2385.119 | 5486.687 | 6318.837 | 13003.014 | 7501.116 | 2524.524 | 15856.178 | 25891.176 | 11775.197 | 4073.644 | 1579.561 | 99582.852
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 4494.422 | 4125.969 | 3876.857 | 1721.323 | 1062.661 | 260.854 | 0 | 71.897 | 244.084 | 1196.606 | 3237.151 | 2562.18 | 22854.002
HP Supp. | 24.972 | 35.477 | 15.661 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0 | 29.853 | 71.112 | 177.288
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9649.024 | 8554.111 | 9720.901 | 7260.484 | 9325.705 | 4873.354 | 2355.413 | 6642.373 | 9606.496 | 9706.101 | 8588.084 | 4475.35 | 90757.398
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10535.77 | 10599.484 | 12069.701 | 8940.695 | 11397.054 | 5201.163 | 0 | 6006.177 | 11578.907 | 11821.943 | 10726.938 | 4715.188 | 103593.023
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357.074 | 13282.676 | 15139.948 | 11597.012 | 14261.103 | 7256.479 | 1219.899 | 8159.951 | 14520.823 | 14797.079 | 13448.707 | 6717.994 | 133758.75
Total | 41249.063 | 38982.836 | 46309.754 | 35838.563 | 49049.531 | 25092.969 | 6099.836 | 36736.578 | 61841.488 | 49296.93 | 40104.375 | 20121.383 | 450723.344
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22622 | 22981 | 26382 | 19924 | 23388 | 10976 | 470 | 11652 | 21825 | 22599 | 21046 | 10390 | 214256
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 23745 | 24104 | 27669 | 20896 | 24587 | 11545 | 470 | 12295 | 23058 | 23852 | 22169 | 10904 | 225295
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 70.25 | 46.25 | 88.38 | 148.11 | 225.43 | 192.51 | 27.32 | 228.41 | 251.13 | 169.03 | 64.27 | 95.99 | 1607.09
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 21.25 | 31.92 | 31.92 | 31.92 | 31.92 | 31.92 | 372.36
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 55.69 | 55.69 | 53.38 | 53.38 | 0 | 55.69 | 57.41 | 55.69 | 55.69 | 55.69 | 609.67
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 60.36 | 59.47 | 60.36 | 60.36 | 60.36 | 664.7
Total | 218.21 | 194.22 | 236.35 | 296.07 | 371.09 | 338.17 | 50.21 | 376.37 | 399.93 | 317 | 212.24 | 243.96 | 3253.82
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 131581 | 134123 | 134335 | 133094 | 128138 | 123208 | 700 | 116240 | 116038 | 118268 | 122450 | 127201 | 1385374
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 11414 | 11414 | 11414 | 11414 | 11414 | 11414 | 0 | 11414 | 11414 | 11414 | 11414 | 11414 | 125552
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 142995 | 145537 | 145748 | 144507 | 139552 | 134622 | 700 | 127654 | 127452 | 129682 | 133864 | 138614 | 1510926
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test\EPr-w09-v03-Post-HP - Baseline Design
07/18/2018 @ 09:32:18

## EPr-Base-AC-08
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 4523 | 4101 | 7442 | 7953 | 13644 | 7757 | 2087 | 14570 | 24632 | 15265 | 5714 | 1962 | 109649
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9262 | 8388 | 9515 | 7045 | 9099 | 4636 | 1892 | 6117 | 9232 | 9496 | 8416 | 4217 | 87315
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10536 | 10599 | 12070 | 8941 | 11397 | 5201 | 0 | 6006 | 11579 | 11822 | 10727 | 4715 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357 | 13283 | 15140 | 11597 | 14261 | 7256 | 1220 | 8160 | 14521 | 14797 | 13449 | 6718 | 133759
Total | 37677 | 36371 | 44166 | 35536 | 48401 | 24851 | 5199 | 34853 | 59965 | 51380 | 38305 | 17612 | 434315
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 61584 | 48758 | 53996 | 24527 | 14758 | 3435 | 0 | 1404 | 4587 | 18097 | 47000 | 42098 | 320244
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22476 | 22760 | 26125 | 19760 | 23339 | 11025 | 474 | 11820 | 22152 | 22853 | 21154 | 10385 | 214324
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 85183 | 72641 | 81409 | 45259 | 39295 | 15028 | 474 | 13867 | 27972 | 42204 | 69277 | 52997 | 545607
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 95.17 | 58.03 | 99.97 | 157.11 | 158.54 | 143.97 | 25.71 | 168.73 | 235.19 | 189.38 | 97.02 | 109.96 | 1538.78
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 20.76 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 365.04
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 53.38 | 55.69 | 53.38 | 55.69 | 0 | 57.41 | 53.38 | 55.69 | 55.69 | 55.69 | 607.36
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 59.47 | 60.36 | 60.36 | 60.36 | 60.36 | 664.7
Total | 242.52 | 205.38 | 245.01 | 304.45 | 303.57 | 291.32 | 48.11 | 316.91 | 380.22 | 336.72 | 244.37 | 257.31 | 3175.89
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 1226611 | 1153236 | 1099931 | 1120116 | 514257 | 198293 | 0 | 106654 | 296249 | 672912 | 1538392 | 1601463 | 9528113
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 80267 | 80028 | 80119 | 79555 | 38896 | 74510 | 714 | 70998 | 70926 | 36419 | 74237 | 76598 | 763267
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1306878 | 1233264 | 1180050 | 1199670 | 553153 | 272804 | 714 | 177652 | 367174 | 709331 | 1612629 | 1678061 | 10291380
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\EPr-w08-v03-airAC - Baseline Design
07/19/2018 @ 13:47:01

## EPr-Post-AC-08
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 4118 | 3798 | 6584 | 6982 | 11969 | 7009 | 2089 | 13036 | 21996 | 13614 | 5429 | 1831 | 98455
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9266 | 8388 | 9533 | 7056 | 9133 | 4676 | 1894 | 6152 | 9361 | 9523 | 8435 | 4257 | 87674
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10536 | 10599 | 12070 | 8941 | 11397 | 5201 | 0 | 6006 | 11579 | 11822 | 10727 | 4715 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357 | 13283 | 15140 | 11597 | 14261 | 7256 | 1220 | 8160 | 14521 | 14797 | 13449 | 6718 | 133759
Total | 37277 | 36068 | 43326 | 34575 | 46761 | 24142 | 5203 | 33354 | 57456 | 49756 | 38040 | 17521 | 423481
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 52725 | 41865 | 46401 | 21666 | 13384 | 3204 | 0 | 1277 | 4143 | 14997 | 38278 | 34671 | 272612
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22474 | 22758 | 26121 | 19754 | 23328 | 11018 | 474 | 11813 | 22137 | 22844 | 21151 | 10386 | 214258
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 76321 | 65746 | 73810 | 42392 | 37911 | 14791 | 474 | 13733 | 27512 | 39095 | 60553 | 45571 | 497910
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 95.81 | 58.03 | 101.56 | 159.02 | 160.79 | 146.5 | 25.71 | 171.78 | 238.23 | 192.88 | 99.52 | 108.72 | 1558.53
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 20.76 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 365.04
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 53.38 | 55.69 | 53.38 | 55.69 | 0 | 57.41 | 53.38 | 55.69 | 55.69 | 55.69 | 607.36
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 59.47 | 60.36 | 60.36 | 60.36 | 60.36 | 664.7
Total | 243.16 | 205.37 | 246.59 | 306.36 | 305.82 | 293.84 | 48.11 | 319.95 | 383.27 | 340.22 | 246.86 | 256.07 | 3195.63
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 1226611 | 1150394 | 1121423 | 1118260 | 498255 | 180909 | 0 | 99202 | 295751 | 647987 | 1544098 | 1612452 | 9495342
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 80267 | 80025 | 80142 | 79554 | 38890 | 74498 | 714 | 70981 | 70912 | 36410 | 74237 | 76600 | 763229
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1306878 | 1230420 | 1201564 | 1197814 | 537144 | 255406 | 714 | 170183 | 366663 | 684397 | 1618335 | 1689052 | 10258572
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\EPr-w08-v03-airAC-Post - Baseline Design
07/19/2018 @ 13:48:20

## EPr-w08-v03-airHP-Base
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 4031.6 | 3647.8 | 6781.5 | 7374.9 | 12881.9 | 7307.4 | 1849 | 14015.1 | 23859.5 | 14414.4 | 5163.3 | 1797.4 | 103123.6
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 4280.6 | 3412 | 3808.4 | 1681.8 | 958.6 | 218.3 | 0 | 78.9 | 285 | 1185.4 | 3292.6 | 3055.5 | 22257.2
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 66.6 | 82.3
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9109 | 8253.7 | 9362.4 | 6932.1 | 8953 | 4556.8 | 1855 | 6011.6 | 9085.9 | 9343.5 | 8282.3 | 4146.1 | 85891.4
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10535.8 | 10599.5 | 12069.7 | 8940.7 | 11397.1 | 5201.2 | 0 | 6006.2 | 11578.9 | 11821.9 | 10726.9 | 4715.2 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357.1 | 13282.7 | 15139.9 | 11597 | 14261.1 | 7256.5 | 1219.9 | 8160 | 14520.8 | 14797.1 | 13448.7 | 6718 | 133758.8
Total | 41314 | 39195.6 | 47162 | 36526.4 | 48451.7 | 24540.1 | 4923.9 | 34271.7 | 59330.1 | 51562.4 | 40929.5 | 20498.8 | 448706.3
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22476 | 22760 | 26125 | 19760 | 23338 | 11025 | 474 | 11819 | 22152 | 22853 | 21154 | 10385 | 214323
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 23599 | 23883 | 27413 | 20733 | 24537 | 11593 | 474 | 12463 | 23384 | 24107 | 22278 | 10899 | 225362
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 89.39 | 52.8 | 96.45 | 155.36 | 158.69 | 143.92 | 22.79 | 170.3 | 236.3 | 188.43 | 91.24 | 105.86 | 1511.53
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 20.37 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 359.15
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 53.38 | 55.69 | 53.38 | 55.69 | 0 | 57.41 | 53.38 | 55.69 | 55.69 | 55.69 | 607.36
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 59.47 | 60.36 | 60.36 | 60.36 | 60.36 | 664.7
Total | 236.24 | 199.64 | 240.98 | 302.21 | 303.23 | 290.77 | 44.8 | 317.98 | 380.84 | 335.28 | 238.09 | 252.7 | 3142.75
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 130681 | 132807 | 132983 | 131935 | 127798 | 123693 | 714 | 117872 | 117708 | 119565 | 123069 | 127031 | 1385853
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 11414 | 11414 | 11414 | 11414 | 11414 | 11414 | 0 | 11414 | 11414 | 11414 | 11414 | 11414 | 125552
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 142095 | 144220 | 144396 | 143349 | 139211 | 135107 | 714 | 129285 | 129122 | 130979 | 134482 | 138444 | 1511405
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\EPr-w08-v03-airHP - Baseline Design
07/19/2018 @ 13:55:33

## EPr-w08-v03-airHP-Post
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 3678.2 | 3385.2 | 6019.2 | 6488.5 | 11356.4 | 6617.8 | 1849.1 | 12581.1 | 21392.2 | 12892.7 | 4921.1 | 1679.5 | 92861.2
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 3693.8 | 2960 | 3294.3 | 1494.2 | 876.4 | 205.1 | 0 | 69.7 | 254.4 | 993.6 | 2711.6 | 2513.1 | 19066.3
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 68.7 | 84.6
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 9113.1 | 8253.7 | 9380 | 6942.7 | 8986.7 | 4595.8 | 1855 | 6045.5 | 9209.4 | 9370.1 | 8299.7 | 4188.4 | 86240.1
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 10535.8 | 10599.5 | 12069.7 | 8940.7 | 11397.1 | 5201.2 | 0 | 6006.2 | 11578.9 | 11821.9 | 10726.9 | 4715.2 | 103593
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 13357.1 | 13282.7 | 15139.9 | 11597 | 14261.1 | 7256.5 | 1219.9 | 8160 | 14520.8 | 14797.1 | 13448.7 | 6718 | 133758.8
Total | 40377.9 | 38481.2 | 45903.2 | 35463.1 | 46877.7 | 23876.2 | 4924 | 32862.5 | 56955.8 | 49875.4 | 40124 | 19882.9 | 435603.9
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 22474 | 22758 | 26121 | 19754 | 23328 | 11018 | 474 | 11813 | 22136 | 22844 | 21151 | 10386 | 214257
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 1123 | 1123 | 1287 | 972 | 1198 | 568 | 0 | 644 | 1233 | 1253 | 1123 | 514 | 11039
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 23597 | 23881 | 27408 | 20727 | 24527 | 11587 | 474 | 12456 | 23369 | 24097 | 22275 | 10899 | 225297
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 90.06 | 52.8 | 98.13 | 157.49 | 161.17 | 146.63 | 22.79 | 172.86 | 239.36 | 192.01 | 93.83 | 104.56 | 1531.69
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 20.37 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 359.15
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 55.69 | 55.69 | 53.38 | 55.69 | 53.38 | 55.69 | 0 | 57.41 | 53.38 | 55.69 | 55.69 | 55.69 | 607.36
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 60.36 | 1.64 | 59.47 | 60.36 | 60.36 | 60.36 | 60.36 | 664.7
Total | 236.91 | 199.64 | 242.67 | 304.34 | 305.71 | 293.48 | 44.8 | 320.53 | 383.89 | 338.85 | 240.68 | 251.4 | 3162.9
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 130681 | 132805 | 132984 | 131934 | 127792 | 123689 | 714 | 117867 | 117703 | 119563 | 123069 | 127031 | 1385831
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 11414 | 11414 | 11414 | 11414 | 11414 | 11414 | 0 | 11414 | 11414 | 11414 | 11414 | 11414 | 125552
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 142095 | 144218 | 144397 | 143348 | 139205 | 135103 | 714 | 129281 | 129117 | 130977 | 134482 | 138445 | 1511383
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\EPr-w08-v03-airHP-Post - Baseline Design
07/19/2018 @ 13:56:54

## ESe-w08-v03-airAC-Base
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 11486.9 | 9841 | 19593.9 | 21090.3 | 38180.7 | 21514.7 | 3684.8 | 43254.6 | 75991 | 44871 | 15776.7 | 5129.7 | 310415.4
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 25580.1 | 23743.2 | 26925.3 | 19868.3 | 25716 | 12290.5 | 2940.7 | 15941.3 | 26023.5 | 26856.1 | 23785.5 | 11268.1 | 240938.4
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 107787.2 | 104132 | 126870 | 101839.1 | 139729 | 71099.6 | 11145.7 | 101511.5 | 179095.5 | 150411.7 | 110931.9 | 50731.5 | 1255284.6
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 204304 | 158801 | 177413 | 72245 | 40462 | 6949 | 0 | 2150 | 7659 | 45523 | 152557 | 146185 | 1014248
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 102326 | 103850 | 119284 | 89951 | 106503 | 49773 | 1101 | 53412 | 101056 | 104200 | 96324 | 46425 | 974206
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 308739 | 264760 | 299094 | 163970 | 149242 | 57753 | 1101 | 56760 | 111015 | 152096 | 250990 | 193545 | 2009065
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 243.1631 | 143.3718 | 244.489 | 424.9674 | 412.5931 | 395.2305 | 49.7331 | 466.7469 | 626.011 | 532.2352 | 263.7426 | 279.2563 | 4081.54
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 37.6714 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 935.1779
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1554.9475
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 2018.6189
Total | 646.8688 | 559.7292 | 648.1948 | 828.6732 | 816.2988 | 798.9362 | 93.48 | 883.1042 | 1029.7168 | 935.941 | 667.4483 | 682.962 | 8591.3506
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 4657542 | 3058660 | 3274270 | 3336021 | 1698690 | 608611 | 0 | 0 | 882012 | 2005226 | 4752351 | 4819485 | 29092868
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 2092 | 367385 | 367988 | 365147 | 1844 | 1767 | 1671 | 542478 | 1734 | 1857 | 1994 | 1976 | 1657933
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34237 | 0 | 0 | 0 | 0 | 34237
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 4659634 | 3426046 | 3642258 | 3701168 | 1700534 | 610378 | 1671 | 576715 | 883745 | 2007083 | 4754345 | 4821462 | 30785036
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\ESe-w08-v03-airAC-Base - Baseline Design
07/19/2018 @ 15:04:12

## ESe-w08-v03-airAC-Post
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 10208.5 | 8955.6 | 16890.1 | 18110.3 | 32983.5 | 19083.9 | 3684.4 | 38512.2 | 67601.3 | 39467.3 | 14743.5 | 4704.3 | 274944.9
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 25588.2 | 23743.2 | 26926.3 | 19899.6 | 25762.3 | 12365.8 | 2940.7 | 16028.2 | 26386 | 26945.8 | 23817 | 11351.2 | 241754.1
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 106516.8 | 103246.6 | 124167.2 | 98890.4 | 134578 | 68744 | 11145.2 | 96856.1 | 171068.3 | 145097.8 | 109930.2 | 50389.1 | 1220629.5
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 187959 | 147065 | 159756 | 67081 | 37144 | 6158 | 0 | 1887 | 6411 | 40951 | 137221 | 127414 | 919048
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 102318 | 103842 | 119273 | 89941 | 106486 | 49764 | 1101 | 53399 | 101030 | 104183 | 96315 | 46425 | 974077
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 292386 | 253016 | 281426 | 158795 | 145907 | 56953 | 1101 | 56484 | 109742 | 147507 | 235645 | 174774 | 1913736
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 245.7693 | 145.2522 | 250.3538 | 431.7798 | 422.657 | 403.8745 | 49.6846 | 477.1653 | 636.2309 | 544.4723 | 272.9107 | 275.9768 | 4156.127
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 37.6714 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 81.5915 | 935.1779
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1554.9475
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 2018.6189
Total | 649.475 | 561.6096 | 654.0595 | 835.4855 | 826.3627 | 807.5802 | 93.4315 | 893.5227 | 1039.9366 | 948.178 | 676.6165 | 679.6826 | 8665.9385
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 4657542 | 3042856 | 3357529 | 3332112 | 1652410 | 36342 | 0 | 0 | 846338 | 1953039 | 4769039 | 4854228 | 28501434
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 2092 | 367378 | 367991 | 365146 | 1836 | 569306 | 1671 | 542469 | 1710 | 1848 | 1989 | 1975 | 2225413
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34237 | 0 | 0 | 0 | 0 | 34237
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 4659634 | 3410234 | 3725520 | 3697258 | 1654246 | 605648 | 1671 | 576706 | 848048 | 1954888 | 4771028 | 4856203 | 30761084
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\ESe-w08-v03-airAC-Post - Baseline Design
07/19/2018 @ 15:05:51

## ESe-w08-v03-airHP-Base
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 9921.2 | 8614.2 | 17623.5 | 19462.1 | 35970.6 | 20741.1 | 4844.8 | 42777.6 | 73627.9 | 42342.2 | 14005.8 | 4525.7 | 294456.8
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 13951.9 | 11000.2 | 12443.2 | 4943.4 | 2577.8 | 405.2 | 0 | 109.7 | 424.1 | 2878.7 | 10634.2 | 10644.1 | 70012.7
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7 | 302.5 | 393.2
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 26159.2 | 23351.6 | 26481.2 | 19602.8 | 25363.8 | 14462.9 | 9314.9 | 19070.1 | 26010.7 | 26738.5 | 23570.4 | 11855.6 | 251981.7
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 120752.5 | 113513.9 | 136898.7 | 104888.7 | 139744.3 | 72903.6 | 18679.9 | 104273.1 | 177143.8 | 150644.1 | 119670.9 | 61661.6 | 1320774.4
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 102329 | 103849 | 119301 | 89971 | 106537 | 49852 | 1226 | 53498 | 101113 | 104226 | 96324 | 46425 | 974650
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 104438 | 105958 | 121698 | 91744 | 108814 | 50883 | 1226 | 54696 | 103414 | 106599 | 98433 | 47359 | 995261
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 225.6538 | 129.431 | 233.2013 | 415.6869 | 412.9409 | 394.5251 | 52.0518 | 471.3976 | 627.2341 | 527.0312 | 246.8256 | 265.8735 | 4001.853
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 49.0859 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 931.791
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1554.9475
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 2018.6189
Total | 628.014 | 544.4427 | 635.5615 | 818.0471 | 815.301 | 796.8853 | 107.2133 | 886.4094 | 1029.5944 | 929.3914 | 649.1857 | 668.2337 | 8508.2783
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 601355 | 611169 | 612008 | 607328 | 588214 | 569278 | 1698 | 542469 | 541607 | 550098 | 566113 | 584486 | 6375825
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 34237 | 34237 | 34237 | 34237 | 34237 | 34237 | 0 | 34237 | 34237 | 34237 | 34237 | 34237 | 376607
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 635592 | 645406 | 646245 | 641565 | 622451 | 603515 | 1698 | 576706 | 575844 | 584335 | 600350 | 618723 | 6752432
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\ESe-w08-v03-airHP-Base - Baseline Design
07/19/2018 @ 15:11:51

## ESe-w08-v03-airHP-Post
Electric Consumption (kWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 8904.3 | 7923.7 | 15309.3 | 16808.6 | 31308.3 | 18550.9 | 4846.6 | 38403.9 | 65923.2 | 37440.7 | 13204.9 | 4150.3 | 262774.8
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 12976.3 | 10316.8 | 11272.4 | 4622.8 | 2370.9 | 350.3 | 0 | 100.2 | 361.6 | 2616.1 | 9680.5 | 9321.2 | 63989.2
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 312.1 | 403.4
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 26179.1 | 23358.2 | 26481.2 | 19711.3 | 25556.1 | 14704 | 9325.4 | 19355.9 | 26907.5 | 27120.7 | 23645.1 | 11939.4 | 254283.9
Pumps & Aux. | 66.3 | 59.9 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 66.3 | 64.2 | 66.3 | 64.2 | 66.3 | 780.6
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 28087.3 | 28106.8 | 31954.7 | 23920.6 | 30284.7 | 14385 | 1172.3 | 16504.1 | 30670.1 | 31392.5 | 28448.3 | 13187.5 | 278113.9
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 42566.6 | 42381.2 | 48329.9 | 36895.6 | 45481.2 | 22845.2 | 3281.5 | 25745.3 | 46346.9 | 47225.8 | 42857.3 | 21079.8 | 425036.2
Total | 118779.9 | 112146.6 | 133413.7 | 102023.1 | 135067.5 | 70899.5 | 18692.2 | 100175.7 | 170273.4 | 145862.3 | 117991.5 | 60056.7 | 1285382
Gas Consumption (kBtu) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 102326 | 103846 | 119298 | 89965 | 106526 | 49843 | 1225 | 53489 | 101089 | 104211 | 96317 | 46425 | 974561
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 2109 | 2109 | 2397 | 1773 | 2277 | 1031 | 0 | 1198 | 2301 | 2373 | 2109 | 935 | 20611
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 104435 | 105955 | 121694 | 91738 | 108802 | 50874 | 1225 | 54687 | 103390 | 106584 | 98426 | 47360 | 995171
Electric Demand (kW) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 228.2826 | 131.171 | 239.1921 | 423.2514 | 424.4595 | 404.3948 | 52.0516 | 481.4255 | 637.5687 | 539.9617 | 257.3565 | 0 | 3819.1152
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.5129 | 416.5129
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9716 | 86.9716
Hot Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vent. Fans | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 49.0859 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 80.2459 | 931.791
Pumps & Aux. | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 0.0891 | 1.0693
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 138.4546 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 138.4546 | 1.5757 | 153.6401 | 138.4546 | 138.4546 | 138.4546 | 10.1044 | 1426.5973
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 183.5705 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 183.5705 | 4.4107 | 181.0367 | 183.5705 | 183.5705 | 183.5705 | 71.5292 | 1906.5776
Total | 630.6428 | 546.1827 | 641.5523 | 825.6116 | 826.8196 | 806.755 | 107.2131 | 896.4373 | 1039.9288 | 942.3219 | 659.7167 | 665.4531 | 8588.6348
Gas Demand (Btu/h) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cool | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Reject. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Space Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HP Supp. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot Water | 601355 | 611168 | 612014 | 607327 | 588206 | 569267 | 1697 | 542449 | 541591 | 550094 | 566113 | 584497 | 6375777
Vent. Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps & Aux. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ext. Usage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Misc. Equip. | 34237 | 34237 | 34237 | 34237 | 34237 | 34237 | 0 | 34237 | 34237 | 34237 | 34237 | 34237 | 376607
Task Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Area Lights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 635592 | 645405 | 646251 | 641564 | 622443 | 603504 | 1697 | 576686 | 575828 | 584331 | 600350 | 618733 | 6752384
eQUEST 3.65.7173
C:\Users\Akhilesh Reddy\Desktop\WP Supporting Docs\Class Room HVAC Occ Sensor\eQuest models\Test-CZ08\ESe-w08-v03-airHP-Post - Baseline Design
07/19/2018 @ 15:13:41