Work Paper SCE17LG087

Revision 0

Southern California Edison

Fluorescent-to-Fluorescent Lamp and Ballast Retrofit

# At-a-Glance Summary

| Measure Codes | See the Measures and Codes table. |
| --- | --- |
| Measure Description | T5 or T8 Linear Fluorescent Lamp and Ballast |
| Base Case Description | T12, T8, or T5 Linear Fluorescent Lamp and Ballast |
| Units | Fixture |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | ILtg-Lfluor-Elec, ILtg-T5, ILtg-Lfluor-CommArea: EUL = Rated Life of Ballast (70,000 hours)/HOU, or 15 years (whichever is less). ILtg-Lfluor-T12Mag: EUL = Rated Life of Ballast (20,000 hours)/HOU, or 15 years (whichever is less). |
| Measure Installation Type | Early Retirement (RET), Replace on Burnout (ROB) (RET Pursuant to POE Draft Resolution E-4818) |
| Net-to-Gross Ratio | NonRes-sAll-mLFOth-Deemed: 0.6 |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 11/18/16 | Chad Sisco (SCE) | - Updated to latest WP Template v0 SCE 09-11-15 from WPSCE13LG087.2 - Updated to latest WP Calculation Template - Updated the EUL and RUL value in accordance with Draft Resolution E-4807 [510] - Updated costs - Removed Solution Codes LT-10436, LT-18934, LT-25867, LT-32845, LT-45291, LT-57432, LT-69821, LT-78193, LT-83912, LT-83945, LT-90462, LT-98587, LT-30612, LT-84012, and LT-19844 due to negative IMC issue. - Removed LT-10494 since this is To-Code Measure. |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details fluorescent to fluorescent lamp and ballast retrofits, with new premium instant, instant, or programmed start ballast and reduced watt or next generation linear fluorescent lamp. The measures are shown in the table below.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Interior T5 or T8 Linear Fluorescent Lamp and Ballast (high efficiency) |
| Existing Condition | Interior T5, T8, or T12 Linear Fluorescent Lamp and Ballast |
| Code/Standard | Interior T5 or T8 Linear Fluorescent Lamp and Ballast (standard efficiency) |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Code | Measure Name |
| --- | --- |
| Non-Residential Measures |  |
| LT-18943 | (1) 24in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 24in T12 Linear Fluorescent |
| LT-43895 | (1) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent |
| LT-69594 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent |
| LT-89708 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent |
| LT-85932 | (1) 48in Reduced 28 Watt T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent |
| LT-48392 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent |
| LT-20983 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent |
| LT-59482 | (2) 24in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 24in T12 Linear Fluorescent |
| LT-91429 | (2) 24in F17 (1) Premium Instant Start Ballast - High Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent |
| LT-49843 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-39875 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-68384 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-40696 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-18409 | (2) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent |
| LT-49810 | (2) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent |
| LT-87326 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent |
| LT-32645 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent |
| LT-60432 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent |
| LT-71214 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-89122 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-24985 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-30765 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-27685 | (2) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent |
| LT-39678 | (2) U-Tube (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent |
| LT-50379 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-60092 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-79821 | (3) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent |
| LT-10154 | (3) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T8 Linear Fluorescent |
| LT-89871 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent |
| LT-99866 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-85958 | (4) 48in (1) Premium Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (6) 48in T12 Linear Fluorescent |
| LT-59103 | (4) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent |
| LT-78327 | (4) 48in (2) Instant Start Ballast - Reduced Light Output (New Fixture) T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-20483 | (4) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent |
| LT-59655 | (4) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T8 Linear Fluorescent |
| LT-54329 | (8) 48in (2) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 96in T12 Linear Fluorescent |

Requirements from the 2016 Solutions Directory

General Lighting Eligibility [A]

- All new lighting fixtures retrofit kits, and components must carry the appropriate, designated Underwriters Laboratory (UL) or Edison Testing Laboratory (ETL) label.

- Customer should make sure that new lighting equipment is compatible with existing equipment and controls.

- When applicable, lighting fixtures must meet existing case and proposed case requirement tables.

- New fixture or lamp wattage must be less than the wattage of lamp being replaced.

T8 or T5 Linear Fluorescent Lamps and Electronic Ballasts – General Requirement

- Four-foot T8 lamps and ballasts must be listed as High-Performance (HP) T8 lamps and HP ballasts, and be listed at http://library.cee1.org/content/commercial-lighting-qualifying-products-lists.

- Lamps and ballasts must be replaced, one for one, with T8 or T5 lamps with electronic, high-frequency (greater than or equal to 20 kHz) ballasts.

- Proposed ballasts must have a power factor of greater than or equal to 0.90.

- At full light output, ballasts must have a total harmonic distortion of less than or equal to 20%.

- Programmed start/programmed rapid-start ballasts must be used for T5 lamp installations.

- Customers installing T5 lamps for direct lighting in low ceilings should consult a lighting professional to address the possibility of excessive glare.

- Replacement lamps and ballasts must meet the color rendering index (CRI) and rated lamp life standards listed in the 2016 Solutions Directory Lamp and Ballast requirement table.

- Manufacturer’s specification sheets for lamps and ballasts must be provided for each measure.

## 1.2 Technical Description

A linear fluorescent lamp is a mercury-vapor gas-discharge lamp that utilizes electric current to excite the low pressure gas contained to produce fluorescent light.  Luminous efficacy, or how much light is produced by a lamp in comparison to the energy it consumes, is generally higher in fluorescent lamps than in most incandescent lighting, thus making it the preferred type in offices and warehouses where consistent, prolonged operation is required.  However, while it is more energy efficient, fluorescent lamps require a ballast to regulate the current through the lamp, consequently increasing the initial cost.  An instant-start ballast lamp is used in one of the measures addressed within this work paper.  This ballast starts lamps without heating by using an adequately high voltage to break down the gas and mercury column.  Instant-start ballasts are the most efficient of the linear fluorescent ballast types, but also allow for fewer starts.  Consequently, instant-start ballasts are ideal in places where light usage is more constant rather than frequently being turned off and on.

The types of linear tubular lamps being replaced in this work paper are 1 inch diameter T8 lamps which generally produce lighting in the range of 80 lumens/watt and 5/8 inch diameter T5 lamps that produce lighting in the range of 100 lumens/watt.  The measure objective is to replace current T12, T8, and T5 linear fluorescent lamps with reduced wattage T8 and T5 lamps, respectively, of the same length.  Installation of a new lamp with adequate lumen output and lower power load for the duration of its expected useful life (EUL) will result in energy savings from the baseline.

Note: Linear fluorescent lamps and ballasts replacements in this workpaper are expressed in “fixture” common units, although the actual fixtures are not being replaced.

## 1.3 Installation Types and Delivery Mechanisms

LT-59482, LT-59655, LT-69594, LT-87326, and LT-89708 are available via ROB installation type only and are available for Mid-Stream and Direct Install delivery methods.

The remainder of the measures are offered as Retrofit (RET) and (ROB), through Financial Support: Direct Install.

- For direct install measures, SCE is currently claiming full customer savings for the RUL as the measures are being implemented as early retirement measures.

- The Non Residential Direct Install program quality control ensures correct documentation of existing measure, base case, and specification of the energy efficient product installed.  SCE requires a detailed Product Location Form (PLF) for each project submitted for rebate or incentive.  The PLF is a form which information for measures installed in all building types related to the Non Residential Direct Install program.  The PLF contains the following fields: Service Account Address, Measures Proposed/Installed, Product Make/Model, Install Locations (detailed to define separate spaces/floors, as well as specific locations within the space including but not limited to:  Bathrooms, Hallways, Meeting Rooms, Offices, Warehouse, etc.).

Customers are solicited to participate primarily through field visits.  Contractors conduct energy consultation and provide recommendation that can help eligible customers use less energy.  If the customer agrees, the Direct Install contractor will help them complete an authorization form and schedule an installation appointment.

SCE can also provide photos to show measure functionality and a sample close up photos to substantiate the measure base case where applicable.  These photos would be part of the required project package.  The project package is identified with the Service Account Number and attached to SCE’s SMART database (SCE Project Tracking System) at each specific project level. The above described information is entered and tracked in the program’s tracking database.  This level of data is provided in the Participation Data that is provided to the CPUC on a quarterly basis.

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Replace on Burnout (ROB) | Above Code or Standard | N/A | EUL | N/A |
| New Construction (NEW/NC) | Above Code or Standard | N/A | EUL | N/A |
| Retrofit or Early Replacement (RET/ER) | Above Customer Existing | Above Code or Standard | RUL | EUL-RUL |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Mid-Stream Programs | See Mid-Stream Incentive in the Incentive Method Descriptions table. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Direct Install | The program implements energy efficiency measures for qualifying customers, at no cost to the customer. |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |
| Mid-Stream Incentive Mid-Stream Buy Down | The program gives a financial incentive to a midstream market actor (distributor, vendor, or retailer) to encourage the promotion of efficient measures. Buy Down means that the incentive is required to be passed down to the end-use customer. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | Yes |
| DEER Measure Case | Yes |
| DEER Building Types | Yes |
| DEER Operating Hours | Yes |
| DEER eQUEST Prototypes | No |
| DEER Version | DEER 2017, READI v2.4.7 |
| Reason for Deviation from DEER | No deviation. These are all DEER measures. |
| DEER Measure IDs Used | E.g. C-In-LFLmpBlst-T8-24in-17w+El-IS-RLO-1(14w)-dWP14 |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mLFOth-Deemed | Nonresidential Linear Fluorescent: measures not listed elsewhere; all delivery mechanisms | NonRes | Any | Deemed | 0.6 |

Commercial Direct Install Program (including Partnership Direct Install Programs)

This work paper includes measures that are offered via direct install activities into hard-to-reach (HTR) customer facilities.  “Final Resolution E-4700”, dated December 18, 2014, defines specific criteria to classify customer facilities as HTR and also states that two criteria are sufficient to identify HTR customers if one of the criteria met is the geographic criteria.

SCE’s Commercial Direct Install program delivers free and low cost energy efficiency hardware retrofits through installation contractors to reduce peak demand and energy savings for small and medium commercial customers.  The barriers for customer participation include limited capital resources, lack of expertise and understanding of the understanding of the benefits of energy efficiency, a suspicion of the “free offer” and its legitimacy, and language and cultural barriers.  The program also addresses the ongoing concern with “split incentives”, where the customer is not the owner of the property, and therefore, lack incentive to improve their energy usage.  SCE’s Commercial Direct Install program will track the following three (3) customer data points to identify direct install activities in HTR customer facilities.  If geography and business size criteria are satisfied, SCE will identify the customer as HTR.  If geography and language criteria are satisfied, SCE will identify the customer as HTR.  Other measures in the Commercial Direct Install program will receive default NTG (NTGR_ID: Com-Default>2), unless otherwise specified in DEER.

- Business Size: Customer must have less than ten employees

- Language: Customer’s primary language spoken is not English

- Geography: Businesses in areas other than the United States Office of Management and Budget (OMB) Combined Statistical Areas (CSA) of the San Francisco Bay Area, the Greater Los Angeles Area and the Greater Sacramento Area or the OBM metropolitan statistical areas or San Diego County

The “Required Corrections to Measure Level Input Parameters Identified by Commission Staff per D.14-10-046 Order Paragraph 16”, dated November 3, 2014, includes additional clarification for the geographic criteria:

“Notes on OMB CSA designations:

The OMB has designated a 12-county CSA titled the San Jose-San Francisco-Oakland, CA Combined Statistical Area which includes the nine counties of Alameda, Contra Costa, Marin, Napa, San Francisco, San Mateo, Santa Clara, Solano, and Sonoma which border the San Francisco Bay plus the three counties of San Joaquin, Santa Cruz, and San Benito that are economically tied to the nine counties that that border the San Francisco Bay.

The OMB definition of this CSA includes Los Angeles, Orange, San Bernardino, Riverside and Ventura counties.

The OMB definition of this CSA includes Sacramento, Yolo, El Dorado, Placer, Sutter, Yuba, and Nevada counties.”

The California Public Utilities Commission is currently evaluating the documentation required to satisfy the Preponderance of Evidence (POE) requirement for measures with RET (to be renamed AR going forward) install type. Draft Resolution E-4818 is currently out for public review and includes specific language for deemed measures in Section 1.5.4. Upon adoption of the Resolution, SCE will modify the data collection activities described above, as needed, to be consistent with the final Resolution requirements.

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below. All non-residential measures use Com-LF-SCE. MFm measures use MFm-LF-SCE, and DMo measures use Def-GSIA.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Com-LF-SCE | Non-Res Linear Fluorescent fixture; Annual Installation Rate | Com | Any | NonUpStrm | 0.95 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below. Some specific EUL and RUL values were obtained in accordance with Draft Resolution E-4807 [510].

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| ILtg-Lfluor-Elec | Linear Fluorescent with Electronic Ballast | Com | Lighting | Rated Life of Ballast (70,000 hours) / Annual usage for building type (usage provided by DEER) OR 15 years (whichever is less). | RUL = EUL/3 |
| ILtg-T5 | HID Lighting (T-5) | Com | Lighting |  |  |
| ILtg-Lfluor-T12Mag | Linear Fluorescent with T12 Lamp + Magnetic Ballast | Com | Lighting | Rated Life of Ballast (20,000 hours) / Annual usage for building type (usage provided by DEER) OR 15 years (whichever is less). | RUL = EUL/3 |

### 1.4.2 Codes and Standards Analysis

In Title 24 2016 Building Energy Efficiency Standards [496], Section 141.0(b) 2J states:

Luminaire Component Modifications. Luminaire component modifications in place that include

replacing the ballasts or drivers and the associated lamps in the luminaire, permanently changing the

light source of the luminaire, or changing the optical system of the luminaire, where 70 or more

existing luminaires are modified either on any single floor of a building or, where multiple tenants

inhabit the same floor, in any single tenant space, in any single year, shall not prevent or disable the

operation of any multi-level, shut-off, or daylighting controls, and shall:

- Meet the lighting power allowance in Section 140.6 and comply with Table 141.0-E; or

- In office, retail, and hotel occupancies have at least 50 percent, and in all other occupancies have at least 35 percent, lower rated power at full light output as compared to the original luminaires prior to being modified, and meet the requirements of Sections 130.1(a)1, 2, and 3, 130.1(c)1A through C, 130.1(c)2, 130.1(c)3, 130.1(c)4, 130.1(c)5, 130.1(c)6A, and for parking garages 130.1(c)7B.

Lamp replacements alone and ballast replacements alone shall not be considered a modification of the

luminaire provided that the replacement lamps or ballasts are installed and powered without modifying

the luminaire.

EXCEPTION 1 to Section 141.0(b)2J. Modification of portable luminaires, luminaires affixed to

moveable partitions, or lighting excluded by Section 140.6(a)3.

EXCEPTION 2 to Section 141.0(b)2J. In an enclosed space where two or fewer luminaires are

modified.

EXCEPTION 3 to Section 141.0(b)2J. Modifications that would directly cause the disturbance of

asbestos, unless the modifications are made in conjunction with asbestos abatement.

EXCEPTION 4 to Section 141.0(b)2J. Acceptance testing requirements of Section 130.4 are not

required for modifications where lighting controls are added to control 20 or fewer luminaires.

Title 20 2015 Appliance Efficiency Regulations [493] includes regulations to fluorescent lamp ballasts, replacement fluorescent lamp ballasts, and lamps.

2012 Federal Standards for General Service Fluorescent Lamps issued by Department of Energy effective July 14, 2012 contains Energy Conservation Standards that applies to various linear fluorescent lamp types [B].

This workpaper uses standard and code wattage values given by the CPUC which are assumed to be within the guidelines of T24, T20, and NEMA standards. T24 Modifications-in-Place is triggered due to lamp & ballast replacements and de-lamping.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2016) | 2016 Building Energy Efficiency Standards for Residential and Non-Residential Buildings, Section 141.0(b)2J | January 1, 2017 |
| Title 20 (2015) | Section 1605.1(j) | July 1, 2015 |
| NEMA (2012) | Federal standards for general service fluorescent lamps issued by DOE | July 14, 2012 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

No studies were reviewed during the development of this work paper.

## 1.6 Data Quality and Future Data Needs

No future data needs are anticipated.

# Section 2. Calculation Methodology

All measures in this work paper are from DEER. The following table shows the DEER MeasureIDs and wattages associated with each measure.

| Measure Code | Measure Name | DEER MeasureID | Measure kW | Code kW | Pre-existing kW |
| --- | --- | --- | --- | --- | --- |
| LT-18943 | (1) 24in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 24in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-24in-17w+El-IS-RLO-1(14w)-dWP14 | 0.014 | 0.028 | 0.028 |
| LT-43895 | (1) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-RLO(25w)-dWP16-dWC6 | 0.025 | 0.031 | 0.041 |
| LT-69594 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-NLO(28w)-dWP3-2 | 0.028 | 0.031 | 0.031 |
| LT-89708 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-RLO(24w)-dWP7-2 | 0.024 | 0.031 | 0.031 |
| LT-85932 | (1) 48in Reduced 28 Watt T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-30w+El-IS-NLO(27w)-dWP16-dWC4 | 0.027 | 0.031 | 0.043 |
| LT-48392 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-96in-59w+El-IS-RLO(57w)-dWP66-dWC52 | 0.057 | 0.109 | 0.123 |
| LT-20983 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-96in-59w+El-IS-RLO(49w)-dWP13-dWC6 | 0.049 | 0.055 | 0.062 |
| LT-59482 | (2) 24in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 24in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-24in-17w+El-IS-NLO(33w)-dWP23 | 0.033 | 0.056 | 0.056 |
| LT-91429 | (2) 24in F17 (1) Premium Instant Start Ballast - High Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent | C-In-LFLmpBlst-T8-24in-17w+El-IS-HLO(35w)-dWP37-dWC25 | 0.035 | 0.06 | 0.072 |
| LT-49843 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(54w)-dWP61-dWC35 | 0.054 | 0.089 | 0.115 |
| LT-39875 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-VHLO(79w)-dWP65-dWC11 | 0.079 | 0.09 | 0.144 |
| LT-68384 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(54w)-dWP61-dWC35 | 0.054 | 0.089 | 0.115 |
| LT-40696 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-NLO+Refl(59w)-dWP85-dWC53 | 0.059 | 0.112 | 0.144 |
| LT-18409 | (2) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-RS-RLO(54w)-dWP8-dWC6 | 0.054 | 0.06 | 0.062 |
| LT-49810 | (2) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-30w+El-IS-RLO(45w)-dWP27-dWC14 | 0.045 | 0.059 | 0.072 |
| LT-87326 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-NLO(53w)-dWP6-1 | 0.053 | 0.059 | 0.059 |
| LT-32645 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-RLO(44w)-dWP15-dWC15 | 0.044 | 0.059 | 0.059 |
| LT-60432 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(54w)-dWP20-dWC5 | 0.054 | 0.059 | 0.074 |
| LT-71214 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-NLO(53w)-dWP67-dWC36 | 0.053 | 0.089 | 0.12 |
| LT-89122 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-NLO(53w)-dWP115-dWC59 | 0.053 | 0.112 | 0.168 |
| LT-24985 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-NLO+Refl(53w)-dWP67-dWC36 | 0.053 | 0.089 | 0.12 |
| LT-30765 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-NLO+Refl(54w)-dWP114-dWC58 | 0.054 | 0.112 | 0.168 |
| LT-27685 | (2) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-96in-59w+El-IS-RLO(98w)-dWP25-dWC11 | 0.098 | 0.109 | 0.123 |
| LT-39678 | (2) U-Tube (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent | C-In-LFLmpBlst-U6-22in-32w+El-IS-RLO(52w)-dWP20-dWC8 | 0.052 | 0.06 | 0.072 |
| LT-50379 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(78w)-dWP42-dWC11 | 0.078 | 0.089 | 0.12 |
| LT-60092 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(83w)-dWP61-dWC6 | 0.083 | 0.089 | 0.144 |
| LT-79821 | (3) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(78w)-dWP37-dWC11 | 0.078 | 0.089 | 0.115 |
| LT-10154 | (3) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-28w+El-IS-RLO(65w)-dWP24-dWC24 | 0.065 | 0.089 | 0.089 |
| LT-89871 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w)-dWP21-dWC10 | 0.102 | 0.112 | 0.123 |
| LT-99866 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w)-dWP58-dWC10 | 0.102 | 0.112 | 0.16 |
| LT-85958 | (4) 48in (1) Premium Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (6) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(112w)-dWP104-dWC63 | 0.112 | 0.175 | 0.216 |
| LT-59103 | (4) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-RLO(94w)-dWP113-dWC73 | 0.094 | 0.167 | 0.207 |
| LT-78327 | (4) 48in (2) Instant Start Ballast - Reduced Light Output (New Fixture) T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w)-dWP42-dWC10 | 0.102 | 0.112 | 0.144 |
| LT-20483 | (4) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w)-dWP42-dWC10 | 0.102 | 0.112 | 0.144 |
| LT-59655 | (4) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T8 Linear Fluorescent | C-In-LFLmpBlst-T8-36in-25w+El-IS-RLO(86w)-dWP26 | 0.086 | 0.112 | 0.112 |
| LT-54329 | (8) 48in (2) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 96in T12 Linear Fluorescent | C-In-LFLmpBlst-T8-48in-32w-3g+El-IS-RLO(188w)-dWP58-dWC36 | 0.188 | 0.224 | 0.246 |

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Assembly | DEER:Indoor_Non-CFL_Ltg | NON_RES |
| Education - Community College |  |  |
| Education - Primary School |  |  |
| Education - Relocatable Classroom |  |  |
| Education - Secondary School |  |  |
| Education - University |  |  |
| Grocery |  |  |
| Health/Medical - Hospital |  |  |
| Health/Medical - Nursing Home |  |  |
| Lodging - Guest Rooms |  |  |
| Lodging - Hotel |  |  |
| Lodging - Motel |  |  |
| Manufacturing - Bio/Tech |  |  |
| Manufacturing - Light Industrial |  |  |
| Office - Large |  |  |
| Office - Small |  |  |
| Restaurant - Fast-Food |  |  |
| Restaurant - Sit-Down |  |  |
| Retail - Multistory Large |  |  |
| Retail - Single-Story Large |  |  |
| Retail - Small |  |  |
| Storage - Conditioned |  |  |
| Storage - Unconditioned |  |  |
| Warehouse - Refrigerated |  |  |

# Section 4. Costs

Most material costs in the table below are from DEER2016. Some measures had material costs that were not in scope of the cost models used in DEER, so a statewide cost study was used [Attachment 2].

Labor costs are from WO017, for a lamp and ballast retrofit: 2.39 hours at $72.55/hour = $173.10. This value is used for all measures.

## 4.1 Base Case Cost

See Section 4.3 below.

## 4.2 Measure Case Cost

See Section 4.3 below.

## 4.3 Full and Incremental Measure Cost

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |
| NEW/NC |  |  |  |
| RET/ER | (MEC + MLC) – (BEC + BLC) | MEC + MLC | (MEC + MLC) – (BEC + BLC) |
| REF | (MEC + MLC) – (BEC + BLC) | MEC + MLC | N/A |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Note that some of the incremental costs are negative; however these measures are direct install and the first baseline costs are positive.

Full and Incremental Costs

| Measure Code | Measure Name | StdCostID | StdMatlCost | MeasCostID | MeasMatlCost (RET 1BL) | ROB or RET 2BL |
| --- | --- | --- | --- | --- | --- | --- |
| LT-18943 | (1) 24in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 24in T12 Linear Fluorescent | SCE13LG087_02_B010 | $33.08 | SCE17LG087_00_M011 | $24.01 | -$9.08 |
| LT-43895 | (1) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(31w) | $20.60 | LFLmpBlst-T8-48in-32w-3g+El-IS-RLO(25w) | $22.20 | $1.60 |
| LT-69594 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent | SCE13LG087_02_B001 | $21.38 | SCE17LG087_00_M012 | $33.20 | $11.82 |
| LT-89708 | (1) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 48in T8 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(31w) | $20.60 | LFLmpBlst-T8-48in-28w+El-IS-RLO(24w) | $23.50 | $2.90 |
| LT-85932 | (1) 48in Reduced 28 Watt T8 Linear Fluorescent replacing (1) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(31w) | $20.60 | LFLmpBlst-T8-48in-30w+El-IS-NLO(27w) | $22.07 | $1.47 |
| LT-48392 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | SCE13LG087_02_B007 | $62.22 | SCE17LG087_00_M008 | $47.93 | -$14.30 |
| LT-20983 | (1) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent | LFLmpBlst-T8-96in-59w+El-IS-NLO(55w) | $40.47 | LFLmpBlst-T8-96in-59w+El-IS-RLO(49w) | $41.31 | $0.84 |
| LT-59482 | (2) 24in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 24in T12 Linear Fluorescent | SCE13LG087_02_B011 | $39.19 | SCE17LG087_00_M006 | $41.88 | $2.69 |
| LT-91429 | (2) 24in F17 (1) Premium Instant Start Ballast - High Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent | SCE13LG087_02_B012 | $47.28 | SCE17LG087_00_M014 | $57.02 | $9.74 |
| LT-49843 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | SCE13LG087_02_B003 | $33.52 | SCE17LG087_00_M003 | $45.04 | $11.52 |
| LT-39875 | (2) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | SCE13LG087_02_B006 | $60.62 | SCE17LG087_00_M003 | $45.04 | -$15.58 |
| LT-68384 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | SCE13LG087_02_B003 | $33.52 | SCE17LG087_00_M003 | $45.04 | $11.52 |
| LT-40696 | (2) 48in (1) Instant Start Ballast - Normal Light Output w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | SCE13LG087_02_B004 | $56.67 | SCE17LG087_00_M003 | $45.04 | -$11.63 |
| LT-18409 | (2) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (1) 96in T12 Linear Fluorescent | SCE13LG087_02_B002 | $26.10 | SCE17LG087_00_M010 | $29.09 | $2.99 |
| LT-49810 | (2) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(59w) | $29.42 | LFLmpBlst-T8-48in-30w+El-IS-RLO(45w) | $33.20 | $3.78 |
| LT-87326 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent | LFLmpBlst-T8-48in-32w-1g+El-IS-NLO(59w) | $27.38 | LFLmpBlst-T8-48in-28w+El-IS-NLO(53w) | $33.53 | $6.15 |
| LT-32645 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 48in T8 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(59w) | $29.42 | LFLmpBlst-T8-48in-28w+El-IS-RLO(44w) | $34.38 | $4.96 |
| LT-60432 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (2) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(59w) | $29.42 | LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(54w) | $30.94 | $1.52 |
| LT-71214 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | SCE13LG087_02_B003 | $33.52 | SCE17LG087_00_M003 | $45.04 | $11.52 |
| LT-89122 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | SCE13LG087_02_B004 | $56.67 | SCE17LG087_00_M001 | $36.35 | -$20.32 |
| LT-24985 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | SCE13LG087_02_B003 | $33.52 | SCE17LG087_00_M003 | $45.04 | $11.52 |
| LT-30765 | (2) 48in Reduced 28 Watt (1) Instant Start Ballast w/ Reflectors T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | SCE13LG087_02_B004 | $56.67 | SCE17LG087_00_M001 | $36.35 | -$20.32 |
| LT-27685 | (2) 96in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | LFLmpBlst-T8-96in-59w+El-IS-NLO(109w) | $50.16 | LFLmpBlst-T8-96in-59w+El-IS-RLO(98w) | $51.00 | $0.84 |
| LT-39678 | (2) U-Tube (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) T12 U-Tube Fluorescent | SCE13LG087_02_B012 | $47.28 | SCE17LG087_00_M013 | $50.90 | $3.63 |
| LT-50379 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(89w) | $38.24 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(78w) | $39.09 | $0.85 |
| LT-60092 | (3) 48in (1) Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(89w) | $38.24 | LFLmpBlst-T8-48in-32w-3g+El-IS-NLO(83w) | $40.52 | $2.28 |
| LT-79821 | (3) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(89w) | $38.24 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(78w) | $39.09 | $0.85 |
| LT-10154 | (3) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (3) 48in T8 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(89w) | $38.24 | LFLmpBlst-T8-48in-28w+El-IS-RLO(65w) | $45.26 | $7.02 |
| LT-89871 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(112w) | $47.07 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w) | $47.91 | $0.84 |
| LT-99866 | (4) 48in (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(112w) | $47.07 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w) | $47.91 | $0.84 |
| LT-85958 | (4) 48in (1) Premium Instant Start Ballast - Normal Light Output T8 Linear Fluorescent replacing (6) 48in T12 Linear Fluorescent | SCE13LG087_02_B005 | $66.37 | SCE17LG087_00_M004 | $60.56 | -$5.82 |
| LT-59103 | (4) 48in (1) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (2) 96in T12 Linear Fluorescent | SCE13LG087_02_B008 | $68.91 | SCE17LG087_00_M005 | $60.56 | -$8.35 |
| LT-78327 | (4) 48in (2) Instant Start Ballast - Reduced Light Output (New Fixture) T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(112w) | $47.07 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w) | $47.91 | $0.84 |
| LT-20483 | (4) 48in (2) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(112w) | $47.07 | LFLmpBlst-T8-48in-32w-2g+El-IS-RLO(102w) | $47.91 | $0.84 |
| LT-59655 | (4) 48in Reduced 28 Watt (1) Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 48in T8 Linear Fluorescent | SCE13LG087_02_B004 | $56.67 | SCE17LG087_00_M002 | $71.27 | $14.60 |
| LT-54329 | (8) 48in (2) Premium Instant Start Ballast - Reduced Light Output T8 Linear Fluorescent replacing (4) 96in T12 Linear Fluorescent | LFLmpBlst-T8-48in-32w-2g+El-IS-NLO(224w) | $61.75 | LFLmpBlst-T8-48in-32w-3g+El-IS-RLO(188w) | $68.67 | $6.92 |

# Attachments

# References

[493]

[496]

[510]

[A] Southern California Edison 2016 Solutions Directory, Nineteenth Edition, September 2016, pgs. 8-9

[B] https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=22