## Cooling Load
Electrical Specifications
Key Parameters | 2 - 3' T12 | 1 - 3' T12HO | 2 - 3' T8 | 1 - 3' T8 | 3' Canopy (2) | 3' Canopy (1) | 3' Shelf (1) | Cold Cathode
Lamp description type | F32SE F30T12 | F32SHS F36T12HO | F32ILL F32T8-STD | F32ILL F32T8-STD
Lamps per ballast | 2 | 2 | 2 | 2
Minimum starting temp. (F)
Input volts | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Ballast factor
Power factor
Input power (W) | 74 | 114 | 46 | 46
Direct power (W/lamp) | 37 | 57 | 23 | 23 | 15.45 | 15.45 | 6.8333 | 39.6
Power (kW) and Energy (kWh) Consumptions
Key Parameters | 2 - 3' T12 | 1 - 3' T12HO | 2 - 3' T8 | 1 - 3' T8 | 3' Canopy (2) | 3' Canopy (1) | 3' Shelf (1) | Cold Cathode
Direct power (kW/lamp) | 0.037 | 0.057 | 0.023 | 0.023 | 0.01545 | 0.01545 | 0.0068333 | 0.0396
Direct power (kW/fixt) | 0.074 | 0.057 | 0.046 | 0.023 | 0.01545 | 0.01545 | 0.0068333 | 0.0396
Lighting power savings T12 base (kW/fixt) | --- | --- | --- |  | 0.05855 | 0.04155 | 0.050167 | 0.0344
Lighting power savings T8 base(kW/fixt) | --- | --- | --- | --- | 0.03055 | 0.00755 | 0.016167 | -0.0166
Daily hours of operation | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 18
Annual hours of operation | 4710 | 4710 | 4710 | 4710 | 4710 | 4710 | 4710 | 6570
Direct annual energy (kWh/fixt/year)* | 348.54 | 268.47 | 216.66 | 108.33 | 72.7695 | 72.7695 | 32.185 | 260.172
Annual lighting energy savings T12 base (kWh/fixt/year) | --- | --- | --- |  | 275.7705 | 195.7005 | 236.285 | 88.368
Annual lighting energy savings T8 base (kWh/fixt/year) | --- | --- | --- | --- | 143.8905 | 35.5605 | 76.145 | -151.842
% of heat entering cold space | 70.31% | 70% | 70% | 70.31% | 80% | 80% | 80% | 70%
Cooling load due to lighting system (Btu/hr/door) | 47.7388 | 73.2194 | 29.5447 | 29.6755 | 22.6815 | 22.6815 | 10.0317 | 70.9563
Change in cooling load T12 base (Btu/hr/door) | --- | --- | --- |  | 25.0574 | 50.5379 | 63.1876 | -23.2174
Change in cooling load T8 base (Btu/hr/door) | --- | --- | --- | --- | 6.8632 | 6.994 | 19.6438 | -41.2808
Cooling Load (Btu/hr/door) | 47.7388 | 73.2194 | 29.5447 | 29.6755 | 22.6815 | 22.6815 | 10.0317 | 70.9563
COP @ -20F using ARI 1200 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 3.02 | 2.02 | 3.02
Indirect refrig power (kW/lamp) | 0.018317 | 0.028218 | 0.011386 | 0.011386 | 0.0076485 | 0.0051159 | 0.0033828 | 0.013113
TOTAL elect. power (kW/lamp) | 0.055317 | 0.085218 | 0.034386 | 0.034386 | 0.023099 | 0.020566 | 0.010216 | 0.052713
TOTAL elect. power (kW/door)* | 0.06638 | 0.10226 | 0.041263 | 0.041263 | 0.023099 | 0.020566 | 0.0034054 | 0.017571
Annual Energy Use (kWh/yr/door) | 312.6507 | 481.6511 | 194.3505 | 194.3505 | 108.794 | 96.8654 | 16.0394 | 115.4406
*5-door display case equipped with 6 T8 or T12 lamps
Note on J29: Devin Rauss: This number seems high… It seems to be set to the same value as the fluorescent, but these operate at lower temp, so I would think less heat should enter.

## LED Watts
| Replacing | Typical Wattage | Quant. | Length | Brand | Product Code | LED Replacement Savings |  | Wattage Saved | % saved
[7 empty] | Lumens | Wattage
Undershelf | 1-36"T12 | 40 | N/A |  | LEDPower
Undershelf | 1-36"T12 | 40 | 1 | 36" | GE | GE-MT303640USL | 398 | 5.4 | 34.6 | 86.5% | GE led horizontal application
Undershelf | 1-36"T12 | 40 | 1 | 35" | Philps | LCM310 900mm | 800 | 7 | 33 | 82.5% | Philips shelf lighting
Undershelf | 1-36"T12 | 40 | 1 | 35" | Sylvania | LSX/Strip/24V/840/36 | 495 | 8.1 | 31.9 | 79.75% | sylvania shelf lighting
[7 empty] | Average | 6.8333
Undershelf | 1-36"T8 | 24 | N/A |  | LEDPower
Undershelf | 1-36"T8 | 24 | 1 | 36" | GE | GE-MT303640USL | 398 | 5.4 | 18.6 | 77.5% | GE led horizontal application
Undershelf | 1-36"T8 | 24 | 1 | 35" | Philps | LCM310 900mm | 800 | 7 | 17 | 70.83% | Philips shelf lighting
Undershelf | 1-36"T8 | 24 | 1 | 35" | Sylvania | LSX/Strip/24V/840/36 | 495 | 8.1 | 15.9 | 66.25% | sylvania shelf lighting
[7 empty] | Average | 6.8333
| Replacing | Typical Wattage | Quant. | Length | Brand | Product Code | LED Replacement Savings |  | Wattage Saved | %
Canopy | 2-36"T12 | 65 | N/A |  | LEDPower
Canopy | 2-36"T12 | 65 | 1 | 36" | GE | GE-MT303640CAN | 1148 | 15.9 | 49.1 | 75.54% | GE led horizontal application
Canopy | 2-36"T12 | 65 | 1 | 35" | Philps | LDM422 35" value plus | 1080 | 15 | 50 | 76.92% | Philips Canopy Lighting
Canopy | 2-36"T12 | 65 | NA |  | Sylvania
[7 empty] | Average | 15.45
Canopy | 2-36"T8 | 43 | N/A |  | LEDPower
Canopy | 2-36"T8 | 43 | 1 | 36" | GE | GE-MT303640CAN | 1148 | 15.9 | 27.1 | 63.02% | GE led horizontal application
Canopy | 2-36"T8 | 43 | 1 | 35" | Philps | LDM422 35" value plus | 1080 | 15 | 28 | 65.12% | Philips Canopy Lighting
Canopy | 2-36"T8 | 43 | N/A |  | Sylvania
[7 empty] | Average | 15.45

## DI_EEM_Savings_16CTZ
Y = a+b*x1+c*x2+d*x1^2+e*x2^2+f*x1*x2+g*x1^3+h*x2^3+i*x1*x2^2+j*x1^2*x2
[6 empty] | MT | LT
[5 empty] | a | 3.7535 | 9.8665
[5 empty] | b | -0.049642 | -0.23036
[5 empty] | c | 29.459 | 22.9056
|  | MT | LT |  | d | 0.00034207 | 0.0021889 | [7 empty] | CTZ1 | CTZ2 | CTZ3 | CTZ4 | CTZ5 | CTZ6 | CTZ7 | CTZ8 | CTZ9 | CTZ10 | CTZ11 | CTZ12 | CTZ13 | CTZ14 | CTZ15 | CTZ16
| Oversizing Factor (OS) | 13.04% | 13.04% |  | e | -11.7706 | -2.4887 | [5 empty] | Weather Factor |  | 74.26% | 74.8% | 76.05% | 77.87% | 76.26% | 78.9% | 79.73% | 79.38% | 78.58% | 77.74% | 74.95% | 76.13% | 77.88% | 77.03% | 85% | 71.04%
| Defrost Factor | 5% | 10% |  | f | -0.21294 | -0.24805 | [5 empty] | Overall Duty Cycle Factor | MT | 61.34% | 61.79% | 62.82% | 64.33% | 63% | 65.18% | 65.86% | 65.57% | 64.91% | 64.22% | 61.92% | 62.89% | 64.34% | 63.63% | 70.22% | 58.69%
| Weather Div. Factor | 85% | 85% |  | g | -1.4661e-06 | -7.575e-06 | [6 empty] | LT | 58.12% | 58.54% | 59.51% | 60.94% | 59.68% | 61.75% | 62.39% | 62.12% | 61.5% | 60.84% | 58.66% | 59.58% | 60.95% | 60.28% | 66.52% | 55.6%
| Overall Duty Cycle Factor | 70.22% | 66.52% |  | h | 6.8017 | 2.0361 | [5 empty] | EFLH | MT | 2889.3124 | 2910.4544 | 2958.8601 | 3029.8603 | 2967.2949 | 3069.8738 | 3102.0385 | 3088.4402 | 3057.3864 | 3024.6053 | 2916.2404 | 2962.0643 | 3030.2387 | 2997.0853 | 3307.2391 | 2764.0656
| Total Hours | 4710 | 4710 |  | i | -0.020187 | -0.021477 | [6 empty] | LT | 2737.2433 | 2757.2726 | 2803.1306 | 2870.394 | 2811.1215 | 2908.3015 | 2938.7733 | 2925.8907 | 2896.4713 | 2865.4156 | 2762.7541 | 2806.1662 | 2870.7525 | 2839.344 | 3133.1739 | 2618.5885
| EFLH | 3307.2391 | 3133.1739 |  | j | 0.00065794 | 0.00093831
Measure | Measure Unit | Total Unit | Box Temp | SET | Baseline Cooling Load | Compressor Capacity (Baseline Cooling Load with 15% OS) | Post Retrofit Cooling Load | Direct Power Reduction | Direct Energy Reduction | Part-Load-Ratio (Post Retrofit / Comp Cap) | Post Retrofit Duty Cycle Factor w/o Weather Factor Term | CTZ 1 - Arcata Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [69oF] |  |  | CTZ9: CTZ 2 - Santa Rosa Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] |  |  |  | CTZ 3 - Oakland Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [89oF] | [10 empty] | CTZ 4 - Sunnyvale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [88oF] | [10 empty] | CTZ 5 - Santa Maria Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 6 - Torrance Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [86oF] | [10 empty] | CTZ 7 - San Diego Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 8 - Fullerton Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [94oF] | [10 empty] | CTZ 9 - Burbank - Glendale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] | [10 empty] | CTZ 10 - Riverside Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 11 - Red Bluff Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [104oF] | [10 empty] | CTZ 12 - Sacramento Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 13 - Fresno Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [101oF] | [10 empty] | CTZ 14 - Palmdale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [103oF] | [10 empty] | CTZ 15 - Palm Springs Intl Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [113oF] | [10 empty] | CTZ 16 - Blue Canyon Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [85oF]
[12 empty] | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit
|  |  | [oF] | [oF] | [Btu/hr] | [Btu/hr] | [Btu/hr] | [kW] | [kWh] |  |  | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit]
[15 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T12 Baseline)
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (2)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 47.7388 | 54.8997 | 22.6815 | 0.05855 | 275.7705 | 0.41314 | 39.25% | 84 | 9.5174 | 0.0050159 | 9.5174 | 0.0023832 | 0.061183 | 0.061183 | 14.4926 | 3.2715 | 286.9916 | 286.9916 | 111 | 6.4426 | 0.0074099 | 6.4426 | 0.0035206 | 0.062439 | 0.062439 | 21.5662 | 4.8682 | 292.4684 | 292.4684 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.003162 | 0.062043 | 0.062043 | 19.229 | 4.4451 | 290.5544 | 290.5544 | 103 | 7.2811 | 0.0065566 | 7.2811 | 0.0031151 | 0.061991 | 0.061991 | 19.3999 | 4.4843 | 290.6861 | 290.6861 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0028949 | 0.061748 | 0.061748 | 18.4614 | 4.0813 | 290.1505 | 290.1505 | 101 | 7.4998 | 0.0063654 | 7.4998 | 0.0030243 | 0.061891 | 0.061891 | 18.8879 | 4.4111 | 290.2474 | 290.2474 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0028949 | 0.061748 | 0.061748 | 18.7052 | 4.2667 | 290.209 | 290.209 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.003162 | 0.062043 | 0.062043 | 20.6448 | 4.6398 | 291.7754 | 291.7754 | 111 | 6.4426 | 0.0074099 | 6.4426 | 0.0035206 | 0.062439 | 0.062439 | 22.885 | 5.114 | 293.5415 | 293.5415 | 115 | 6.044 | 0.0078985 | 6.044 | 0.0037527 | 0.062696 | 0.062696 | 24.1487 | 5.3928 | 294.5265 | 294.5265 | 119 | 5.6586 | 0.0084365 | 5.6586 | 0.0040083 | 0.062978 | 0.062978 | 25.5172 | 5.5538 | 295.7339 | 295.7339 | 115 | 6.044 | 0.0078985 | 6.044 | 0.0037527 | 0.062696 | 0.062696 | 23.0339 | 5.2813 | 293.5231 | 293.5231 | 116 | 5.9465 | 0.0080281 | 5.9465 | 0.0038143 | 0.062764 | 0.062764 | 23.7797 | 5.4915 | 294.0587 | 294.0587 | 118 | 5.7538 | 0.008297 | 5.7538 | 0.003942 | 0.062905 | 0.062905 | 25.1419 | 5.6133 | 295.299 | 295.299 | 128 | 4.8362 | 0.0098712 | 4.8362 | 0.00469 | 0.063731 | 0.063731 | 29.5849 | 7.3695 | 297.9859 | 297.9859 | 100 | 7.6105 | 0.0062728 | 7.6105 | 0.0029803 | 0.061842 | 0.061842 | 20.7455 | 3.9139 | 292.6021 | 292.6021
LT, (2)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 47.7388 | 54.8997 | 22.6815 | 0.05855 | 275.7705 | 0.41314 | 37.18% | 79 | 7.7386 | 0.0061689 | 7.7386 | 0.0029309 | 0.061788 | 0.061788 | 16.8858 | 3.8117 | 288.8446 | 288.8446 | 106 | 4.9788 | 0.0095885 | 4.9788 | 0.0045557 | 0.063583 | 0.063583 | 26.4382 | 5.968 | 296.2406 | 296.2406 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.0040686 | 0.063045 | 0.063045 | 23.44 | 5.4186 | 293.7919 | 293.7919 | 98 | 5.6656 | 0.0084261 | 5.6656 | 0.0040034 | 0.062973 | 0.062973 | 23.6194 | 5.4597 | 293.9303 | 293.9303 | 93 | 6.144 | 0.00777 | 6.144 | 0.0036917 | 0.062628 | 0.062628 | 22.3031 | 4.9306 | 293.143 | 293.143 | 96 | 5.852 | 0.0081578 | 5.852 | 0.0038759 | 0.062832 | 0.062832 | 22.9324 | 5.3556 | 293.3473 | 293.3473 | 93 | 6.144 | 0.00777 | 6.144 | 0.0036917 | 0.062628 | 0.062628 | 22.5976 | 5.1545 | 293.2136 | 293.2136 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.0040686 | 0.063045 | 0.063045 | 25.1658 | 5.6559 | 295.2804 | 295.2804 | 106 | 4.9788 | 0.0095885 | 4.9788 | 0.0045557 | 0.063583 | 0.063583 | 28.0549 | 6.2693 | 297.5561 | 297.5561 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.0048616 | 0.063921 | 0.063921 | 29.6383 | 6.6187 | 298.7901 | 298.7901 | 114 | 4.3682 | 0.010929 | 4.3682 | 0.0051924 | 0.064286 | 0.064286 | 31.3154 | 6.8157 | 300.2701 | 300.2701 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.0048616 | 0.063921 | 0.063921 | 28.27 | 6.4818 | 297.5587 | 297.5587 | 111 | 4.5897 | 0.010401 | 4.5897 | 0.0049418 | 0.064009 | 0.064009 | 29.1878 | 6.7404 | 298.218 | 298.218 | 113 | 4.4411 | 0.010749 | 4.4411 | 0.0051071 | 0.064192 | 0.064192 | 30.8584 | 6.8896 | 299.7393 | 299.7393 | 123 | 3.7435 | 0.012752 | 3.7435 | 0.0060588 | 0.065244 | 0.065244 | 36.2083 | 9.0193 | 302.9595 | 302.9595 | 95 | 5.9476 | 0.0080266 | 5.9476 | 0.0038136 | 0.062763 | 0.062763 | 25.1487 | 4.7446 | 296.1746 | 296.1746
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 73.2194 | 84.2023 | 22.6815 | 0.04155 | 195.7005 | 0.26937 | 25.59% | 84 | 9.5174 | 0.0076932 | 9.5174 | 0.0023832 | 0.04686 | 0.04686 | 22.228 | 2.133 | 215.7955 | 215.7955 | 111 | 6.4426 | 0.011365 | 6.4426 | 0.0035206 | 0.049394 | 0.049394 | 33.0771 | 3.1741 | 225.6035 | 225.6035 | 104 | 7.1731 | 0.010207 | 7.1731 | 0.003162 | 0.048595 | 0.048595 | 29.4925 | 2.8982 | 222.2947 | 222.2947 | 103 | 7.2811 | 0.010056 | 7.2811 | 0.0031151 | 0.048491 | 0.048491 | 29.7546 | 2.9238 | 222.5313 | 222.5313 | 98 | 7.8349 | 0.0093453 | 7.8349 | 0.0028949 | 0.048 | 0.048 | 28.3151 | 2.661 | 221.3546 | 221.3546 | 101 | 7.4998 | 0.0097629 | 7.4998 | 0.0030243 | 0.048289 | 0.048289 | 28.9694 | 2.876 | 221.7939 | 221.7939 | 98 | 7.8349 | 0.0093453 | 7.8349 | 0.0028949 | 0.048 | 0.048 | 28.689 | 2.7818 | 221.6077 | 221.6077 | 104 | 7.1731 | 0.010207 | 7.1731 | 0.003162 | 0.048595 | 0.048595 | 31.6639 | 3.0252 | 224.3392 | 224.3392 | 111 | 6.4426 | 0.011365 | 6.4426 | 0.0035206 | 0.049394 | 0.049394 | 35.0999 | 3.3343 | 227.4661 | 227.4661 | 115 | 6.044 | 0.012114 | 6.044 | 0.0037527 | 0.049912 | 0.049912 | 37.0381 | 3.5161 | 229.2225 | 229.2225 | 119 | 5.6586 | 0.01294 | 5.6586 | 0.0040083 | 0.050481 | 0.050481 | 39.1369 | 3.621 | 231.2164 | 231.2164 | 115 | 6.044 | 0.012114 | 6.044 | 0.0037527 | 0.049912 | 0.049912 | 35.3282 | 3.4434 | 227.5853 | 227.5853 | 116 | 5.9465 | 0 | 5.9465 | 0.0038143 | 0.037736 | 0.037736 | 0 | 3.5804 | 192.1201 | 192.1201 | 118 | 5.7538 | 0.012725 | 5.7538 | 0.003942 | 0.050333 | 0.050333 | 38.5613 | 3.6599 | 230.6019 | 230.6019 | 128 | 4.8362 | 0.01514 | 4.8362 | 0.00469 | 0.052 | 0.052 | 45.3758 | 4.8049 | 236.2714 | 236.2714 | 100 | 7.6105 | 0.0096208 | 7.6105 | 0.0029803 | 0.048191 | 0.048191 | 31.8184 | 2.5518 | 224.967 | 224.967
LT, (1)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 73.2194 | 84.2023 | 22.6815 | 0.04155 | 195.7005 | 0.26937 | 24.24% | 79 | 7.7386 | 0.0094616 | 7.7386 | 0.0029309 | 0.048081 | 0.048081 | 25.8986 | 2.4852 | 219.1138 | 219.1138 | 106 | 4.9788 | 0.014706 | 4.9788 | 0.0045557 | 0.051701 | 0.051701 | 40.5495 | 3.8911 | 232.3588 | 232.3588 | 99 | 5.5748 | 0.013134 | 5.5748 | 0.0040686 | 0.050615 | 0.050615 | 35.9511 | 3.5329 | 228.1187 | 228.1187 | 98 | 5.6656 | 0.012924 | 5.6656 | 0.0040034 | 0.05047 | 0.05047 | 36.2263 | 3.5597 | 228.3671 | 228.3671 | 93 | 6.144 | 0.011917 | 6.144 | 0.0036917 | 0.049776 | 0.049776 | 34.2073 | 3.2148 | 226.6931 | 226.6931 | 96 | 5.852 | 0.012512 | 5.852 | 0.0038759 | 0.050186 | 0.050186 | 35.1726 | 3.4918 | 227.3812 | 227.3812 | 93 | 6.144 | 0.011917 | 6.144 | 0.0036917 | 0.049776 | 0.049776 | 34.6591 | 3.3607 | 226.9988 | 226.9988 | 99 | 5.5748 | 0.013134 | 5.5748 | 0.0040686 | 0.050615 | 0.050615 | 38.598 | 3.6876 | 230.6109 | 230.6109 | 106 | 4.9788 | 0.014706 | 4.9788 | 0.0045557 | 0.051701 | 0.051701 | 43.0292 | 4.0876 | 234.6422 | 234.6422 | 110 | 4.6654 | 0.015694 | 4.6654 | 0.0048616 | 0.052383 | 0.052383 | 45.4577 | 4.3154 | 236.8428 | 236.8428 | 114 | 4.3682 | 0.016762 | 4.3682 | 0.0051924 | 0.05312 | 0.05312 | 48.0299 | 4.4438 | 239.2866 | 239.2866 | 110 | 4.6654 | 0.015694 | 4.6654 | 0.0048616 | 0.052383 | 0.052383 | 43.3591 | 4.2261 | 234.8335 | 234.8335 | 111 | 4.5897 | 0.015953 | 4.5897 | 0.0049418 | 0.052561 | 0.052561 | 44.7668 | 4.3947 | 236.0726 | 236.0726 | 113 | 4.4411 | 0.016487 | 4.4411 | 0.0051071 | 0.052929 | 0.052929 | 47.329 | 4.492 | 238.5375 | 238.5375 | 123 | 3.7435 | 0.019559 | 3.7435 | 0.0060588 | 0.05505 | 0.05505 | 55.5344 | 5.8806 | 245.3543 | 245.3543 | 95 | 5.9476 | 0.012311 | 5.9476 | 0.0038136 | 0.050047 | 0.050047 | 38.5718 | 3.0935 | 231.1788 | 231.1788
MT, (2)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 29.5447 | 33.9764 | 22.6815 | 0.03055 | 143.8905 | 0.66757 | 63.42% | 84 | 9.5174 | 0.0031043 | 9.5174 | 0.0023832 | 0.031271 | 0.031271 | 8.9692 | 5.2861 | 147.5736 | 147.5736 | 111 | 6.4426 | 0.0045858 | 6.4426 | 0.0035206 | 0.031615 | 0.031615 | 13.3469 | 7.8662 | 149.3712 | 149.3712 | 104 | 7.1731 | 0.0041188 | 7.1731 | 0.003162 | 0.031507 | 0.031507 | 11.9005 | 7.1826 | 148.6084 | 148.6084 | 103 | 7.2811 | 0.0040577 | 7.2811 | 0.0031151 | 0.031493 | 0.031493 | 12.0062 | 7.2459 | 148.6509 | 148.6509 | 98 | 7.8349 | 0.0037709 | 7.8349 | 0.0028949 | 0.031426 | 0.031426 | 11.4254 | 6.5947 | 148.7212 | 148.7212 | 101 | 7.4998 | 0.0039394 | 7.4998 | 0.0030243 | 0.031465 | 0.031465 | 11.6894 | 7.1275 | 148.4524 | 148.4524 | 98 | 7.8349 | 0.0037709 | 7.8349 | 0.0028949 | 0.031426 | 0.031426 | 11.5763 | 6.8941 | 148.5726 | 148.5726 | 104 | 7.1731 | 0.0041188 | 7.1731 | 0.003162 | 0.031507 | 0.031507 | 12.7766 | 7.4971 | 149.17 | 149.17 | 111 | 6.4426 | 0.0045858 | 6.4426 | 0.0035206 | 0.031615 | 0.031615 | 14.1631 | 8.2633 | 149.7903 | 149.7903 | 115 | 6.044 | 0.0048882 | 6.044 | 0.0037527 | 0.031686 | 0.031686 | 14.9452 | 8.7138 | 150.1219 | 150.1219 | 119 | 5.6586 | 0.0052212 | 5.6586 | 0.0040083 | 0.031763 | 0.031763 | 15.7921 | 8.9739 | 150.7087 | 150.7087 | 115 | 6.044 | 0.0048882 | 6.044 | 0.0037527 | 0.031686 | 0.031686 | 14.2552 | 8.5336 | 149.6122 | 149.6122 | 116 | 5.9465 | 0.0049684 | 5.9465 | 0.0038143 | 0.031704 | 0.031704 | 14.7168 | 8.8732 | 149.7341 | 149.7341 | 118 | 5.7538 | 0.0051348 | 5.7538 | 0.003942 | 0.031743 | 0.031743 | 15.5598 | 9.0701 | 150.3802 | 150.3802 | 128 | 4.8362 | 0.0061091 | 4.8362 | 0.00469 | 0.031969 | 0.031969 | 18.3095 | 11.9077 | 150.2923 | 150.2923 | 100 | 7.6105 | 0.0038821 | 7.6105 | 0.0029803 | 0.031452 | 0.031452 | 12.839 | 6.3241 | 150.4054 | 150.4054
LT, (2)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 29.5447 | 33.9764 | 22.6815 | 0.03055 | 143.8905 | 0.66757 | 60.08% | 79 | 7.7386 | 0.0038178 | 7.7386 | 0.0029309 | 0.031437 | 0.031437 | 10.4503 | 6.1591 | 148.1817 | 148.1817 | 106 | 4.9788 | 0.0059341 | 4.9788 | 0.0045557 | 0.031928 | 0.031928 | 16.3621 | 9.6432 | 150.6093 | 150.6093 | 99 | 5.5748 | 0.0052997 | 5.5748 | 0.0040686 | 0.031781 | 0.031781 | 14.5066 | 8.7555 | 149.6416 | 149.6416 | 98 | 5.6656 | 0.0052147 | 5.6656 | 0.0040034 | 0.031761 | 0.031761 | 14.6176 | 8.8219 | 149.6863 | 149.6863 | 93 | 6.144 | 0.0048087 | 6.144 | 0.0036917 | 0.031667 | 0.031667 | 13.803 | 7.967 | 149.7264 | 149.7264 | 96 | 5.852 | 0.0050487 | 5.852 | 0.0038759 | 0.031723 | 0.031723 | 14.1925 | 8.6537 | 149.4292 | 149.4292 | 93 | 6.144 | 0.0048087 | 6.144 | 0.0036917 | 0.031667 | 0.031667 | 13.9852 | 8.3288 | 149.547 | 149.547 | 99 | 5.5748 | 0.0052997 | 5.5748 | 0.0040686 | 0.031781 | 0.031781 | 15.5746 | 9.1389 | 150.3262 | 150.3262 | 106 | 4.9788 | 0.0059341 | 4.9788 | 0.0045557 | 0.031928 | 0.031928 | 17.3627 | 10.1301 | 151.1231 | 151.1231 | 110 | 4.6654 | 0.0063327 | 4.6654 | 0.0048616 | 0.032021 | 0.032021 | 18.3426 | 10.6946 | 151.5385 | 151.5385 | 114 | 4.3682 | 0.0067636 | 4.3682 | 0.0051924 | 0.032121 | 0.032121 | 19.3805 | 11.013 | 152.258 | 152.258 | 110 | 4.6654 | 0.0063327 | 4.6654 | 0.0048616 | 0.032021 | 0.032021 | 17.4958 | 10.4734 | 150.9128 | 150.9128 | 111 | 4.5897 | 0.0064372 | 4.5897 | 0.0049418 | 0.032045 | 0.032045 | 18.0638 | 10.8912 | 151.0631 | 151.0631 | 113 | 4.4411 | 0.0066525 | 4.4411 | 0.0051071 | 0.032095 | 0.032095 | 19.0977 | 11.1324 | 151.8558 | 151.8558 | 123 | 3.7435 | 0.0078922 | 3.7435 | 0.0060588 | 0.032383 | 0.032383 | 22.4086 | 14.5736 | 151.7255 | 151.7255 | 95 | 5.9476 | 0.0049675 | 5.9476 | 0.0038136 | 0.031704 | 0.031704 | 15.5641 | 7.6664 | 151.7882 | 151.7882
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 29.6755 | 34.1268 | 22.6815 | 0.00755 | 35.5605 | 0.66462 | 63.14% | 84 | 9.5174 | 0.003118 | 9.5174 | 0.0023832 | 0.0082849 | 0.0082849 | 9.0089 | 5.2628 | 39.3066 | 39.3066 | 111 | 6.4426 | 0.0046062 | 6.4426 | 0.0035206 | 0.0086356 | 0.0086356 | 13.406 | 7.8315 | 41.135 | 41.135 | 104 | 7.1731 | 0.004137 | 7.1731 | 0.003162 | 0.008525 | 0.008525 | 11.9532 | 7.1509 | 40.3628 | 40.3628 | 103 | 7.2811 | 0.0040757 | 7.2811 | 0.0031151 | 0.0085106 | 0.0085106 | 12.0594 | 7.2139 | 40.406 | 40.406 | 98 | 7.8349 | 0.0037876 | 7.8349 | 0.0028949 | 0.0084427 | 0.0084427 | 11.476 | 6.5656 | 40.4709 | 40.4709 | 101 | 7.4998 | 0.0039569 | 7.4998 | 0.0030243 | 0.0084826 | 0.0084826 | 11.7412 | 7.0961 | 40.2056 | 40.2056 | 98 | 7.8349 | 0.0037876 | 7.8349 | 0.0028949 | 0.0084427 | 0.0084427 | 11.6275 | 6.8637 | 40.3243 | 40.3243 | 104 | 7.1731 | 0.004137 | 7.1731 | 0.003162 | 0.008525 | 0.008525 | 12.8332 | 7.4641 | 40.9297 | 40.9297 | 111 | 6.4426 | 0.0046062 | 6.4426 | 0.0035206 | 0.0086356 | 0.0086356 | 14.2258 | 8.2269 | 41.5594 | 41.5594 | 115 | 6.044 | 0.0049099 | 6.044 | 0.0037527 | 0.0087072 | 0.0087072 | 15.0114 | 8.6753 | 41.8965 | 41.8965 | 119 | 5.6586 | 0.0052443 | 5.6586 | 0.0040083 | 0.008786 | 0.008786 | 15.862 | 8.9343 | 42.4882 | 42.4882 | 115 | 6.044 | 0.0049099 | 6.044 | 0.0037527 | 0.0087072 | 0.0087072 | 14.3184 | 8.4959 | 41.3829 | 41.3829 | 116 | 5.9465 | 0.0049904 | 5.9465 | 0.0038143 | 0.0087262 | 0.0087262 | 14.782 | 8.8341 | 41.5084 | 41.5084 | 118 | 5.7538 | 0.0051576 | 5.7538 | 0.003942 | 0.0087656 | 0.0087656 | 15.6287 | 9.0301 | 42.1591 | 42.1591 | 128 | 4.8362 | 0.0061362 | 4.8362 | 0.00469 | 0.0089962 | 0.0089962 | 18.3906 | 11.8552 | 42.0959 | 42.0959 | 100 | 7.6105 | 0.0038993 | 7.6105 | 0.0029803 | 0.008469 | 0.008469 | 12.8958 | 6.2962 | 42.1601 | 42.1601
LT, (1)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 29.6755 | 34.1268 | 22.6815 | 0.00755 | 35.5605 | 0.66462 | 59.82% | 79 | 7.7386 | 0.0038347 | 7.7386 | 0.0029309 | 0.0084538 | 0.0084538 | 10.4966 | 6.1319 | 39.9252 | 39.9252 | 106 | 4.9788 | 0.0059604 | 4.9788 | 0.0045557 | 0.0089548 | 0.0089548 | 16.4345 | 9.6007 | 42.3943 | 42.3943 | 99 | 5.5748 | 0.0053232 | 5.5748 | 0.0040686 | 0.0088046 | 0.0088046 | 14.5708 | 8.7169 | 41.4144 | 41.4144 | 98 | 5.6656 | 0.0052378 | 5.6656 | 0.0040034 | 0.0087845 | 0.0087845 | 14.6823 | 8.783 | 41.4599 | 41.4599 | 93 | 6.144 | 0.00483 | 6.144 | 0.0036917 | 0.0086884 | 0.0086884 | 13.8641 | 7.9319 | 41.4927 | 41.4927 | 96 | 5.852 | 0.005071 | 5.852 | 0.0038759 | 0.0087452 | 0.0087452 | 14.2553 | 8.6156 | 41.2002 | 41.2002 | 93 | 6.144 | 0.00483 | 6.144 | 0.0036917 | 0.0086884 | 0.0086884 | 14.0472 | 8.2921 | 41.3156 | 41.3156 | 99 | 5.5748 | 0.0053232 | 5.5748 | 0.0040686 | 0.0088046 | 0.0088046 | 15.6436 | 9.0986 | 42.1055 | 42.1055 | 106 | 4.9788 | 0.0059604 | 4.9788 | 0.0045557 | 0.0089548 | 0.0089548 | 17.4396 | 10.0854 | 42.9146 | 42.9146 | 110 | 4.6654 | 0.0063608 | 4.6654 | 0.0048616 | 0.0090491 | 0.0090491 | 18.4238 | 10.6474 | 43.3369 | 43.3369 | 114 | 4.3682 | 0.0067935 | 4.3682 | 0.0051924 | 0.0091511 | 0.0091511 | 19.4663 | 10.9644 | 44.0624 | 44.0624 | 110 | 4.6654 | 0.0063608 | 4.6654 | 0.0048616 | 0.0090491 | 0.0090491 | 17.5732 | 10.4273 | 42.7065 | 42.7065 | 111 | 4.5897 | 0.0064657 | 4.5897 | 0.0049418 | 0.0090739 | 0.0090739 | 18.1438 | 10.8432 | 42.8611 | 42.8611 | 113 | 4.4411 | 0.006682 | 4.4411 | 0.0051071 | 0.0091248 | 0.0091248 | 19.1822 | 11.0833 | 43.6595 | 43.6595 | 123 | 3.7435 | 0.0079271 | 3.7435 | 0.0060588 | 0.0094183 | 0.0094183 | 22.5079 | 14.5093 | 43.559 | 43.559 | 95 | 5.9476 | 0.0049895 | 5.9476 | 0.0038136 | 0.0087259 | 0.0087259 | 15.633 | 7.6326 | 43.5609 | 43.5609
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T12 to CC retrofit | /Fixture | 1 | 38 | 28 | 47.7388 | 54.8997 | 70.9563 | 0.0344 | 88.368 | 1.2925 | 122.8% | 84 | 9.5174 | 0.0050159 | 9.5174 | 0.0074554 | 0.031961 | 0.031961 | 14.4926 | 32.0173 | 70.8433 | 70.8433 | 111 | 6.4426 | 0.0074099 | 6.4426 | 0.011014 | 0.030796 | 0.030796 | 21.5662 | 47.6443 | 62.2899 | 62.2899 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | 0.031163 | 0.031163 | 19.229 | 43.5036 | 64.0935 | 64.0935 | 103 | 7.2811 | 0.0065566 | 7.2811 | 0.0097453 | 0.031211 | 0.031211 | 19.3999 | 43.887 | 63.8809 | 63.8809 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0090565 | 0.031437 | 0.031437 | 18.4614 | 39.9429 | 66.8865 | 66.8865 | 99 | 7.7222 | 0.006182 | 7.7222 | 0.0091886 | 0.031393 | 0.031393 | 18.3439 | 41.9265 | 64.7854 | 64.7854 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0090565 | 0.031437 | 0.031437 | 18.7052 | 41.7567 | 65.3165 | 65.3165 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | 0.031163 | 0.031163 | 20.6448 | 45.4087 | 63.604 | 63.604 | 109 | 6.6469 | 0.0071821 | 6.6469 | 0.010675 | 0.030907 | 0.030907 | 22.1815 | 48.511 | 62.0385 | 62.0385 | 115 | 6.044 | 0.0078985 | 6.044 | 0.01174 | 0.030559 | 0.030559 | 24.1487 | 52.7777 | 59.739 | 59.739 | 119 | 5.6586 | 0.0084365 | 5.6586 | 0.01254 | 0.030297 | 0.030297 | 25.5172 | 54.3532 | 59.532 | 59.532 | 115 | 6.044 | 0.0078985 | 6.044 | 0.01174 | 0.030559 | 0.030559 | 23.0339 | 51.6864 | 59.7155 | 59.7155 | 116 | 5.9465 | 0.0080281 | 5.9465 | 0.011932 | 0.030496 | 0.030496 | 23.7797 | 53.7436 | 58.4041 | 58.4041 | 123 | 5.2856 | 0.0090318 | 5.2856 | 0.013424 | 0.030007 | 0.030007 | 27.3686 | 59.8015 | 55.9351 | 55.9351 | 126 | 5.0138 | 0.0095215 | 5.0138 | 0.014152 | 0.029769 | 0.029769 | 28.5368 | 69.568 | 47.3368 | 47.3368 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | 0.031163 | 0.031163 | 22.0104 | 40.6395 | 69.7389 | 69.7389
LT, T12 to CC retrofit | /Fixture | 1 | 0 | -10 | 47.7388 | 54.8997 | 70.9563 | 0.0344 | 88.368 | 1.2925 | 116.3% | 79 | 7.7386 | 0.0061689 | 7.7386 | 0.0091691 | 0.0314 | 0.0314 | 16.8858 | 37.3043 | 67.9495 | 67.9495 | 106 | 4.9788 | 0.0095885 | 4.9788 | 0.014252 | 0.029737 | 0.029737 | 26.4382 | 58.4075 | 56.3986 | 56.3986 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | 0.030235 | 0.030235 | 23.44 | 53.0305 | 58.7775 | 58.7775 | 98 | 5.6656 | 0.0084261 | 5.6656 | 0.012524 | 0.030302 | 0.030302 | 23.6194 | 53.4325 | 58.555 | 58.555 | 93 | 6.144 | 0.00777 | 6.144 | 0.011549 | 0.030621 | 0.030621 | 22.3031 | 48.2549 | 62.4162 | 62.4162 | 94 | 6.0449 | 0.0078974 | 6.0449 | 0.011738 | 0.030559 | 0.030559 | 22.2005 | 50.7411 | 59.8274 | 59.8274 | 93 | 6.144 | 0.00777 | 6.144 | 0.011549 | 0.030621 | 0.030621 | 22.5976 | 50.4461 | 60.5196 | 60.5196 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | 0.030235 | 0.030235 | 25.1658 | 55.3529 | 58.1809 | 58.1809 | 104 | 5.1424 | 0.0092834 | 5.1424 | 0.013798 | 0.029885 | 0.029885 | 27.1621 | 59.4036 | 56.1265 | 56.1265 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.015209 | 0.029423 | 0.029423 | 29.6383 | 64.7752 | 53.231 | 53.231 | 114 | 4.3682 | 0.010929 | 4.3682 | 0.016244 | 0.029085 | 0.029085 | 31.3154 | 66.7037 | 52.9797 | 52.9797 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.015209 | 0.029423 | 0.029423 | 28.27 | 63.4359 | 53.2021 | 53.2021 | 111 | 4.5897 | 0.010401 | 4.5897 | 0.01546 | 0.029341 | 0.029341 | 29.1878 | 65.9663 | 51.5896 | 51.5896 | 118 | 4.0843 | 0.011689 | 4.0843 | 0.017373 | 0.028715 | 0.028715 | 33.5548 | 73.3187 | 48.6041 | 48.6041 | 121 | 3.8782 | 0.012309 | 3.8782 | 0.018296 | 0.028413 | 0.028413 | 34.9506 | 85.2038 | 38.1148 | 38.1148 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | 0.030235 | 0.030235 | 26.8305 | 49.5393 | 65.6593 | 65.6593
| /Fixture | [13 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T8 Baseline) | /Fixture
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Shelf | /Fixture | 1 | 38 | 28 | 73.2194 | 84.2023 | 10.0317 | 0.050167 | 236.285 | 0.11914 | 11.32% | 84 | 9.5174 | 0.0076932 | 9.5174 | 0.001054 | 0.056806 | 0.056806 | 22.228 | 0.41725 | 258.0958 | 258.0958 | 111 | 6.4426 | 0.011365 | 6.4426 | 0.0015571 | 0.059974 | 0.059974 | 33.0771 | 0.62091 | 268.7412 | 268.7412 | 104 | 7.1731 | 0.010207 | 7.1731 | 0.0013985 | 0.058976 | 0.058976 | 29.4925 | 0.56694 | 265.2105 | 265.2105 | 103 | 7.2811 | 0.010056 | 7.2811 | 0.0013778 | 0.058845 | 0.058845 | 29.7546 | 0.57194 | 265.4676 | 265.4676 | 98 | 7.8349 | 0.0093453 | 7.8349 | 0.0012804 | 0.058232 | 0.058232 | 28.3151 | 0.52054 | 264.0795 | 264.0795 | 101 | 7.4998 | 0.0097629 | 7.4998 | 0.0013376 | 0.058592 | 0.058592 | 28.9694 | 0.5626 | 264.6918 | 264.6918 | 98 | 7.8349 | 0.0093453 | 7.8349 | 0.0012804 | 0.058232 | 0.058232 | 28.689 | 0.54418 | 264.4298 | 264.4298 | 104 | 7.1731 | 0.010207 | 7.1731 | 0.0013985 | 0.058976 | 0.058976 | 31.6639 | 0.59177 | 267.3571 | 267.3571 | 111 | 6.4426 | 0.011365 | 6.4426 | 0.0015571 | 0.059974 | 0.059974 | 35.0999 | 0.65225 | 270.7326 | 270.7326 | 115 | 6.044 | 0.012114 | 6.044 | 0.0016598 | 0.060621 | 0.060621 | 37.0381 | 0.68781 | 272.6353 | 272.6353 | 119 | 5.6586 | 0.01294 | 5.6586 | 0.0017728 | 0.061333 | 0.061333 | 39.1369 | 0.70834 | 274.7136 | 274.7136 | 115 | 6.044 | 0.012114 | 6.044 | 0.0016598 | 0.060621 | 0.060621 | 35.3282 | 0.67358 | 270.9396 | 270.9396 | 116 | 5.9465 | 0.012313 | 5.9465 | 0.001687 | 0.060793 | 0.060793 | 36.4721 | 0.70039 | 272.0567 | 272.0567 | 118 | 5.7538 | 0.012725 | 5.7538 | 0.0017435 | 0.061149 | 0.061149 | 38.5613 | 0.71593 | 274.1303 | 274.1303 | 128 | 4.8362 | 0.01514 | 4.8362 | 0.0020743 | 0.063232 | 0.063232 | 45.3758 | 0.93992 | 280.7208 | 280.7208 | 100 | 7.6105 | 0.0096208 | 7.6105 | 0.0013181 | 0.058469 | 0.058469 | 31.8184 | 0.49918 | 267.6042 | 267.6042
LT, (1)T12 to LED Shelf | /Fixture | 1 | 0 | -10 | 73.2194 | 84.2023 | 10.0317 | 0.050167 | 236.285 | 0.11914 | 10.72% | 79 | 7.7386 | 0.0094616 | 7.7386 | 0.0012963 | 0.058332 | 0.058332 | 25.8986 | 0.48616 | 261.6974 | 261.6974 | 106 | 4.9788 | 0.014706 | 4.9788 | 0.0020149 | 0.062858 | 0.062858 | 40.5495 | 0.76118 | 276.0733 | 276.0733 | 99 | 5.5748 | 0.013134 | 5.5748 | 0.0017995 | 0.061501 | 0.061501 | 35.9511 | 0.6911 | 271.545 | 271.545 | 98 | 5.6656 | 0.012924 | 5.6656 | 0.0017706 | 0.06132 | 0.06132 | 36.2263 | 0.69634 | 271.8149 | 271.8149 | 93 | 6.144 | 0.011917 | 6.144 | 0.0016328 | 0.060451 | 0.060451 | 34.2073 | 0.62886 | 269.8635 | 269.8635 | 96 | 5.852 | 0.012512 | 5.852 | 0.0017143 | 0.060964 | 0.060964 | 35.1726 | 0.68307 | 270.7745 | 270.7745 | 93 | 6.144 | 0.011917 | 6.144 | 0.0016328 | 0.060451 | 0.060451 | 34.6591 | 0.65742 | 270.2867 | 270.2867 | 99 | 5.5748 | 0.013134 | 5.5748 | 0.0017995 | 0.061501 | 0.061501 | 38.598 | 0.72137 | 274.1616 | 274.1616 | 106 | 4.9788 | 0.014706 | 4.9788 | 0.0020149 | 0.062858 | 0.062858 | 43.0292 | 0.7996 | 278.5146 | 278.5146 | 110 | 4.6654 | 0.015694 | 4.6654 | 0.0021502 | 0.063711 | 0.063711 | 45.4577 | 0.84416 | 280.8985 | 280.8985 | 114 | 4.3682 | 0.016762 | 4.3682 | 0.0022965 | 0.064632 | 0.064632 | 48.0299 | 0.86929 | 283.4456 | 283.4456 | 110 | 4.6654 | 0.015694 | 4.6654 | 0.0021502 | 0.063711 | 0.063711 | 43.3591 | 0.82671 | 278.8174 | 278.8174 | 111 | 4.5897 | 0.015953 | 4.5897 | 0.0021857 | 0.063934 | 0.063934 | 44.7668 | 0.85968 | 280.1921 | 280.1921 | 113 | 4.4411 | 0.016487 | 4.4411 | 0.0022588 | 0.064394 | 0.064394 | 47.329 | 0.87872 | 282.7353 | 282.7353 | 123 | 3.7435 | 0.019559 | 3.7435 | 0.0026797 | 0.067046 | 0.067046 | 55.5344 | 1.1503 | 290.6691 | 290.6691 | 95 | 5.9476 | 0.012311 | 5.9476 | 0.0016867 | 0.060791 | 0.060791 | 38.5718 | 0.60513 | 274.2517 | 274.2517
MT, (1)T8 to LED Shelf | /Fixture | 1 | 38 | 28 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 27.93% | 84 | 9.5174 | 0.003118 | 9.5174 | 0.001054 | 0.018231 | 0.018231 | 9.0089 | 1.0295 | 84.1244 | 84.1244 | 111 | 6.4426 | 0.0046062 | 6.4426 | 0.0015571 | 0.019216 | 0.019216 | 13.406 | 1.532 | 88.019 | 88.019 | 104 | 7.1731 | 0.004137 | 7.1731 | 0.0013985 | 0.018905 | 0.018905 | 11.9532 | 1.3988 | 86.6993 | 86.6993 | 103 | 7.2811 | 0.0040757 | 7.2811 | 0.0013778 | 0.018865 | 0.018865 | 12.0594 | 1.4112 | 86.7932 | 86.7932 | 98 | 7.8349 | 0.0037876 | 7.8349 | 0.0012804 | 0.018674 | 0.018674 | 11.476 | 1.2843 | 86.3366 | 86.3366 | 101 | 7.4998 | 0.0039569 | 7.4998 | 0.0013376 | 0.018786 | 0.018786 | 11.7412 | 1.3881 | 86.498 | 86.498 | 98 | 7.8349 | 0.0037876 | 7.8349 | 0.0012804 | 0.018674 | 0.018674 | 11.6275 | 1.3427 | 86.4299 | 86.4299 | 104 | 7.1731 | 0.004137 | 7.1731 | 0.0013985 | 0.018905 | 0.018905 | 12.8332 | 1.4601 | 87.5181 | 87.5181 | 111 | 6.4426 | 0.0046062 | 6.4426 | 0.0015571 | 0.019216 | 0.019216 | 14.2258 | 1.6093 | 88.7615 | 88.7615 | 115 | 6.044 | 0.0049099 | 6.044 | 0.0016598 | 0.019417 | 0.019417 | 15.0114 | 1.697 | 89.4593 | 89.4593 | 119 | 5.6586 | 0.0052443 | 5.6586 | 0.0017728 | 0.019638 | 0.019638 | 15.862 | 1.7477 | 90.2593 | 90.2593 | 115 | 6.044 | 0.0049099 | 6.044 | 0.0016598 | 0.019417 | 0.019417 | 14.3184 | 1.662 | 88.8014 | 88.8014 | 116 | 5.9465 | 0.0049904 | 5.9465 | 0.001687 | 0.01947 | 0.01947 | 14.782 | 1.7281 | 89.1989 | 89.1989 | 118 | 5.7538 | 0.0051576 | 5.7538 | 0.0017435 | 0.019581 | 0.019581 | 15.6287 | 1.7664 | 90.0073 | 90.0073 | 128 | 4.8362 | 0.0061362 | 4.8362 | 0.0020743 | 0.020229 | 0.020229 | 18.3906 | 2.3191 | 92.2165 | 92.2165 | 100 | 7.6105 | 0.0038993 | 7.6105 | 0.0013181 | 0.018748 | 0.018748 | 12.8958 | 1.2317 | 87.8092 | 87.8092
LT, (1)T8 to LED Shelf | /Fixture | 1 | 0 | -10 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 26.46% | 79 | 7.7386 | 0.0038347 | 7.7386 | 0.0012963 | 0.018705 | 0.018705 | 10.4966 | 1.1995 | 85.4421 | 85.4421 | 106 | 4.9788 | 0.0059604 | 4.9788 | 0.0020149 | 0.020112 | 0.020112 | 16.4345 | 1.8781 | 90.7015 | 90.7015 | 99 | 5.5748 | 0.0053232 | 5.5748 | 0.0017995 | 0.01969 | 0.01969 | 14.5708 | 1.7052 | 89.0106 | 89.0106 | 98 | 5.6656 | 0.0052378 | 5.6656 | 0.0017706 | 0.019634 | 0.019634 | 14.6823 | 1.7181 | 89.1092 | 89.1092 | 93 | 6.144 | 0.00483 | 6.144 | 0.0016328 | 0.019364 | 0.019364 | 13.8641 | 1.5516 | 88.4575 | 88.4575 | 96 | 5.852 | 0.005071 | 5.852 | 0.0017143 | 0.019523 | 0.019523 | 14.2553 | 1.6854 | 88.7149 | 88.7149 | 93 | 6.144 | 0.00483 | 6.144 | 0.0016328 | 0.019364 | 0.019364 | 14.0472 | 1.6221 | 88.5701 | 88.5701 | 99 | 5.5748 | 0.0053232 | 5.5748 | 0.0017995 | 0.01969 | 0.01969 | 15.6436 | 1.7799 | 90.0087 | 90.0087 | 106 | 4.9788 | 0.0059604 | 4.9788 | 0.0020149 | 0.020112 | 0.020112 | 17.4396 | 1.9729 | 91.6117 | 91.6117 | 110 | 4.6654 | 0.0063608 | 4.6654 | 0.0021502 | 0.020377 | 0.020377 | 18.4238 | 2.0828 | 92.486 | 92.486 | 114 | 4.3682 | 0.0067935 | 4.3682 | 0.0022965 | 0.020664 | 0.020664 | 19.4663 | 2.1448 | 93.4665 | 93.4665 | 110 | 4.6654 | 0.0063608 | 4.6654 | 0.0021502 | 0.020377 | 0.020377 | 17.5732 | 2.0398 | 91.6785 | 91.6785 | 111 | 4.5897 | 0.0064657 | 4.5897 | 0.0021857 | 0.020447 | 0.020447 | 18.1438 | 2.1211 | 92.1677 | 92.1677 | 113 | 4.4411 | 0.006682 | 4.4411 | 0.0022588 | 0.02059 | 0.02059 | 19.1822 | 2.1681 | 93.1592 | 93.1592 | 123 | 3.7435 | 0.0079271 | 3.7435 | 0.0026797 | 0.021414 | 0.021414 | 22.5079 | 2.8383 | 95.8146 | 95.8146 | 95 | 5.9476 | 0.0049895 | 5.9476 | 0.0016867 | 0.019469 | 0.019469 | 15.633 | 1.4931 | 90.2849 | 90.2849
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to FO retrofit | /Door | 1 | 38 | 28 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 27.93% | 84 | 9.5174 | 0.0050159 | 9.5174 | 0.001054 | 0.020129 | 0.020129 | 14.4926 | 1.0295 | 89.6081 | 89.6081 | 111 | 6.4426 | 0.0074099 | 6.4426 | 0.0015571 | 0.022019 | 0.022019 | 21.5662 | 1.532 | 96.1792 | 96.1792 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0013985 | 0.021423 | 0.021423 | 19.229 | 1.3988 | 93.9752 | 93.9752 | 103 | 7.2811 | 0.0065566 | 7.2811 | 0.0013778 | 0.021345 | 0.021345 | 19.3999 | 1.4112 | 94.1337 | 94.1337 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0012804 | 0.020979 | 0.020979 | 18.4614 | 1.2843 | 93.322 | 93.322 | 99 | 7.7222 | 0.006182 | 7.7222 | 0.0012991 | 0.02105 | 0.02105 | 18.3439 | 1.3481 | 93.1408 | 93.1408 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0012804 | 0.020979 | 0.020979 | 18.7052 | 1.3427 | 93.5075 | 93.5075 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0013985 | 0.021423 | 0.021423 | 20.6448 | 1.4601 | 95.3297 | 95.3297 | 109 | 6.6469 | 0.0071821 | 6.6469 | 0.0015092 | 0.02184 | 0.02184 | 22.1815 | 1.5599 | 96.7666 | 96.7666 | 115 | 6.044 | 0.0078985 | 6.044 | 0.0016598 | 0.022405 | 0.022405 | 24.1487 | 1.697 | 98.5967 | 98.5967 | 119 | 5.6586 | 0.0084365 | 5.6586 | 0.0017728 | 0.02283 | 0.02283 | 25.5172 | 1.7477 | 99.9145 | 99.9145 | 115 | 6.044 | 0.0078985 | 6.044 | 0.0016598 | 0.022405 | 0.022405 | 23.0339 | 1.662 | 97.5169 | 97.5169 | 116 | 5.9465 | 0.0080281 | 5.9465 | 0.001687 | 0.022508 | 0.022508 | 23.7797 | 1.7281 | 98.1966 | 98.1966 | 123 | 5.2856 | 0.0090318 | 5.2856 | 0.0018979 | 0.023301 | 0.023301 | 27.3686 | 1.9229 | 101.5907 | 101.5907 | 126 | 5.0138 | 0.0095215 | 5.0138 | 0.0020008 | 0.023687 | 0.023687 | 28.5368 | 2.2369 | 102.4449 | 102.4449 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0013985 | 0.021423 | 0.021423 | 22.0104 | 1.3067 | 96.8487 | 96.8487
LT, T8 to FO retrofit | /Door | 1 | 0 | -10 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 26.46% | 79 | 7.7386 | 0.0061689 | 7.7386 | 0.0012963 | 0.021039 | 0.021039 | 16.8858 | 1.1995 | 91.8313 | 91.8313 | 106 | 4.9788 | 0.0095885 | 4.9788 | 0.0020149 | 0.02374 | 0.02374 | 26.4382 | 1.8781 | 100.7051 | 100.7051 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.0017995 | 0.022931 | 0.022931 | 23.44 | 1.7052 | 97.8798 | 97.8798 | 98 | 5.6656 | 0.0084261 | 5.6656 | 0.0017706 | 0.022822 | 0.022822 | 23.6194 | 1.7181 | 98.0463 | 98.0463 | 93 | 6.144 | 0.00777 | 6.144 | 0.0016328 | 0.022304 | 0.022304 | 22.3031 | 1.5516 | 96.8965 | 96.8965 | 94 | 6.0449 | 0.0078974 | 6.0449 | 0.0016595 | 0.022405 | 0.022405 | 22.2005 | 1.6316 | 96.7139 | 96.7139 | 93 | 6.144 | 0.00777 | 6.144 | 0.0016328 | 0.022304 | 0.022304 | 22.5976 | 1.6221 | 97.1206 | 97.1206 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.0017995 | 0.022931 | 0.022931 | 25.1658 | 1.7799 | 99.5309 | 99.5309 | 104 | 5.1424 | 0.0092834 | 5.1424 | 0.0019508 | 0.023499 | 0.023499 | 27.1621 | 1.9101 | 101.397 | 101.397 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.0021502 | 0.024249 | 0.024249 | 29.6383 | 2.0828 | 103.7005 | 103.7005 | 114 | 4.3682 | 0.010929 | 4.3682 | 0.0022965 | 0.024799 | 0.024799 | 31.3154 | 2.1448 | 105.3155 | 105.3155 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.0021502 | 0.024249 | 0.024249 | 28.27 | 2.0398 | 102.3753 | 102.3753 | 111 | 4.5897 | 0.010401 | 4.5897 | 0.0021857 | 0.024382 | 0.024382 | 29.1878 | 2.1211 | 103.2117 | 103.2117 | 118 | 4.0843 | 0.011689 | 4.0843 | 0.0024562 | 0.025399 | 0.025399 | 33.5548 | 2.3575 | 107.3423 | 107.3423 | 121 | 3.8782 | 0.012309 | 3.8782 | 0.0025867 | 0.025889 | 0.025889 | 34.9506 | 2.7397 | 108.3559 | 108.3559 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.0017995 | 0.022931 | 0.022931 | 26.8305 | 1.5929 | 101.3826 | 101.3826
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to CC retrofit | /Door | 1 | 38 | 28 | 29.6755 | 34.1268 | 70.9563 | -0.0166 | -151.842 | 2.0792 | 197.5% | 84 | 9.5174 | 0.0050159 | 9.5174 | 0.0074554 | -0.019039 | -0.019039 | 14.4926 | 51.5061 | -188.8555 | -188.8555 | 111 | 6.4426 | 0.0074099 | 6.4426 | 0.011014 | -0.020204 | -0.020204 | 21.5662 | 76.6452 | -206.921 | -206.921 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | -0.019837 | -0.019837 | 19.229 | 69.984 | -202.597 | -202.597 | 103 | 7.2811 | 0.0065566 | 7.2811 | 0.0097453 | -0.019789 | -0.019789 | 19.3999 | 70.6008 | -203.0429 | -203.0429 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0090565 | -0.019563 | -0.019563 | 18.4614 | 64.2559 | -197.6366 | -197.6366 | 99 | 7.7222 | 0.006182 | 7.7222 | 0.0091886 | -0.019607 | -0.019607 | 18.3439 | 67.447 | -200.9451 | -200.9451 | 98 | 7.8349 | 0.0060931 | 7.8349 | 0.0090565 | -0.019563 | -0.019563 | 18.7052 | 67.1738 | -200.3106 | -200.3106 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | -0.019837 | -0.019837 | 20.6448 | 73.0489 | -204.2461 | -204.2461 | 109 | 6.6469 | 0.0071821 | 6.6469 | 0.010675 | -0.020093 | -0.020093 | 22.1815 | 78.0394 | -207.6999 | -207.6999 | 115 | 6.044 | 0.0078985 | 6.044 | 0.01174 | -0.020441 | -0.020441 | 24.1487 | 84.9033 | -212.5965 | -212.5965 | 119 | 5.6586 | 0.0084365 | 5.6586 | 0.01254 | -0.020703 | -0.020703 | 25.5172 | 87.4378 | -213.7626 | -213.7626 | 115 | 6.044 | 0.0078985 | 6.044 | 0.01174 | -0.020441 | -0.020441 | 23.0339 | 83.1477 | -211.9558 | -211.9558 | 116 | 5.9465 | 0.0080281 | 5.9465 | 0.011932 | -0.020504 | -0.020504 | 23.7797 | 86.4571 | -214.5194 | -214.5194 | 123 | 5.2856 | 0.0090318 | 5.2856 | 0.013424 | -0.020993 | -0.020993 | 27.3686 | 96.2024 | -220.6758 | -220.6758 | 126 | 5.0138 | 0.0095215 | 5.0138 | 0.014152 | -0.021231 | -0.021231 | 28.5368 | 111.9138 | -235.219 | -235.219 | 104 | 7.1731 | 0.0066552 | 7.1731 | 0.0098919 | -0.019837 | -0.019837 | 22.0104 | 65.3766 | -195.2082 | -195.2082
LT, T8 to CC retrofit | /Door | 1 | 0 | -10 | 29.6755 | 34.1268 | 70.9563 | -0.0166 | -151.842 | 2.0792 | 187.1% | 79 | 7.7386 | 0.0061689 | 7.7386 | 0.0091691 | -0.0196 | -0.0196 | 16.8858 | 60.0113 | -194.9675 | -194.9675 | 106 | 4.9788 | 0.0095885 | 4.9788 | 0.014252 | -0.021263 | -0.021263 | 26.4382 | 93.9599 | -219.3638 | -219.3638 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | -0.020765 | -0.020765 | 23.44 | 85.3099 | -213.7119 | -213.7119 | 98 | 5.6656 | 0.0084261 | 5.6656 | 0.012524 | -0.020698 | -0.020698 | 23.6194 | 85.9566 | -214.1792 | -214.1792 | 93 | 6.144 | 0.00777 | 6.144 | 0.011549 | -0.020379 | -0.020379 | 22.3031 | 77.6274 | -207.1663 | -207.1663 | 94 | 6.0449 | 0.0078974 | 6.0449 | 0.011738 | -0.020441 | -0.020441 | 22.2005 | 81.627 | -211.2685 | -211.2685 | 93 | 6.144 | 0.00777 | 6.144 | 0.011549 | -0.020379 | -0.020379 | 22.5976 | 81.1524 | -210.3968 | -210.3968 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | -0.020765 | -0.020765 | 25.1658 | 89.046 | -215.7222 | -215.7222 | 104 | 5.1424 | 0.0092834 | 5.1424 | 0.013798 | -0.021115 | -0.021115 | 27.1621 | 95.5623 | -220.2422 | -220.2422 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.015209 | -0.021577 | -0.021577 | 29.6383 | 104.2037 | -226.4074 | -226.4074 | 114 | 4.3682 | 0.010929 | 4.3682 | 0.016244 | -0.021915 | -0.021915 | 31.3154 | 107.3059 | -227.8326 | -227.8326 | 110 | 4.6654 | 0.010233 | 4.6654 | 0.015209 | -0.021577 | -0.021577 | 28.27 | 102.049 | -225.621 | -225.621 | 111 | 4.5897 | 0.010401 | 4.5897 | 0.01546 | -0.021659 | -0.021659 | 29.1878 | 106.1196 | -228.7738 | -228.7738 | 118 | 4.0843 | 0.011689 | 4.0843 | 0.017373 | -0.022285 | -0.022285 | 33.5548 | 117.9475 | -236.2347 | -236.2347 | 121 | 3.8782 | 0.012309 | 3.8782 | 0.018296 | -0.022587 | -0.022587 | 34.9506 | 137.0669 | -253.9583 | -253.9583 | 99 | 5.5748 | 0.0085634 | 5.5748 | 0.012728 | -0.020765 | -0.020765 | 26.8305 | 79.6936 | -204.7051 | -204.7051
Change reference after Copy/paste
42.2296
0
20.6216
25.252
0
-55.8579
-68.4002
0

## Multiplex_EEM_Savings_16CTZ
Y = a+b*x1+c*x2+d*x1^2+e*x2^2+f*x1*x2+g*x1^3+h*x2^3+i*x1*x2^2+j*x1^2*x2
[6 empty] | MT | LT
[5 empty] | a | 3.7535 | 9.8665
[5 empty] | b | -0.049642 | -0.23036
[5 empty] | c | 29.459 | 22.9056
|  | MT | LT |  | d | 0.00034207 | 0.0021889 | [7 empty] | CTZ1 | CTZ2 | CTZ3 | CTZ4 | CTZ5 | CTZ6 | CTZ7 | CTZ8 | CTZ9 | CTZ10 | CTZ11 | CTZ12 | CTZ13 | CTZ14 | CTZ15 | CTZ16
| Oversizing Factor (OS) | 13.04% | 13.04% |  | e | -11.7706 | -2.4887 | [5 empty] | Weather Factor |  | 74.26% | 74.8% | 76.05% | 77.87% | 76.26% | 78.9% | 79.73% | 79.38% | 78.58% | 77.74% | 74.95% | 76.13% | 77.88% | 77.03% | 85% | 71.04%
| Defrost Factor | 5% | 10% |  | f | -0.21294 | -0.24805 | [5 empty] | Overall Duty Cycle Factor | MT | 61.34% | 61.79% | 62.82% | 64.33% | 63% | 65.18% | 65.86% | 65.57% | 64.91% | 64.22% | 61.92% | 62.89% | 64.34% | 63.63% | 70.22% | 58.69%
| Weather Div. Factor | 85% | 85% |  | g | -1.4661e-06 | -7.575e-06 | [6 empty] | LT | 58.12% | 58.54% | 59.51% | 60.94% | 59.68% | 61.75% | 62.39% | 62.12% | 61.5% | 60.84% | 58.66% | 59.58% | 60.95% | 60.28% | 66.52% | 55.6%
| Overall Duty Cycle Factor | 70.22% | 66.52% |  | h | 6.8017 | 2.0361 | [5 empty] | EFLH | MT | 2889.3124 | 2910.4544 | 2958.8601 | 3029.8603 | 2967.2949 | 3069.8738 | 3102.0385 | 3088.4402 | 3057.3864 | 3024.6053 | 2916.2404 | 2962.0643 | 3030.2387 | 2997.0853 | 3307.2391 | 2764.0656
| Total Hours | 4710 | 4710 |  | i | -0.020187 | -0.021477 | [6 empty] | LT | 2737.2433 | 2757.2726 | 2803.1306 | 2870.394 | 2811.1215 | 2908.3015 | 2938.7733 | 2925.8907 | 2896.4713 | 2865.4156 | 2762.7541 | 2806.1662 | 2870.7525 | 2839.344 | 3133.1739 | 2618.5885
| EFLH | 3307.2391 | 3133.1739 |  | j | 0.00065794 | 0.00093831
Measure | Measure Unit | Total Unit | Box Temp | SET | Baseline Cooling Load | Compressor Capacity (Baseline Cooling Load with 15% OS) | Post Retrofit Cooling Load | Direct Power Reduction | Direct Energy Reduction | Part-Load-Ratio (Post Retrofit / Comp Cap) | Post Retrofit Duty Cycle Factor w/o Weather Factor Term | CTZ 1 - Arcata Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [69oF] |  |  | CTZ9: CTZ 2 - Santa Rosa Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] |  |  |  | CTZ 3 - Oakland Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [89oF] | [10 empty] | CTZ 4 - Sunnyvale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [88oF] | [10 empty] | CTZ 5 - Santa Maria Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 6 - Torrance Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [86oF] | [10 empty] | CTZ 7 - San Diego Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 8 - Fullerton Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [94oF] | [10 empty] | CTZ 9 - Burbank - Glendale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] | [10 empty] | CTZ 10 - Riverside Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 11 - Red Bluff Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [104oF] | [10 empty] | CTZ 12 - Sacramento Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 13 - Fresno Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [101oF] | [10 empty] | CTZ 14 - Palmdale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [103oF] | [10 empty] | CTZ 15 - Palm Springs Intl Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [113oF] | [10 empty] | CTZ 16 - Blue Canyon Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [85oF]
[12 empty] | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit
|  |  | [oF] | [oF] | [Btu/hr] | [Btu/hr] | [Btu/hr] | [kW] | [kWh] |  |  | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit]
[15 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T12 Baseline)
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (2)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 47.7388 | 54.8997 | 22.6815 | 0.05855 | 275.7705 | 0.41314 | 39.25% | 84 | 16.6547 | 0.0028664 | 16.6547 | 0.0013619 | 0.060055 | 0.060055 | 8.2819 | 1.8695 | 282.1829 | 282.1829 | 111 | 10.841 | 0.0044036 | 10.841 | 0.0020922 | 0.060861 | 0.060861 | 12.8164 | 2.8931 | 285.6938 | 285.6938 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0018917 | 0.06064 | 0.06064 | 11.5037 | 2.6593 | 284.6149 | 284.6149 | 103 | 12.1711 | 0.0039223 | 12.1711 | 0.0018636 | 0.060609 | 0.060609 | 11.6056 | 2.6827 | 284.6934 | 284.6934 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.0017252 | 0.060456 | 0.060456 | 11.0016 | 2.4322 | 284.34 | 284.34 | 101 | 12.5467 | 0.0038049 | 12.5467 | 0.0018078 | 0.060547 | 0.060547 | 11.2902 | 2.6367 | 284.424 | 284.424 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.0017252 | 0.060456 | 0.060456 | 11.1469 | 2.5426 | 284.3748 | 284.3748 | 109 | 11.15 | 0.0042815 | 11.15 | 0.0020342 | 0.060797 | 0.060797 | 13.2814 | 2.9849 | 286.0669 | 286.0669 | 111 | 10.841 | 0.0044036 | 10.841 | 0.0020922 | 0.060861 | 0.060861 | 13.6001 | 3.0392 | 286.3315 | 286.3315 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0022102 | 0.060992 | 0.060992 | 14.2224 | 3.1761 | 286.8168 | 286.8168 | 119 | 9.7287 | 0.004907 | 9.7287 | 0.0023314 | 0.061126 | 0.061126 | 14.8418 | 3.2303 | 287.382 | 287.382 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0022102 | 0.060992 | 0.060992 | 13.5658 | 3.1104 | 286.2259 | 286.2259 | 116 | 10.1252 | 0.0047149 | 10.1252 | 0.0022401 | 0.061025 | 0.061025 | 13.9658 | 3.2251 | 286.5111 | 286.5111 | 118 | 9.8584 | 0.0048424 | 9.8584 | 0.0023007 | 0.061092 | 0.061092 | 14.6737 | 3.2761 | 287.1681 | 287.1681 | 128 | 8.6415 | 0.0055244 | 8.6415 | 0.0026247 | 0.06145 | 0.06145 | 16.557 | 4.1243 | 288.2032 | 288.2032 | 100 | 12.7418 | 0.0037466 | 12.7418 | 0.0017801 | 0.060517 | 0.060517 | 12.391 | 2.3377 | 285.8238 | 285.8238
LT, (2)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 47.7388 | 54.8997 | 22.6815 | 0.05855 | 275.7705 | 0.41314 | 37.18% | 79 | 9.1087 | 0.005241 | 9.1087 | 0.0024901 | 0.061301 | 0.061301 | 14.346 | 3.2384 | 286.8781 | 286.8781 | 106 | 6.3763 | 0.007487 | 6.3763 | 0.0035572 | 0.06248 | 0.06248 | 20.6436 | 4.66 | 291.7541 | 291.7541 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.0032221 | 0.06211 | 0.06211 | 18.5634 | 4.2913 | 290.0426 | 290.0426 | 98 | 7.1373 | 0.0066886 | 7.1373 | 0.0031779 | 0.062061 | 0.062061 | 18.7491 | 4.3339 | 290.1857 | 290.1857 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0029695 | 0.061831 | 0.061831 | 17.94 | 3.9661 | 289.7444 | 289.7444 | 96 | 7.3357 | 0.0065078 | 7.3357 | 0.003092 | 0.061966 | 0.061966 | 18.2942 | 4.2724 | 289.7923 | 289.7923 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0029695 | 0.061831 | 0.061831 | 18.1769 | 4.1462 | 289.8012 | 289.8012 | 104 | 6.5612 | 0.0072759 | 6.5612 | 0.0034569 | 0.062369 | 0.062369 | 21.3822 | 4.8056 | 292.3472 | 292.3472 | 106 | 6.3763 | 0.007487 | 6.3763 | 0.0035572 | 0.06248 | 0.06248 | 21.906 | 4.8952 | 292.7813 | 292.7813 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.0037687 | 0.062713 | 0.062713 | 22.9754 | 5.1307 | 293.6151 | 293.6151 | 114 | 5.6781 | 0.0084076 | 5.6781 | 0.0039946 | 0.062963 | 0.062963 | 24.0913 | 5.2434 | 294.6183 | 294.6183 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.0037687 | 0.062713 | 0.062713 | 21.9147 | 5.0247 | 292.6606 | 292.6606 | 111 | 5.9316 | 0.0080483 | 5.9316 | 0.0038239 | 0.062774 | 0.062774 | 22.5848 | 5.2155 | 293.1398 | 293.1398 | 113 | 5.7614 | 0.008286 | 5.7614 | 0.0039368 | 0.062899 | 0.062899 | 23.7871 | 5.3108 | 294.2467 | 294.2467 | 123 | 4.9865 | 0.0095736 | 4.9865 | 0.0045486 | 0.063575 | 0.063575 | 27.1827 | 6.7711 | 296.1821 | 296.1821 | 95 | 7.4359 | 0.0064201 | 7.4359 | 0.0030503 | 0.06192 | 0.06192 | 20.1152 | 3.795 | 292.0908 | 292.0908
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 73.2194 | 84.2023 | 22.6815 | 0.04155 | 195.7005 | 0.26937 | 25.59% | 84 | 16.6547 | 0.0043963 | 16.6547 | 0.0013619 | 0.044584 | 0.044584 | 12.7024 | 1.2189 | 207.184 | 207.184 | 111 | 10.841 | 0.006754 | 10.841 | 0.0020922 | 0.046212 | 0.046212 | 19.6571 | 1.8863 | 213.4713 | 213.4713 | 104 | 11.9903 | 0.0061066 | 11.9903 | 0.0018917 | 0.045765 | 0.045765 | 17.6438 | 1.7339 | 211.6104 | 211.6104 | 103 | 12.1711 | 0.0060159 | 12.1711 | 0.0018636 | 0.045702 | 0.045702 | 17.8001 | 1.7491 | 211.7515 | 211.7515 | 98 | 13.1473 | 0.0055691 | 13.1473 | 0.0017252 | 0.045394 | 0.045394 | 16.8737 | 1.5858 | 210.9885 | 210.9885 | 101 | 12.5467 | 0.0058358 | 12.5467 | 0.0018078 | 0.045578 | 0.045578 | 17.3164 | 1.7191 | 211.2978 | 211.2978 | 98 | 13.1473 | 0.0055691 | 13.1473 | 0.0017252 | 0.045394 | 0.045394 | 17.0966 | 1.6578 | 211.1393 | 211.1393 | 109 | 11.15 | 0.0065667 | 11.15 | 0.0020342 | 0.046083 | 0.046083 | 20.3703 | 1.9462 | 214.1246 | 214.1246 | 111 | 10.841 | 0.006754 | 10.841 | 0.0020922 | 0.046212 | 0.046212 | 20.8592 | 1.9815 | 214.5782 | 214.5782 | 115 | 10.2624 | 0.0071347 | 10.2624 | 0.0022102 | 0.046475 | 0.046475 | 21.8136 | 2.0708 | 215.4433 | 215.4433 | 119 | 9.7287 | 0.0075261 | 9.7287 | 0.0023314 | 0.046745 | 0.046745 | 22.7636 | 2.1061 | 216.358 | 216.358 | 115 | 10.2624 | 0.0071347 | 10.2624 | 0.0022102 | 0.046475 | 0.046475 | 20.8065 | 2.028 | 214.4791 | 214.4791 | 116 | 10.1252 | 0 | 10.1252 | 0.0022401 | 0.03931 | 0.03931 | 0 | 2.1028 | 193.5977 | 193.5977 | 118 | 9.8584 | 0.0074271 | 9.8584 | 0.0023007 | 0.046676 | 0.046676 | 22.5058 | 2.136 | 216.0703 | 216.0703 | 128 | 8.6415 | 0.008473 | 8.6415 | 0.0026247 | 0.047398 | 0.047398 | 25.3942 | 2.689 | 218.4057 | 218.4057 | 100 | 12.7418 | 0.0057464 | 12.7418 | 0.0017801 | 0.045516 | 0.045516 | 19.0047 | 1.5242 | 213.181 | 213.181
LT, (1)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 73.2194 | 84.2023 | 22.6815 | 0.04155 | 195.7005 | 0.26937 | 24.24% | 79 | 9.1087 | 0.0080384 | 9.1087 | 0.0024901 | 0.047098 | 0.047098 | 22.0031 | 2.1114 | 215.5922 | 215.5922 | 106 | 6.3763 | 0.011483 | 6.3763 | 0.0035572 | 0.049476 | 0.049476 | 31.6621 | 3.0383 | 224.3243 | 224.3243 | 99 | 7.0393 | 0.010402 | 7.0393 | 0.0032221 | 0.048729 | 0.048729 | 28.4716 | 2.7979 | 221.3742 | 221.3742 | 98 | 7.1373 | 0.010259 | 7.1373 | 0.0031779 | 0.048631 | 0.048631 | 28.7563 | 2.8257 | 221.6312 | 221.6312 | 93 | 7.6382 | 0.0095859 | 7.6382 | 0.0029695 | 0.048166 | 0.048166 | 27.5154 | 2.5859 | 220.63 | 220.63 | 96 | 7.3357 | 0.0099813 | 7.3357 | 0.003092 | 0.048439 | 0.048439 | 28.0587 | 2.7856 | 220.9736 | 220.9736 | 93 | 7.6382 | 0.0095859 | 7.6382 | 0.0029695 | 0.048166 | 0.048166 | 27.8788 | 2.7033 | 220.876 | 220.876 | 104 | 6.5612 | 0.011159 | 6.5612 | 0.0034569 | 0.049253 | 0.049253 | 32.795 | 3.1332 | 225.3623 | 225.3623 | 106 | 6.3763 | 0.011483 | 6.3763 | 0.0035572 | 0.049476 | 0.049476 | 33.5984 | 3.1917 | 226.1072 | 226.1072 | 110 | 6.0184 | 0.012166 | 6.0184 | 0.0037687 | 0.049947 | 0.049947 | 35.2385 | 3.3452 | 227.5937 | 227.5937 | 114 | 5.6781 | 0.012895 | 5.6781 | 0.0039946 | 0.050451 | 0.050451 | 36.9499 | 3.4187 | 229.2317 | 229.2317 | 110 | 6.0184 | 0.012166 | 6.0184 | 0.0037687 | 0.049947 | 0.049947 | 33.6117 | 3.2761 | 226.0361 | 226.0361 | 111 | 5.9316 | 0.012344 | 5.9316 | 0.0038239 | 0.05007 | 0.05007 | 34.6394 | 3.4005 | 226.9394 | 226.9394 | 113 | 5.7614 | 0.012709 | 5.7614 | 0.0039368 | 0.050322 | 0.050322 | 36.4834 | 3.4626 | 228.7212 | 228.7212 | 123 | 4.9865 | 0.014683 | 4.9865 | 0.0045486 | 0.051685 | 0.051685 | 41.6914 | 4.4147 | 232.9772 | 232.9772 | 95 | 7.4359 | 0.0098468 | 7.4359 | 0.0030503 | 0.048347 | 0.048347 | 30.8517 | 2.4743 | 224.0779 | 224.0779
MT, (2)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 29.5447 | 33.9764 | 22.6815 | 0.03055 | 143.8905 | 0.66757 | 63.42% | 84 | 16.6547 | 0.001774 | 16.6547 | 0.0013619 | 0.030962 | 0.030962 | 5.1255 | 3.0208 | 145.9952 | 145.9952 | 111 | 10.841 | 0.0027253 | 10.841 | 0.0020922 | 0.031183 | 0.031183 | 7.9318 | 4.6747 | 147.1476 | 147.1476 | 104 | 11.9903 | 0.0024641 | 11.9903 | 0.0018917 | 0.031122 | 0.031122 | 7.1194 | 4.2969 | 146.713 | 146.713 | 103 | 12.1711 | 0.0024274 | 12.1711 | 0.0018636 | 0.031114 | 0.031114 | 7.1825 | 4.3347 | 146.7383 | 146.7383 | 98 | 13.1473 | 0.0022472 | 13.1473 | 0.0017252 | 0.031072 | 0.031072 | 6.8087 | 3.93 | 146.7692 | 146.7692 | 101 | 12.5467 | 0.0023548 | 12.5467 | 0.0018078 | 0.031097 | 0.031097 | 6.9873 | 4.2605 | 146.6174 | 146.6174 | 98 | 13.1473 | 0.0022472 | 13.1473 | 0.0017252 | 0.031072 | 0.031072 | 6.8986 | 4.1084 | 146.6807 | 146.6807 | 109 | 11.15 | 0.0026497 | 11.15 | 0.0020342 | 0.031166 | 0.031166 | 8.2196 | 4.8231 | 147.287 | 147.287 | 111 | 10.841 | 0.0027253 | 10.841 | 0.0020922 | 0.031183 | 0.031183 | 8.4169 | 4.9107 | 147.3966 | 147.3966 | 115 | 10.2624 | 0.0028789 | 10.2624 | 0.0022102 | 0.031219 | 0.031219 | 8.802 | 5.132 | 147.5605 | 147.5605 | 119 | 9.7287 | 0.0030369 | 9.7287 | 0.0023314 | 0.031255 | 0.031255 | 9.1853 | 5.2196 | 147.8563 | 147.8563 | 115 | 10.2624 | 0.0028789 | 10.2624 | 0.0022102 | 0.031219 | 0.031219 | 8.3956 | 5.0258 | 147.2603 | 147.2603 | 116 | 10.1252 | 0.0029179 | 10.1252 | 0.0022401 | 0.031228 | 0.031228 | 8.6431 | 5.2112 | 147.3224 | 147.3224 | 118 | 9.8584 | 0.0029969 | 9.8584 | 0.0023007 | 0.031246 | 0.031246 | 9.0813 | 5.2937 | 147.6781 | 147.6781 | 128 | 8.6415 | 0.0034189 | 8.6415 | 0.0026247 | 0.031344 | 0.031344 | 10.2468 | 6.6641 | 147.4732 | 147.4732 | 100 | 12.7418 | 0.0023187 | 12.7418 | 0.0017801 | 0.031089 | 0.031089 | 7.6686 | 3.7773 | 147.7818 | 147.7818
LT, (2)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 29.5447 | 33.9764 | 22.6815 | 0.03055 | 143.8905 | 0.66757 | 60.08% | 79 | 9.1087 | 0.0032436 | 9.1087 | 0.0024901 | 0.031303 | 0.031303 | 8.8785 | 5.2327 | 147.5363 | 147.5363 | 106 | 6.3763 | 0.0046335 | 6.3763 | 0.0035572 | 0.031626 | 0.031626 | 12.7759 | 7.5297 | 149.1367 | 149.1367 | 99 | 7.0393 | 0.0041971 | 7.0393 | 0.0032221 | 0.031525 | 0.031525 | 11.4885 | 6.9339 | 148.4451 | 148.4451 | 98 | 7.1373 | 0.0041395 | 7.1373 | 0.0031779 | 0.031512 | 0.031512 | 11.6034 | 7.0028 | 148.4912 | 148.4912 | 93 | 7.6382 | 0.003868 | 7.6382 | 0.0029695 | 0.031449 | 0.031449 | 11.1027 | 6.4084 | 148.5848 | 148.5848 | 96 | 7.3357 | 0.0040275 | 7.3357 | 0.003092 | 0.031486 | 0.031486 | 11.3219 | 6.9034 | 148.309 | 148.309 | 93 | 7.6382 | 0.003868 | 7.6382 | 0.0029695 | 0.031449 | 0.031449 | 11.2493 | 6.6994 | 148.4404 | 148.4404 | 104 | 6.5612 | 0.0045029 | 6.5612 | 0.0034569 | 0.031596 | 0.031596 | 13.2331 | 7.7649 | 149.3586 | 149.3586 | 106 | 6.3763 | 0.0046335 | 6.3763 | 0.0035572 | 0.031626 | 0.031626 | 13.5572 | 7.9098 | 149.5379 | 149.5379 | 110 | 6.0184 | 0.0049091 | 6.0184 | 0.0037687 | 0.03169 | 0.03169 | 14.219 | 8.2904 | 149.8192 | 149.8192 | 114 | 5.6781 | 0.0052033 | 5.6781 | 0.0039946 | 0.031759 | 0.031759 | 14.9096 | 8.4724 | 150.3277 | 150.3277 | 110 | 6.0184 | 0.0049091 | 6.0184 | 0.0037687 | 0.03169 | 0.03169 | 13.5626 | 8.1189 | 149.3342 | 149.3342 | 111 | 5.9316 | 0.0049809 | 5.9316 | 0.0038239 | 0.031707 | 0.031707 | 13.9773 | 8.4273 | 149.4405 | 149.4405 | 113 | 5.7614 | 0.005128 | 5.7614 | 0.0039368 | 0.031741 | 0.031741 | 14.7214 | 8.5813 | 150.0305 | 150.0305 | 123 | 4.9865 | 0.0059249 | 4.9865 | 0.0045486 | 0.031926 | 0.031926 | 16.8229 | 10.9409 | 149.7725 | 149.7725 | 95 | 7.4359 | 0.0039733 | 7.4359 | 0.0030503 | 0.031473 | 0.031473 | 12.4489 | 6.132 | 150.2075 | 150.2075
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 29.6755 | 34.1268 | 22.6815 | 0.00755 | 35.5605 | 0.66462 | 63.14% | 84 | 16.6547 | 0.0017818 | 16.6547 | 0.0013619 | 0.0079699 | 0.0079699 | 5.1482 | 3.0075 | 37.7012 | 37.7012 | 111 | 10.841 | 0.0027373 | 10.841 | 0.0020922 | 0.0081951 | 0.0081951 | 7.9669 | 4.6541 | 38.8733 | 38.8733 | 104 | 11.9903 | 0.002475 | 11.9903 | 0.0018917 | 0.0081333 | 0.0081333 | 7.151 | 4.278 | 38.4335 | 38.4335 | 103 | 12.1711 | 0.0024382 | 12.1711 | 0.0018636 | 0.0081246 | 0.0081246 | 7.2143 | 4.3156 | 38.4592 | 38.4592 | 98 | 13.1473 | 0.0022571 | 13.1473 | 0.0017252 | 0.008082 | 0.008082 | 6.8388 | 3.9126 | 38.4867 | 38.4867 | 101 | 12.5467 | 0.0023652 | 12.5467 | 0.0018078 | 0.0081074 | 0.0081074 | 7.0183 | 4.2417 | 38.3371 | 38.3371 | 98 | 13.1473 | 0.0022571 | 13.1473 | 0.0017252 | 0.008082 | 0.008082 | 6.9292 | 4.0903 | 38.3994 | 38.3994 | 109 | 11.15 | 0.0026615 | 11.15 | 0.0020342 | 0.0081773 | 0.0081773 | 8.256 | 4.8018 | 39.0146 | 39.0146 | 111 | 10.841 | 0.0027373 | 10.841 | 0.0020922 | 0.0081951 | 0.0081951 | 8.4541 | 4.8891 | 39.1256 | 39.1256 | 115 | 10.2624 | 0.0028917 | 10.2624 | 0.0022102 | 0.0082315 | 0.0082315 | 8.8409 | 5.1093 | 39.2921 | 39.2921 | 119 | 9.7287 | 0.0030503 | 9.7287 | 0.0023314 | 0.0082689 | 0.0082689 | 9.226 | 5.1965 | 39.5899 | 39.5899 | 115 | 10.2624 | 0.0028917 | 10.2624 | 0.0022102 | 0.0082315 | 0.0082315 | 8.4328 | 5.0037 | 38.9896 | 38.9896 | 116 | 10.1252 | 0.0029309 | 10.1252 | 0.0022401 | 0.0082408 | 0.0082408 | 8.6814 | 5.1882 | 39.0537 | 39.0537 | 118 | 9.8584 | 0.0030102 | 9.8584 | 0.0023007 | 0.0082594 | 0.0082594 | 9.1215 | 5.2703 | 39.4117 | 39.4117 | 128 | 8.6415 | 0.0034341 | 8.6415 | 0.0026247 | 0.0083593 | 0.0083593 | 10.2922 | 6.6347 | 39.218 | 39.218 | 100 | 12.7418 | 0.002329 | 12.7418 | 0.0017801 | 0.0080989 | 0.0080989 | 7.7025 | 3.7607 | 39.5024 | 39.5024
LT, (1)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 29.6755 | 34.1268 | 22.6815 | 0.00755 | 35.5605 | 0.66462 | 59.82% | 79 | 9.1087 | 0.0032579 | 9.1087 | 0.0024901 | 0.0083178 | 0.0083178 | 8.9178 | 5.2096 | 39.2687 | 39.2687 | 106 | 6.3763 | 0.0046541 | 6.3763 | 0.0035572 | 0.0086469 | 0.0086469 | 12.8325 | 7.4965 | 40.8965 | 40.8965 | 99 | 7.0393 | 0.0042157 | 7.0393 | 0.0032221 | 0.0085436 | 0.0085436 | 11.5394 | 6.9034 | 40.1965 | 40.1965 | 98 | 7.1373 | 0.0041578 | 7.1373 | 0.0031779 | 0.0085299 | 0.0085299 | 11.6548 | 6.9719 | 40.2434 | 40.2434 | 93 | 7.6382 | 0.0038851 | 7.6382 | 0.0029695 | 0.0084657 | 0.0084657 | 11.1519 | 6.3802 | 40.3322 | 40.3322 | 96 | 7.3357 | 0.0040454 | 7.3357 | 0.003092 | 0.0085034 | 0.0085034 | 11.3721 | 6.873 | 40.0596 | 40.0596 | 93 | 7.6382 | 0.0038851 | 7.6382 | 0.0029695 | 0.0084657 | 0.0084657 | 11.2991 | 6.6699 | 40.1897 | 40.1897 | 104 | 6.5612 | 0.0045229 | 6.5612 | 0.0034569 | 0.008616 | 0.008616 | 13.2917 | 7.7307 | 41.1215 | 41.1215 | 106 | 6.3763 | 0.0046541 | 6.3763 | 0.0035572 | 0.0086469 | 0.0086469 | 13.6173 | 7.875 | 41.3028 | 41.3028 | 110 | 6.0184 | 0.0049308 | 6.0184 | 0.0037687 | 0.0087121 | 0.0087121 | 14.282 | 8.2538 | 41.5887 | 41.5887 | 114 | 5.6781 | 0.0052263 | 5.6781 | 0.0039946 | 0.0087818 | 0.0087818 | 14.9756 | 8.435 | 42.1011 | 42.1011 | 110 | 6.0184 | 0.0049308 | 6.0184 | 0.0037687 | 0.0087121 | 0.0087121 | 13.6227 | 8.0831 | 41.1 | 41.1 | 111 | 5.9316 | 0.005003 | 5.9316 | 0.0038239 | 0.0087291 | 0.0087291 | 14.0392 | 8.3902 | 41.2095 | 41.2095 | 113 | 5.7614 | 0.0051508 | 5.7614 | 0.0039368 | 0.0087639 | 0.0087639 | 14.7866 | 8.5435 | 41.8035 | 41.8035 | 123 | 4.9865 | 0.0059512 | 4.9865 | 0.0045486 | 0.0089526 | 0.0089526 | 16.8974 | 10.8926 | 41.5652 | 41.5652 | 95 | 7.4359 | 0.0039909 | 7.4359 | 0.0030503 | 0.0084906 | 0.0084906 | 12.5041 | 6.1049 | 41.9596 | 41.9596
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| /Fixture | 1 | 38 | 28 | 47.7388 | 54.8997 | 70.9563 | 0.0344 | 88.368 | 1.2925 | 122.8% | 84 | 16.6547 | 0.0028664 | 16.6547 | 0.0042604 | 0.033006 | 0.033006 | 8.2819 | 18.2965 | 78.3534 | 78.3534 | 111 | 10.841 | 0.0044036 | 10.841 | 0.0065452 | 0.032258 | 0.032258 | 12.8164 | 28.3141 | 72.8703 | 72.8703 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | 0.032464 | 0.032464 | 11.5037 | 26.0259 | 73.8458 | 73.8458 | 103 | 12.1711 | 0.0039223 | 12.1711 | 0.0058299 | 0.032492 | 0.032492 | 11.6056 | 26.2545 | 73.7191 | 73.7191 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.005397 | 0.032634 | 0.032634 | 11.0016 | 23.8031 | 75.5666 | 75.5666 | 99 | 12.942 | 0.0036887 | 12.942 | 0.0054827 | 0.032606 | 0.032606 | 10.9454 | 25.0167 | 74.2967 | 74.2967 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.005397 | 0.032634 | 0.032634 | 11.1469 | 24.8839 | 74.631 | 74.631 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | 0.032464 | 0.032464 | 12.3507 | 27.1657 | 73.553 | 73.553 | 109 | 11.15 | 0.0042815 | 11.15 | 0.0063638 | 0.032318 | 0.032318 | 13.2231 | 28.919 | 72.6721 | 72.6721 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0069142 | 0.032138 | 0.032138 | 14.2224 | 31.0834 | 71.507 | 71.507 | 119 | 9.7287 | 0.004907 | 9.7287 | 0.0072935 | 0.032014 | 0.032014 | 14.8418 | 31.614 | 71.5958 | 71.5958 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0069142 | 0.032138 | 0.032138 | 13.5658 | 30.4407 | 71.4931 | 71.4931 | 116 | 10.1252 | 0.0047149 | 10.1252 | 0.0070079 | 0.032107 | 0.032107 | 13.9658 | 31.5635 | 70.7703 | 70.7703 | 123 | 9.2301 | 0.0051721 | 9.2301 | 0.0076875 | 0.031885 | 0.031885 | 15.6727 | 34.2455 | 69.7952 | 69.7952 | 126 | 8.8734 | 0.00538 | 8.8734 | 0.0079965 | 0.031783 | 0.031783 | 16.1244 | 39.3085 | 65.1838 | 65.1838 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | 0.032464 | 0.032464 | 13.1677 | 24.3125 | 77.2232 | 77.2232
| /Fixture | 1 | 0 | -10 | 47.7388 | 54.8997 | 70.9563 | 0.0344 | 88.368 | 1.2925 | 116.3% | 79 | 9.1087 | 0.005241 | 9.1087 | 0.00779 | 0.031851 | 0.031851 | 14.346 | 31.6934 | 71.0206 | 71.0206 | 106 | 6.3763 | 0.007487 | 6.3763 | 0.011128 | 0.030759 | 0.030759 | 20.6436 | 45.6061 | 63.4055 | 63.4055 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | 0.031102 | 0.031102 | 18.5634 | 41.9977 | 64.9337 | 64.9337 | 98 | 7.1373 | 0.0066886 | 7.1373 | 0.0099416 | 0.031147 | 0.031147 | 18.7491 | 42.4146 | 64.7025 | 64.7025 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0092896 | 0.03136 | 0.03136 | 17.94 | 38.8148 | 67.4932 | 67.4932 | 94 | 7.5367 | 0.0063342 | 7.5367 | 0.0094147 | 0.031319 | 0.031319 | 17.8061 | 40.6974 | 65.4767 | 65.4767 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0092896 | 0.03136 | 0.03136 | 18.1769 | 40.5774 | 65.9675 | 65.9675 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | 0.031102 | 0.031102 | 19.9301 | 43.8369 | 64.4612 | 64.4612 | 104 | 6.5612 | 0.0072759 | 6.5612 | 0.010814 | 0.030861 | 0.030861 | 21.2885 | 46.558 | 63.0985 | 63.0985 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.01179 | 0.030542 | 0.030542 | 22.9754 | 50.2133 | 61.1301 | 61.1301 | 114 | 5.6781 | 0.0084076 | 5.6781 | 0.012497 | 0.030311 | 0.030311 | 24.0913 | 51.3159 | 61.1434 | 61.1434 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.01179 | 0.030542 | 0.030542 | 21.9147 | 49.175 | 61.1077 | 61.1077 | 111 | 5.9316 | 0.0080483 | 5.9316 | 0.011962 | 0.030486 | 0.030486 | 22.5848 | 51.043 | 59.9098 | 59.9098 | 118 | 5.3573 | 0.0089111 | 5.3573 | 0.013245 | 0.030066 | 0.030066 | 25.5815 | 55.8966 | 58.0528 | 58.0528 | 121 | 5.1306 | 0.0093048 | 5.1306 | 0.01383 | 0.029875 | 0.029875 | 26.4195 | 64.4064 | 50.3811 | 50.3811 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | 0.031102 | 0.031102 | 21.2485 | 39.2328 | 70.3837 | 70.3837
| /Fixture | [13 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
/Fixture
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Shelf | /Fixture | 1 | 38 | 28 | 73.2194 | 84.2023 | 10.0317 | 0.050167 | 236.285 | 0.11914 | 11.32% | 84 | 16.6547 | 0.0043963 | 16.6547 | 0.00060234 | 0.053961 | 0.053961 | 12.7024 | 0.23844 | 248.7489 | 248.7489 | 111 | 10.841 | 0.006754 | 10.841 | 0.00092535 | 0.055995 | 0.055995 | 19.6571 | 0.36899 | 255.5731 | 255.5731 | 104 | 11.9903 | 0.0061066 | 11.9903 | 0.00083666 | 0.055437 | 0.055437 | 17.6438 | 0.33917 | 253.5896 | 253.5896 | 103 | 12.1711 | 0.0060159 | 12.1711 | 0.00082423 | 0.055358 | 0.055358 | 17.8001 | 0.34215 | 253.7429 | 253.7429 | 98 | 13.1473 | 0.0055691 | 13.1473 | 0.00076302 | 0.054973 | 0.054973 | 16.8737 | 0.3102 | 252.8485 | 252.8485 | 101 | 12.5467 | 0.0058358 | 12.5467 | 0.00079955 | 0.055203 | 0.055203 | 17.3164 | 0.33629 | 253.2651 | 253.2651 | 98 | 13.1473 | 0.0055691 | 13.1473 | 0.00076302 | 0.054973 | 0.054973 | 17.0966 | 0.32429 | 253.0573 | 253.0573 | 109 | 11.15 | 0.0065667 | 11.15 | 0.0008997 | 0.055834 | 0.055834 | 20.3703 | 0.3807 | 256.2745 | 256.2745 | 111 | 10.841 | 0.006754 | 10.841 | 0.00092535 | 0.055995 | 0.055995 | 20.8592 | 0.38762 | 256.7566 | 256.7566 | 115 | 10.2624 | 0.0071347 | 10.2624 | 0.00097752 | 0.056324 | 0.056324 | 21.8136 | 0.40508 | 257.6935 | 257.6935 | 119 | 9.7287 | 0.0075261 | 9.7287 | 0.0010312 | 0.056662 | 0.056662 | 22.7636 | 0.412 | 258.6366 | 258.6366 | 115 | 10.2624 | 0.0071347 | 10.2624 | 0.00097752 | 0.056324 | 0.056324 | 20.8065 | 0.39671 | 256.6948 | 256.6948 | 116 | 10.1252 | 0.0072314 | 10.1252 | 0.00099077 | 0.056407 | 0.056407 | 21.42 | 0.41134 | 257.2936 | 257.2936 | 118 | 9.8584 | 0.0074271 | 9.8584 | 0.0010176 | 0.056576 | 0.056576 | 22.5058 | 0.41785 | 258.373 | 258.373 | 128 | 8.6415 | 0.008473 | 8.6415 | 0.0011609 | 0.057479 | 0.057479 | 25.3942 | 0.52602 | 261.1532 | 261.1532 | 100 | 12.7418 | 0.0057464 | 12.7418 | 0.00078731 | 0.055126 | 0.055126 | 19.0047 | 0.29816 | 254.9915 | 254.9915
LT, (1)T12 to LED Shelf | /Fixture | 1 | 0 | -10 | 73.2194 | 84.2023 | 10.0317 | 0.050167 | 236.285 | 0.11914 | 10.72% | 79 | 9.1087 | 0.0080384 | 9.1087 | 0.0011013 | 0.057104 | 0.057104 | 22.0031 | 0.41303 | 257.8751 | 257.8751 | 106 | 6.3763 | 0.011483 | 6.3763 | 0.0015733 | 0.060076 | 0.060076 | 31.6621 | 0.59435 | 267.3527 | 267.3527 | 99 | 7.0393 | 0.010402 | 7.0393 | 0.0014251 | 0.059143 | 0.059143 | 28.4716 | 0.54732 | 264.2093 | 264.2093 | 98 | 7.1373 | 0.010259 | 7.1373 | 0.0014055 | 0.05902 | 0.05902 | 28.7563 | 0.55275 | 264.4886 | 264.4886 | 93 | 7.6382 | 0.0095859 | 7.6382 | 0.0013134 | 0.058439 | 0.058439 | 27.5154 | 0.50584 | 263.2945 | 263.2945 | 96 | 7.3357 | 0.0099813 | 7.3357 | 0.0013675 | 0.05878 | 0.05878 | 28.0587 | 0.54491 | 263.7988 | 263.7988 | 93 | 7.6382 | 0.0095859 | 7.6382 | 0.0013134 | 0.058439 | 0.058439 | 27.8788 | 0.52881 | 263.6349 | 263.6349 | 104 | 6.5612 | 0.011159 | 6.5612 | 0.0015289 | 0.059797 | 0.059797 | 32.795 | 0.61291 | 268.4671 | 268.4671 | 106 | 6.3763 | 0.011483 | 6.3763 | 0.0015733 | 0.060076 | 0.060076 | 33.5984 | 0.62435 | 269.259 | 269.259 | 110 | 6.0184 | 0.012166 | 6.0184 | 0.0016669 | 0.060666 | 0.060666 | 35.2385 | 0.65439 | 270.8691 | 270.8691 | 114 | 5.6781 | 0.012895 | 5.6781 | 0.0017668 | 0.061295 | 0.061295 | 36.9499 | 0.66876 | 272.5662 | 272.5662 | 110 | 6.0184 | 0.012166 | 6.0184 | 0.0016669 | 0.060666 | 0.060666 | 33.6117 | 0.64086 | 269.2558 | 269.2558 | 111 | 5.9316 | 0.012344 | 5.9316 | 0.0016912 | 0.060819 | 0.060819 | 34.6394 | 0.6652 | 270.2592 | 270.2592 | 113 | 5.7614 | 0.012709 | 5.7614 | 0.0017412 | 0.061134 | 0.061134 | 36.4834 | 0.67736 | 272.091 | 272.091 | 123 | 4.9865 | 0.014683 | 4.9865 | 0.0020118 | 0.062838 | 0.062838 | 41.6914 | 0.8636 | 277.1128 | 277.1128 | 95 | 7.4359 | 0.0098468 | 7.4359 | 0.0013491 | 0.058664 | 0.058664 | 30.8517 | 0.48402 | 266.6527 | 266.6527
MT, (1)T8 to LED Shelf | /Fixture | 1 | 38 | 28 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 27.93% | 84 | 16.6547 | 0.0017818 | 16.6547 | 0.00060234 | 0.017346 | 0.017346 | 5.1482 | 0.58832 | 80.7049 | 80.7049 | 111 | 10.841 | 0.0027373 | 10.841 | 0.00092535 | 0.017979 | 0.017979 | 7.9669 | 0.91043 | 83.2015 | 83.2015 | 104 | 11.9903 | 0.002475 | 11.9903 | 0.00083666 | 0.017805 | 0.017805 | 7.151 | 0.83685 | 82.4591 | 82.4591 | 103 | 12.1711 | 0.0024382 | 12.1711 | 0.00082423 | 0.017781 | 0.017781 | 7.2143 | 0.8442 | 82.5151 | 82.5151 | 98 | 13.1473 | 0.0022571 | 13.1473 | 0.00076302 | 0.017661 | 0.017661 | 6.8388 | 0.76538 | 82.2185 | 82.2185 | 101 | 12.5467 | 0.0023652 | 12.5467 | 0.00079955 | 0.017732 | 0.017732 | 7.0183 | 0.82975 | 82.3335 | 82.3335 | 98 | 13.1473 | 0.0022571 | 13.1473 | 0.00076302 | 0.017661 | 0.017661 | 6.9292 | 0.80013 | 82.274 | 82.274 | 109 | 11.15 | 0.0026615 | 11.15 | 0.0008997 | 0.017928 | 0.017928 | 8.256 | 0.93932 | 83.4617 | 83.4617 | 111 | 10.841 | 0.0027373 | 10.841 | 0.00092535 | 0.017979 | 0.017979 | 8.4541 | 0.95639 | 83.6427 | 83.6427 | 115 | 10.2624 | 0.0028917 | 10.2624 | 0.00097752 | 0.018081 | 0.018081 | 8.8409 | 0.99948 | 83.9865 | 83.9865 | 119 | 9.7287 | 0.0030503 | 9.7287 | 0.0010312 | 0.018186 | 0.018186 | 9.226 | 1.0165 | 84.3545 | 84.3545 | 115 | 10.2624 | 0.0028917 | 10.2624 | 0.00097752 | 0.018081 | 0.018081 | 8.4328 | 0.97881 | 83.599 | 83.599 | 116 | 10.1252 | 0.0029309 | 10.1252 | 0.00099077 | 0.018107 | 0.018107 | 8.6814 | 1.0149 | 83.8115 | 83.8115 | 118 | 9.8584 | 0.0030102 | 9.8584 | 0.0010176 | 0.018159 | 0.018159 | 9.1215 | 1.031 | 84.2355 | 84.2355 | 128 | 8.6415 | 0.0034341 | 8.6415 | 0.0011609 | 0.01844 | 0.01844 | 10.2922 | 1.2979 | 85.1393 | 85.1393 | 100 | 12.7418 | 0.002329 | 12.7418 | 0.00078731 | 0.017708 | 0.017708 | 7.7025 | 0.73565 | 83.1119 | 83.1119
LT, (1)T8 to LED Shelf | /Fixture | 1 | 0 | -10 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 26.46% | 79 | 9.1087 | 0.0032579 | 9.1087 | 0.0011013 | 0.018323 | 0.018323 | 8.9178 | 1.0191 | 84.0437 | 84.0437 | 106 | 6.3763 | 0.0046541 | 6.3763 | 0.0015733 | 0.019247 | 0.019247 | 12.8325 | 1.4664 | 87.5111 | 87.5111 | 99 | 7.0393 | 0.0042157 | 7.0393 | 0.0014251 | 0.018957 | 0.018957 | 11.5394 | 1.3504 | 86.334 | 86.334 | 98 | 7.1373 | 0.0041578 | 7.1373 | 0.0014055 | 0.018919 | 0.018919 | 11.6548 | 1.3638 | 86.436 | 86.436 | 93 | 7.6382 | 0.0038851 | 7.6382 | 0.0013134 | 0.018738 | 0.018738 | 11.1519 | 1.2481 | 86.0488 | 86.0488 | 96 | 7.3357 | 0.0040454 | 7.3357 | 0.0013675 | 0.018845 | 0.018845 | 11.3721 | 1.3445 | 86.1726 | 86.1726 | 93 | 7.6382 | 0.0038851 | 7.6382 | 0.0013134 | 0.018738 | 0.018738 | 11.2991 | 1.3048 | 86.1394 | 86.1394 | 104 | 6.5612 | 0.0045229 | 6.5612 | 0.0015289 | 0.019161 | 0.019161 | 13.2917 | 1.5123 | 87.9244 | 87.9244 | 106 | 6.3763 | 0.0046541 | 6.3763 | 0.0015733 | 0.019247 | 0.019247 | 13.6173 | 1.5405 | 88.2218 | 88.2218 | 110 | 6.0184 | 0.0049308 | 6.0184 | 0.0016669 | 0.019431 | 0.019431 | 14.282 | 1.6146 | 88.8124 | 88.8124 | 114 | 5.6781 | 0.0052263 | 5.6781 | 0.0017668 | 0.019626 | 0.019626 | 14.9756 | 1.65 | 89.4706 | 89.4706 | 110 | 6.0184 | 0.0049308 | 6.0184 | 0.0016669 | 0.019431 | 0.019431 | 13.6227 | 1.5812 | 88.1865 | 88.1865 | 111 | 5.9316 | 0.005003 | 5.9316 | 0.0016912 | 0.019478 | 0.019478 | 14.0392 | 1.6413 | 88.5429 | 88.5429 | 113 | 5.7614 | 0.0051508 | 5.7614 | 0.0017412 | 0.019576 | 0.019576 | 14.7866 | 1.6713 | 89.2603 | 89.2603 | 123 | 4.9865 | 0.0059512 | 4.9865 | 0.0020118 | 0.020106 | 0.020106 | 16.8974 | 2.1308 | 90.9116 | 90.9116 | 95 | 7.4359 | 0.0039909 | 7.4359 | 0.0013491 | 0.018808 | 0.018808 | 12.5041 | 1.1942 | 87.4548 | 87.4548
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to FO retrofit | /Door | 1 | 38 | 28 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 27.93% | 84 | 16.6547 | 0.0028664 | 16.6547 | 0.00060234 | 0.018431 | 0.018431 | 8.2819 | 0.58832 | 83.8386 | 83.8386 | 111 | 10.841 | 0.0044036 | 10.841 | 0.00092535 | 0.019645 | 0.019645 | 12.8164 | 0.91043 | 88.0509 | 88.0509 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.00083666 | 0.019311 | 0.019311 | 11.5037 | 0.83685 | 86.8119 | 86.8119 | 103 | 12.1711 | 0.0039223 | 12.1711 | 0.00082423 | 0.019265 | 0.019265 | 11.6056 | 0.8442 | 86.9064 | 86.9064 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.00076302 | 0.019035 | 0.019035 | 11.0016 | 0.76538 | 86.3812 | 86.3812 | 99 | 12.942 | 0.0036887 | 12.942 | 0.00077513 | 0.01908 | 0.01908 | 10.9454 | 0.8044 | 86.286 | 86.286 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.00076302 | 0.019035 | 0.019035 | 11.1469 | 0.80013 | 86.4918 | 86.4918 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.00083666 | 0.019311 | 0.019311 | 12.3507 | 0.8735 | 87.6222 | 87.6222 | 109 | 11.15 | 0.0042815 | 11.15 | 0.0008997 | 0.019548 | 0.019548 | 13.2231 | 0.92988 | 88.4383 | 88.4383 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.00097752 | 0.019841 | 0.019841 | 14.2224 | 0.99948 | 89.3679 | 89.3679 | 119 | 9.7287 | 0.004907 | 9.7287 | 0.0010312 | 0.020043 | 0.020043 | 14.8418 | 1.0165 | 89.9703 | 89.9703 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.00097752 | 0.019841 | 0.019841 | 13.5658 | 0.97881 | 88.732 | 88.732 | 116 | 10.1252 | 0.0047149 | 10.1252 | 0.00099077 | 0.019891 | 0.019891 | 13.9658 | 1.0149 | 89.0958 | 89.0958 | 123 | 9.2301 | 0.0051721 | 9.2301 | 0.0010869 | 0.020252 | 0.020252 | 15.6727 | 1.1012 | 90.7166 | 90.7166 | 126 | 8.8734 | 0.00538 | 8.8734 | 0.0011305 | 0.020416 | 0.020416 | 16.1244 | 1.264 | 91.0054 | 91.0054 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.00083666 | 0.019311 | 0.019311 | 13.1677 | 0.78176 | 88.5309 | 88.5309
LT, T8 to FO retrofit | /Door | 1 | 0 | -10 | 29.6755 | 34.1268 | 10.0317 | 0.016167 | 76.145 | 0.29395 | 26.46% | 79 | 9.1087 | 0.005241 | 9.1087 | 0.0011013 | 0.020306 | 0.020306 | 14.346 | 1.0191 | 89.4719 | 89.4719 | 106 | 6.3763 | 0.007487 | 6.3763 | 0.0015733 | 0.02208 | 0.02208 | 20.6436 | 1.4664 | 95.3222 | 95.3222 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.0014251 | 0.021523 | 0.021523 | 18.5634 | 1.3504 | 93.358 | 93.358 | 98 | 7.1373 | 0.0066886 | 7.1373 | 0.0014055 | 0.02145 | 0.02145 | 18.7491 | 1.3638 | 93.5302 | 93.5302 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0013134 | 0.021103 | 0.021103 | 17.94 | 1.2481 | 92.8369 | 92.8369 | 94 | 7.5367 | 0.0063342 | 7.5367 | 0.001331 | 0.02117 | 0.02117 | 17.8061 | 1.3086 | 92.6425 | 92.6425 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0013134 | 0.021103 | 0.021103 | 18.1769 | 1.3048 | 93.0171 | 93.0171 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.0014251 | 0.021523 | 0.021523 | 19.9301 | 1.4096 | 94.6656 | 94.6656 | 104 | 6.5612 | 0.0072759 | 6.5612 | 0.0015289 | 0.021914 | 0.021914 | 21.2885 | 1.4971 | 95.9364 | 95.9364 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.0016669 | 0.022432 | 0.022432 | 22.9754 | 1.6146 | 97.5058 | 97.5058 | 114 | 5.6781 | 0.0084076 | 5.6781 | 0.0017668 | 0.022808 | 0.022808 | 24.0913 | 1.65 | 98.5862 | 98.5862 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.0016669 | 0.022432 | 0.022432 | 21.9147 | 1.5812 | 96.4785 | 96.4785 | 111 | 5.9316 | 0.0080483 | 5.9316 | 0.0016912 | 0.022524 | 0.022524 | 22.5848 | 1.6413 | 97.0885 | 97.0885 | 118 | 5.3573 | 0.0089111 | 5.3573 | 0.0018726 | 0.023205 | 0.023205 | 25.5815 | 1.7973 | 99.9291 | 99.9291 | 121 | 5.1306 | 0.0093048 | 5.1306 | 0.0019553 | 0.023516 | 0.023516 | 26.4195 | 2.071 | 100.4935 | 100.4935 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.0014251 | 0.021523 | 0.021523 | 21.2485 | 1.2615 | 96.132 | 96.132
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to CC retrofit | /Door | 1 | 38 | 28 | 29.6755 | 34.1268 | 70.9563 | -0.0166 | -151.842 | 2.0792 | 197.5% | 84 | 16.6547 | 0.0028664 | 16.6547 | 0.0042604 | -0.017994 | -0.017994 | 8.2819 | 29.4335 | -172.9936 | -172.9936 | 111 | 10.841 | 0.0044036 | 10.841 | 0.0065452 | -0.018742 | -0.018742 | 12.8164 | 45.5488 | -184.5744 | -184.5744 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | -0.018536 | -0.018536 | 11.5037 | 41.8677 | -182.206 | -182.206 | 103 | 12.1711 | 0.0039223 | 12.1711 | 0.0058299 | -0.018508 | -0.018508 | 11.6056 | 42.2355 | -182.4719 | -182.4719 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.005397 | -0.018366 | -0.018366 | 11.0016 | 38.2919 | -179.1322 | -179.1322 | 99 | 12.942 | 0.0036887 | 12.942 | 0.0054827 | -0.018394 | -0.018394 | 10.9454 | 40.2443 | -181.1409 | -181.1409 | 98 | 13.1473 | 0.0036311 | 13.1473 | 0.005397 | -0.018366 | -0.018366 | 11.1469 | 40.0307 | -180.7258 | -180.7258 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | -0.018536 | -0.018536 | 12.3507 | 43.7013 | -183.1926 | -183.1926 | 109 | 11.15 | 0.0042815 | 11.15 | 0.0063638 | -0.018682 | -0.018682 | 13.2231 | 46.5219 | -185.1407 | -185.1407 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0069142 | -0.018862 | -0.018862 | 14.2224 | 50.0038 | -187.6234 | -187.6234 | 119 | 9.7287 | 0.004907 | 9.7287 | 0.0072935 | -0.018986 | -0.018986 | 14.8418 | 50.8573 | -187.8575 | -187.8575 | 115 | 10.2624 | 0.0046518 | 10.2624 | 0.0069142 | -0.018862 | -0.018862 | 13.5658 | 48.9698 | -187.246 | -187.246 | 116 | 10.1252 | 0.0047149 | 10.1252 | 0.0070079 | -0.018893 | -0.018893 | 13.9658 | 50.776 | -188.6523 | -188.6523 | 123 | 9.2301 | 0.0051721 | 9.2301 | 0.0076875 | -0.019115 | -0.019115 | 15.6727 | 55.0906 | -191.2599 | -191.2599 | 126 | 8.8734 | 0.00538 | 8.8734 | 0.0079965 | -0.019217 | -0.019217 | 16.1244 | 63.2355 | -198.9531 | -198.9531 | 104 | 11.9903 | 0.0039815 | 11.9903 | 0.0059178 | -0.018536 | -0.018536 | 13.1677 | 39.1114 | -177.7857 | -177.7857
LT, T8 to CC retrofit | /Door | 1 | 0 | -10 | 29.6755 | 34.1268 | 70.9563 | -0.0166 | -151.842 | 2.0792 | 187.1% | 79 | 9.1087 | 0.005241 | 9.1087 | 0.00779 | -0.019149 | -0.019149 | 14.346 | 50.985 | -188.481 | -188.481 | 106 | 6.3763 | 0.007487 | 6.3763 | 0.011128 | -0.020241 | -0.020241 | 20.6436 | 73.3664 | -204.5648 | -204.5648 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | -0.019898 | -0.019898 | 18.5634 | 67.5615 | -200.8401 | -200.8401 | 98 | 7.1373 | 0.0066886 | 7.1373 | 0.0099416 | -0.019853 | -0.019853 | 18.7491 | 68.2322 | -201.3251 | -201.3251 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0092896 | -0.01964 | -0.01964 | 17.94 | 62.4412 | -196.3432 | -196.3432 | 94 | 7.5367 | 0.0063342 | 7.5367 | 0.0094147 | -0.019681 | -0.019681 | 17.8061 | 65.4697 | -199.5056 | -199.5056 | 93 | 7.6382 | 0.00625 | 7.6382 | 0.0092896 | -0.01964 | -0.01964 | 18.1769 | 65.2766 | -198.9417 | -198.9417 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | -0.019898 | -0.019898 | 19.9301 | 70.5203 | -202.4321 | -202.4321 | 104 | 6.5612 | 0.0072759 | 6.5612 | 0.010814 | -0.020139 | -0.020139 | 21.2885 | 74.8976 | -205.4511 | -205.4511 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.01179 | -0.020458 | -0.020458 | 22.9754 | 80.778 | -209.6446 | -209.6446 | 114 | 5.6781 | 0.0084076 | 5.6781 | 0.012497 | -0.020689 | -0.020689 | 24.0913 | 82.5516 | -210.3024 | -210.3024 | 110 | 6.0184 | 0.0079322 | 6.0184 | 0.01179 | -0.020458 | -0.020458 | 21.9147 | 79.1077 | -209.035 | -209.035 | 111 | 5.9316 | 0.0080483 | 5.9316 | 0.011962 | -0.020514 | -0.020514 | 22.5848 | 82.1127 | -211.3699 | -211.3699 | 118 | 5.3573 | 0.0089111 | 5.3573 | 0.013245 | -0.020934 | -0.020934 | 25.5815 | 89.9207 | -216.1812 | -216.1812 | 121 | 5.1306 | 0.0093048 | 5.1306 | 0.01383 | -0.021125 | -0.021125 | 26.4195 | 103.6103 | -229.0328 | -229.0328 | 99 | 7.0393 | 0.0067818 | 7.0393 | 0.01008 | -0.019898 | -0.019898 | 21.2485 | 63.1136 | -193.7071 | -193.7071
Change reference after Copy/paste
32.974
0
12.2933
19.7914
0
-33.2987
-53.6091
0

## Summary
| Single Compressor System | [41 empty] | Demand w/Interactive Effects for original measures
Climate Zone | Representative City and Temperature (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf |  | 1T12 Shelf
|  |  | MT, (2)T12 to LED Canopy |  | LT, (2)T12 to LED Canopy |  | MT, (1)T12 to LED Canopy |  | LT, (1)T12 to LED Canopy |  | MT, (2)T8 to LED Canopy |  | LT, (2)T8 to LED Canopy |  | MT, (1)T8 to LED Canopy |  | LT, (1)T8 to LED Canopy |  | MT, T12 to CC retrofit |  | LT, T12 to CC retrofit |  | MT, (1)T12 to LED Shelf |  | LT, (1)T12 to LED Shelf |  | MT, (1)T8 to LED Shelf |  | LT, (1)T8 to LED Shelf |  | MT, T8 to FO retrofit |  | LT, T8 to FO retrofit |  | MT, T8 to CC retrofit |  | LT, T8 to CC retrofit |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT
|  |  | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Base 3' (2)T12 | Measure 3' LED | Base 3' (2)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 4' (1)T8 | Measure 4' LED
1 | Arcata - 69oF | /Fixture | 0.061183 | 286.9916 | 0.061788 | 288.8446 | 0.04686 | 215.7955 | 0.048081 | 219.1138 | 0.031271 | 147.5736 | 0.031437 | 148.1817 | 0.0082849 | 39.3066 | 0.0084538 | 39.9252 | 0.031961 | 70.8433 | 0.0314 | 67.9495 | 0.056806 | 258.0958 | 0.058332 | 261.6974 | 0.018231 | 84.1244 | 0.018705 | 85.4421 | 0.020129 | 89.6081 | 0.021039 | 91.8313 | -0.019039 | -188.8555 | -0.0196 | -194.9675 | 0.079016 | 0.017833 | 0.080169 | 0.018381 | 0.064693 | 0.017833 | 0.066462 | 0.018381 | 0.049104 | 0.017833 | 0.049818 | 0.018381 | 0.026118 | 0.017833 | 0.032462 | 0.016746 | 0.064693 | 0.0078874 | 0.060818 | 0.0097643 | 0.026118 | 0.0078874 | 0.032462 | 0.0081297
2 | Santa Rosa - 96oF | /Fixture | 0.062439 | 292.4684 | 0.063583 | 296.2406 | 0.049394 | 225.6035 | 0.051701 | 232.3588 | 0.031615 | 149.3712 | 0.031928 | 150.6093 | 0.0086356 | 41.135 | 0.0089548 | 42.3943 | 0.030796 | 62.2899 | 0.029737 | 56.3986 | 0.059974 | 268.7412 | 0.062858 | 276.0733 | 0.019216 | 88.019 | 0.020112 | 90.7015 | 0.022019 | 96.1792 | 0.02374 | 100.7051 | -0.020204 | -206.921 | -0.021263 | -219.3638 | 0.08141 | 0.018971 | 0.083589 | 0.020006 | 0.068365 | 0.018971 | 0.071706 | 0.020006 | 0.050586 | 0.018971 | 0.051934 | 0.020006 | 0.027606 | 0.018971 | 0.037706 | 0.017465 | 0.068365 | 0.0083904 | 0.062934 | 0.011389 | 0.027606 | 0.0083904 | 0.037706 | 0.0088482
3 | Oakland - 89oF | /Fixture | 0.062043 | 290.5544 | 0.063045 | 293.7919 | 0.048595 | 222.2947 | 0.050615 | 228.1187 | 0.031507 | 148.6084 | 0.031781 | 149.6416 | 0.008525 | 40.3628 | 0.0088046 | 41.4144 | 0.031163 | 64.0935 | 0.030235 | 58.7775 | 0.058976 | 265.2105 | 0.061501 | 271.545 | 0.018905 | 86.6993 | 0.01969 | 89.0106 | 0.021423 | 93.9752 | 0.022931 | 97.8798 | -0.019837 | -202.597 | -0.020765 | -213.7119 | 0.080655 | 0.018612 | 0.082563 | 0.019519 | 0.067207 | 0.018612 | 0.070134 | 0.019519 | 0.050119 | 0.018612 | 0.0513 | 0.019519 | 0.027137 | 0.018612 | 0.036134 | 0.017249 | 0.067207 | 0.0082318 | 0.0623 | 0.010902 | 0.027137 | 0.0082318 | 0.036134 | 0.0086328
4 | Sunnyvale - 88oF | /Fixture | 0.061991 | 290.6861 | 0.062973 | 293.9303 | 0.048491 | 222.5313 | 0.05047 | 228.3671 | 0.031493 | 148.6509 | 0.031761 | 149.6863 | 0.0085106 | 40.406 | 0.0087845 | 41.4599 | 0.031211 | 63.8809 | 0.030302 | 58.555 | 0.058845 | 265.4676 | 0.06132 | 271.8149 | 0.018865 | 86.7932 | 0.019634 | 89.1092 | 0.021345 | 94.1337 | 0.022822 | 98.0463 | -0.019789 | -203.0429 | -0.020698 | -214.1792 | 0.080557 | 0.018565 | 0.082426 | 0.019453 | 0.067056 | 0.018565 | 0.069924 | 0.019453 | 0.050058 | 0.018565 | 0.051215 | 0.019453 | 0.027076 | 0.018565 | 0.035924 | 0.017221 | 0.067056 | 0.0082111 | 0.062215 | 0.010837 | 0.027076 | 0.0082111 | 0.035924 | 0.008604
5 | Santa Maria - 83oF | /Fixture | 0.061748 | 290.1505 | 0.062628 | 293.143 | 0.048 | 221.3546 | 0.049776 | 226.6931 | 0.031426 | 148.7212 | 0.031667 | 149.7264 | 0.0084427 | 40.4709 | 0.0086884 | 41.4927 | 0.031437 | 66.8865 | 0.030621 | 62.4162 | 0.058232 | 264.0795 | 0.060451 | 269.8635 | 0.018674 | 86.3366 | 0.019364 | 88.4575 | 0.020979 | 93.322 | 0.022304 | 96.8965 | -0.019563 | -197.6366 | -0.020379 | -207.1663 | 0.080093 | 0.018345 | 0.08177 | 0.019142 | 0.066345 | 0.018345 | 0.068917 | 0.019142 | 0.049771 | 0.018345 | 0.050809 | 0.019142 | 0.026788 | 0.018345 | 0.034917 | 0.017083 | 0.066345 | 0.0081137 | 0.061809 | 0.010525 | 0.026788 | 0.0081137 | 0.034917 | 0.0084661
6 | Torrance - 86⁰F | /Fixture | 0.061891 | 290.2474 | 0.062832 | 293.3473 | 0.048289 | 221.7939 | 0.050186 | 227.3812 | 0.031465 | 148.4524 | 0.031723 | 149.4292 | 0.0084826 | 40.2056 | 0.0087452 | 41.2002 | 0.031393 | 64.7854 | 0.030559 | 59.8274 | 0.058592 | 264.6918 | 0.060964 | 270.7745 | 0.018786 | 86.498 | 0.019523 | 88.7149 | 0.02105 | 93.1408 | 0.022405 | 96.7139 | -0.019607 | -200.9451 | -0.020441 | -211.2685 | 0.080365 | 0.018474 | 0.082158 | 0.019326 | 0.066763 | 0.018474 | 0.069512 | 0.019326 | 0.049939 | 0.018474 | 0.051049 | 0.019326 | 0.026957 | 0.018474 | 0.035512 | 0.017164 | 0.066763 | 0.0081709 | 0.062049 | 0.010709 | 0.026957 | 0.0081709 | 0.035512 | 0.0085476
7 | San Diego - 83oF | /Fixture | 0.061748 | 290.209 | 0.062628 | 293.2136 | 0.048 | 221.6077 | 0.049776 | 226.9988 | 0.031426 | 148.5726 | 0.031667 | 149.547 | 0.0084427 | 40.3243 | 0.0086884 | 41.3156 | 0.031437 | 65.3165 | 0.030621 | 60.5196 | 0.058232 | 264.4298 | 0.060451 | 270.2867 | 0.018674 | 86.4299 | 0.019364 | 88.5701 | 0.020979 | 93.5075 | 0.022304 | 97.1206 | -0.019563 | -200.3106 | -0.020379 | -210.3968 | 0.080093 | 0.018345 | 0.08177 | 0.019142 | 0.066345 | 0.018345 | 0.068917 | 0.019142 | 0.049771 | 0.018345 | 0.050809 | 0.019142 | 0.026788 | 0.018345 | 0.034917 | 0.017083 | 0.066345 | 0.0081137 | 0.061809 | 0.010525 | 0.026788 | 0.0081137 | 0.034917 | 0.0084661
8 | Fullerton - 94⁰F | /Fixture | 0.062043 | 291.7754 | 0.063045 | 295.2804 | 0.048595 | 224.3392 | 0.050615 | 230.6109 | 0.031507 | 149.17 | 0.031781 | 150.3262 | 0.008525 | 40.9297 | 0.0088046 | 42.1055 | 0.031163 | 63.604 | 0.030235 | 58.1809 | 0.058976 | 267.3571 | 0.061501 | 274.1616 | 0.018905 | 87.5181 | 0.01969 | 90.0087 | 0.021423 | 95.3297 | 0.022931 | 99.5309 | -0.019837 | -204.2461 | -0.020765 | -215.7222 | 0.080655 | 0.018612 | 0.082563 | 0.019519 | 0.067207 | 0.018612 | 0.070134 | 0.019519 | 0.050119 | 0.018612 | 0.0513 | 0.019519 | 0.027137 | 0.018612 | 0.036134 | 0.017249 | 0.067207 | 0.0082318 | 0.0623 | 0.010902 | 0.027137 | 0.0082318 | 0.036134 | 0.0086328
9 | Burbank-Glendale - 96⁰F | /Fixture | 0.062439 | 293.5415 | 0.063583 | 297.5561 | 0.049394 | 227.4661 | 0.051701 | 234.6422 | 0.031615 | 149.7903 | 0.031928 | 151.1231 | 0.0086356 | 41.5594 | 0.0089548 | 42.9146 | 0.030907 | 62.0385 | 0.029885 | 56.1265 | 0.059974 | 270.7326 | 0.062858 | 278.5146 | 0.019216 | 88.7615 | 0.020112 | 91.6117 | 0.02184 | 96.7666 | 0.023499 | 101.397 | -0.020093 | -207.6999 | -0.021115 | -220.2422 | 0.08141 | 0.018971 | 0.083589 | 0.020006 | 0.068365 | 0.018971 | 0.071706 | 0.020006 | 0.050586 | 0.018971 | 0.051934 | 0.020006 | 0.027606 | 0.018971 | 0.037706 | 0.017465 | 0.068365 | 0.0083904 | 0.062934 | 0.011389 | 0.027606 | 0.0083904 | 0.037706 | 0.0088482
10 | Riverside - 100oF | /Fixture | 0.062696 | 294.5265 | 0.063921 | 298.7901 | 0.049912 | 229.2225 | 0.052383 | 236.8428 | 0.031686 | 150.1219 | 0.032021 | 151.5385 | 0.0087072 | 41.8965 | 0.0090491 | 43.3369 | 0.030559 | 59.739 | 0.029423 | 53.231 | 0.060621 | 272.6353 | 0.063711 | 280.8985 | 0.019417 | 89.4593 | 0.020377 | 92.486 | 0.022405 | 98.5967 | 0.024249 | 103.7005 | -0.020441 | -212.5965 | -0.021577 | -226.4074 | 0.081898 | 0.019203 | 0.084233 | 0.020312 | 0.069114 | 0.019203 | 0.072694 | 0.020312 | 0.050888 | 0.019203 | 0.052333 | 0.020312 | 0.02791 | 0.019203 | 0.038694 | 0.0176 | 0.069114 | 0.0084931 | 0.063333 | 0.011695 | 0.02791 | 0.0084931 | 0.038694 | 0.0089836
11 | Red Bluff - 104oF | /Fixture | 0.062978 | 295.7339 | 0.064286 | 300.2701 | 0.050481 | 231.2164 | 0.05312 | 239.2866 | 0.031763 | 150.7087 | 0.032121 | 152.258 | 0.008786 | 42.4882 | 0.0091511 | 44.0624 | 0.030297 | 59.532 | 0.029085 | 52.9797 | 0.061333 | 274.7136 | 0.064632 | 283.4456 | 0.019638 | 90.2593 | 0.020664 | 93.4665 | 0.02283 | 99.9145 | 0.024799 | 105.3155 | -0.020703 | -213.7626 | -0.021915 | -227.8326 | 0.082437 | 0.019458 | 0.084929 | 0.020642 | 0.06994 | 0.019458 | 0.073762 | 0.020642 | 0.051221 | 0.019458 | 0.052764 | 0.020642 | 0.028244 | 0.019458 | 0.039762 | 0.017747 | 0.06994 | 0.0086062 | 0.063764 | 0.012026 | 0.028244 | 0.0086062 | 0.039762 | 0.0091299
12 | Sacramento - 100oF | /Fixture | 0.062696 | 293.5231 | 0.063921 | 297.5587 | 0.049912 | 227.5853 | 0.052383 | 234.8335 | 0.031686 | 149.6122 | 0.032021 | 150.9128 | 0.0087072 | 41.3829 | 0.0090491 | 42.7065 | 0.030559 | 59.7155 | 0.029423 | 53.2021 | 0.060621 | 270.9396 | 0.063711 | 278.8174 | 0.019417 | 88.8014 | 0.020377 | 91.6785 | 0.022405 | 97.5169 | 0.024249 | 102.3753 | -0.020441 | -211.9558 | -0.021577 | -225.621 | 0.081898 | 0.019203 | 0.084233 | 0.020312 | 0.069114 | 0.019203 | 0.072694 | 0.020312 | 0.050888 | 0.019203 | 0.052333 | 0.020312 | 0.02791 | 0.019203 | 0.038694 | 0.0176 | 0.069114 | 0.0084931 | 0.063333 | 0.011695 | 0.02791 | 0.0084931 | 0.038694 | 0.0089836
13 | Fresno - 101oF | /Fixture | 0.062764 | 294.0587 | 0.064009 | 298.218 | 0.037736 | 192.1201 | 0.052561 | 236.0726 | 0.031704 | 149.7341 | 0.032045 | 151.0631 | 0.0087262 | 41.5084 | 0.0090739 | 42.8611 | 0.030496 | 58.4041 | 0.029341 | 51.5896 | 0.060793 | 272.0567 | 0.063934 | 280.1921 | 0.01947 | 89.1989 | 0.020447 | 92.1677 | 0.022508 | 98.1966 | 0.024382 | 103.2117 | -0.020504 | -214.5194 | -0.021659 | -228.7738 | 0.082028 | 0.019264 | 0.084401 | 0.020392 | 0.057 | 0.019264 | 0.072953 | 0.020392 | 0.050968 | 0.019264 | 0.052437 | 0.020392 | 0.02799 | 0.019264 | 0.038953 | 0.017636 | 0.069313 | 0.0085203 | 0.063437 | 0.011775 | 0.02799 | 0.0085203 | 0.038953 | 0.009019
14 | Palmdale - 103⁰F | /Fixture | 0.062905 | 295.299 | 0.064192 | 299.7393 | 0.050333 | 230.6019 | 0.052929 | 238.5375 | 0.031743 | 150.3802 | 0.032095 | 151.8558 | 0.0087656 | 42.1591 | 0.0091248 | 43.6595 | 0.030007 | 55.9351 | 0.028715 | 48.6041 | 0.061149 | 274.1303 | 0.064394 | 282.7353 | 0.019581 | 90.0073 | 0.02059 | 93.1592 | 0.023301 | 101.5907 | 0.025399 | 107.3423 | -0.020993 | -220.6758 | -0.022285 | -236.2347 | 0.082297 | 0.019392 | 0.084749 | 0.020557 | 0.069725 | 0.019392 | 0.073487 | 0.020557 | 0.051135 | 0.019392 | 0.052652 | 0.020557 | 0.028158 | 0.019392 | 0.039487 | 0.017709 | 0.069725 | 0.0085768 | 0.063652 | 0.01194 | 0.028158 | 0.0085768 | 0.039487 | 0.0090922
15 | Palm Springs-Intl - 113⁰F | /Fixture | 0.063731 | 297.9859 | 0.065244 | 302.9595 | 0.052 | 236.2714 | 0.05505 | 245.3543 | 0.031969 | 150.2923 | 0.032383 | 151.7255 | 0.0089962 | 42.0959 | 0.0094183 | 43.559 | 0.029769 | 47.3368 | 0.028413 | 38.1148 | 0.063232 | 280.7208 | 0.067046 | 290.6691 | 0.020229 | 92.2165 | 0.021414 | 95.8146 | 0.023687 | 102.4449 | 0.025889 | 108.3559 | -0.021231 | -235.219 | -0.022587 | -253.9583 | 0.083871 | 0.02014 | 0.086752 | 0.021509 | 0.07214 | 0.02014 | 0.076559 | 0.021509 | 0.052109 | 0.02014 | 0.053892 | 0.021509 | 0.029136 | 0.02014 | 0.042559 | 0.01813 | 0.07214 | 0.0089076 | 0.064892 | 0.012892 | 0.029136 | 0.0089076 | 0.042559 | 0.0095131
16 | Blue Canyon - 85⁰F | /Fixture | 0.061842 | 292.6021 | 0.062763 | 296.1746 | 0.048191 | 224.967 | 0.050047 | 231.1788 | 0.031452 | 150.4054 | 0.031704 | 151.7882 | 0.008469 | 42.1601 | 0.0087259 | 43.5609 | 0.031163 | 69.7389 | 0.030235 | 65.6593 | 0.058469 | 267.6042 | 0.060791 | 274.2517 | 0.018748 | 87.8092 | 0.019469 | 90.2849 | 0.021423 | 96.8487 | 0.022931 | 101.3826 | -0.019837 | -195.2082 | -0.020765 | -204.7051 | 0.080273 | 0.01843 | 0.082027 | 0.019264 | 0.066621 | 0.01843 | 0.069311 | 0.019264 | 0.049882 | 0.01843 | 0.050968 | 0.019264 | 0.026899 | 0.01843 | 0.035311 | 0.017137 | 0.066621 | 0.0081515 | 0.061968 | 0.010647 | 0.026899 | 0.0081515 | 0.035311 | 0.00852
|  |  | 0.061183 | 286.9916 | 0.061788 | 288.8446 | [20 empty] | 0.018231 | 84.1244 | 0.018705 | 85.4421 | 0.020129 | 89.6081 | 0.021039 | 91.8313 | -0.021231 | -235.219 | -0.022587 | -253.9583
|  |  | 0.063731 | 297.9859 | 0.065244 | 302.9595 | [20 empty] | 0.020229 | 92.2165 | 0.021414 | 95.8146 | 0.023687 | 102.4449 | 0.025889 | 108.3559 | -0.019039 | -188.8555 | -0.0196 | -194.9675
Multiplex Compressor System
Climate Zone | Representative City and Temperature (Summer Design Dry-Bubl, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf |  | 1T12 Shelf
|  |  | MT, (2)T12 to LED Canopy |  | LT, (2)T12 to LED Canopy |  | MT, (1)T12 to LED Canopy |  | LT, (1)T12 to LED Canopy |  | MT, (2)T8 to LED Canopy |  | LT, (2)T8 to LED Canopy |  | MT, (1)T8 to LED Canopy |  | LT, (1)T8 to LED Canopy |  | MT, T12 to CC retrofit |  | LT, T12 to CC retrofit |  | MT, (1)T12 to LED Shelf |  | LT, (1)T12 to LED Shelf |  | MT, (1)T8 to LED Shelf |  | LT, (1)T8 to LED Shelf |  | MT, T8 to FO retrofit |  | LT, T8 to FO retrofit |  | MT, T8 to CC retrofit |  | LT, T8 to CC retrofit |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT
|  |  | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Base 3' (2)T12 | Measure 3' LED | Base 3' (2)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 4' (1)T8 | Measure 4' LED
1 | Arcata - 69oF | /Fixture | 0.060055 | 282.1829 | 0.061301 | 286.8781 | 0.044584 | 207.184 | 0.047098 | 215.5922 | 0.030962 | 145.9952 | 0.031303 | 147.5363 | 0.0079699 | 37.7012 | 0.0083178 | 39.2687 | 0.033006 | 78.3534 | 0.031851 | 71.0206 | 0.053961 | 248.7489 | 0.057104 | 257.8751 | 0.017346 | 80.7049 | 0.018323 | 84.0437 | 0.018431 | 83.8386 | 0.020306 | 89.4719 | -0.017994 | -172.9936 | -0.019149 | -188.481 | 0.076866 | 0.016812 | 0.079241 | 0.01794 | 0.061396 | 0.016812 | 0.065038 | 0.01794 | 0.047774 | 0.016812 | 0.049244 | 0.01794 | 0.024782 | 0.016812 | 0.031038 | 0.016551 | 0.061396 | 0.0074357 | 0.060244 | 0.0093234 | 0.024782 | 0.0074357 | 0.031038 | 0.0079347
2 | Santa Rosa - 96oF | /Fixture | 0.060861 | 285.6938 | 0.06248 | 291.7541 | 0.046212 | 213.4713 | 0.049476 | 224.3243 | 0.031183 | 147.1476 | 0.031626 | 149.1367 | 0.0081951 | 38.8733 | 0.0086469 | 40.8965 | 0.032258 | 72.8703 | 0.030759 | 63.4055 | 0.055995 | 255.5731 | 0.060076 | 267.3527 | 0.017979 | 83.2015 | 0.019247 | 87.5111 | 0.019645 | 88.0509 | 0.02208 | 95.3222 | -0.018742 | -184.5744 | -0.020241 | -204.5648 | 0.078404 | 0.017542 | 0.081487 | 0.019007 | 0.063754 | 0.017542 | 0.068483 | 0.019007 | 0.048725 | 0.017542 | 0.050634 | 0.019007 | 0.025737 | 0.017542 | 0.034483 | 0.017023 | 0.063754 | 0.0077587 | 0.061634 | 0.010391 | 0.025737 | 0.0077587 | 0.034483 | 0.0084066
3 | Oakland - 89oF | /Fixture | 0.06064 | 284.6149 | 0.06211 | 290.0426 | 0.045765 | 211.6104 | 0.048729 | 221.3742 | 0.031122 | 146.713 | 0.031525 | 148.4451 | 0.0081333 | 38.4335 | 0.0085436 | 40.1965 | 0.032464 | 73.8458 | 0.031102 | 64.9337 | 0.055437 | 253.5896 | 0.059143 | 264.2093 | 0.017805 | 82.4591 | 0.018957 | 86.334 | 0.019311 | 86.8119 | 0.021523 | 93.358 | -0.018536 | -182.206 | -0.019898 | -200.8401 | 0.077981 | 0.017342 | 0.080782 | 0.018672 | 0.063107 | 0.017342 | 0.067402 | 0.018672 | 0.048464 | 0.017342 | 0.050197 | 0.018672 | 0.025475 | 0.017342 | 0.033402 | 0.016875 | 0.063107 | 0.00767 | 0.061197 | 0.010055 | 0.025475 | 0.00767 | 0.033402 | 0.0082584
4 | Sunnyvale - 88oF | /Fixture | 0.060609 | 284.6934 | 0.062061 | 290.1857 | 0.045702 | 211.7515 | 0.048631 | 221.6312 | 0.031114 | 146.7383 | 0.031512 | 148.4912 | 0.0081246 | 38.4592 | 0.0085299 | 40.2434 | 0.032492 | 73.7191 | 0.031147 | 64.7025 | 0.055358 | 253.7429 | 0.05902 | 264.4886 | 0.017781 | 82.5151 | 0.018919 | 86.436 | 0.019265 | 86.9064 | 0.02145 | 93.5302 | -0.018508 | -182.4719 | -0.019853 | -201.3251 | 0.077922 | 0.017314 | 0.080689 | 0.018628 | 0.063016 | 0.017314 | 0.067259 | 0.018628 | 0.048427 | 0.017314 | 0.050139 | 0.018628 | 0.025438 | 0.017314 | 0.033259 | 0.016856 | 0.063016 | 0.0076576 | 0.061139 | 0.010011 | 0.025438 | 0.0076576 | 0.033259 | 0.0082389
5 | Santa Maria - 83oF | /Fixture | 0.060456 | 284.34 | 0.061831 | 289.7444 | 0.045394 | 210.9885 | 0.048166 | 220.63 | 0.031072 | 146.7692 | 0.031449 | 148.5848 | 0.008082 | 38.4867 | 0.0084657 | 40.3322 | 0.032634 | 75.5666 | 0.03136 | 67.4932 | 0.054973 | 252.8485 | 0.058439 | 263.2945 | 0.017661 | 82.2185 | 0.018738 | 86.0488 | 0.019035 | 86.3812 | 0.021103 | 92.8369 | -0.018366 | -179.1322 | -0.01964 | -196.3432 | 0.077631 | 0.017175 | 0.08025 | 0.018419 | 0.062569 | 0.017175 | 0.066586 | 0.018419 | 0.048247 | 0.017175 | 0.049868 | 0.018419 | 0.025257 | 0.017175 | 0.032586 | 0.016763 | 0.062569 | 0.0075964 | 0.060868 | 0.0098028 | 0.025257 | 0.0075964 | 0.032586 | 0.0081467
6 | Torrance - 86⁰F | /Fixture | 0.060547 | 284.424 | 0.061966 | 289.7923 | 0.045578 | 211.2978 | 0.048439 | 220.9736 | 0.031097 | 146.6174 | 0.031486 | 148.309 | 0.0081074 | 38.3371 | 0.0085034 | 40.0596 | 0.032606 | 74.2967 | 0.031319 | 65.4767 | 0.055203 | 253.2651 | 0.05878 | 263.7988 | 0.017732 | 82.3335 | 0.018845 | 86.1726 | 0.01908 | 86.286 | 0.02117 | 92.6425 | -0.018394 | -181.1409 | -0.019681 | -199.5056 | 0.077805 | 0.017258 | 0.080508 | 0.018542 | 0.062836 | 0.017258 | 0.066981 | 0.018542 | 0.048355 | 0.017258 | 0.050028 | 0.018542 | 0.025365 | 0.017258 | 0.032981 | 0.016818 | 0.062836 | 0.0076329 | 0.061028 | 0.0099253 | 0.025365 | 0.0076329 | 0.032981 | 0.0082009
7 | San Diego - 83oF | /Fixture | 0.060456 | 284.3748 | 0.061831 | 289.8012 | 0.045394 | 211.1393 | 0.048166 | 220.876 | 0.031072 | 146.6807 | 0.031449 | 148.4404 | 0.008082 | 38.3994 | 0.0084657 | 40.1897 | 0.032634 | 74.631 | 0.03136 | 65.9675 | 0.054973 | 253.0573 | 0.058439 | 263.6349 | 0.017661 | 82.274 | 0.018738 | 86.1394 | 0.019035 | 86.4918 | 0.021103 | 93.0171 | -0.018366 | -180.7258 | -0.01964 | -198.9417 | 0.077631 | 0.017175 | 0.08025 | 0.018419 | 0.062569 | 0.017175 | 0.066586 | 0.018419 | 0.048247 | 0.017175 | 0.049868 | 0.018419 | 0.025257 | 0.017175 | 0.032586 | 0.016763 | 0.062569 | 0.0075964 | 0.060868 | 0.0098028 | 0.025257 | 0.0075964 | 0.032586 | 0.0081467
8 | Fullerton - 94⁰F | /Fixture | 0.060797 | 286.0669 | 0.062369 | 292.3472 | 0.046083 | 214.1246 | 0.049253 | 225.3623 | 0.031166 | 147.287 | 0.031596 | 149.3586 | 0.0081773 | 39.0146 | 0.008616 | 41.1215 | 0.032464 | 73.553 | 0.031102 | 64.4612 | 0.055834 | 256.2745 | 0.059797 | 268.4671 | 0.017928 | 83.4617 | 0.019161 | 87.9244 | 0.019311 | 87.6222 | 0.021523 | 94.6656 | -0.018536 | -183.1926 | -0.019898 | -202.4321 | 0.078281 | 0.017484 | 0.081276 | 0.018907 | 0.063567 | 0.017484 | 0.068159 | 0.018907 | 0.04865 | 0.017484 | 0.050503 | 0.018907 | 0.025661 | 0.017484 | 0.034159 | 0.016979 | 0.063567 | 0.007733 | 0.061503 | 0.01029 | 0.025661 | 0.007733 | 0.034159 | 0.0083623
9 | Burbank-Glendale - 96⁰F | /Fixture | 0.060861 | 286.3315 | 0.06248 | 292.7813 | 0.046212 | 214.5782 | 0.049476 | 226.1072 | 0.031183 | 147.3966 | 0.031626 | 149.5379 | 0.0081951 | 39.1256 | 0.0086469 | 41.3028 | 0.032318 | 72.6721 | 0.030861 | 63.0985 | 0.055995 | 256.7566 | 0.060076 | 269.259 | 0.017979 | 83.6427 | 0.019247 | 88.2218 | 0.019548 | 88.4383 | 0.021914 | 95.9364 | -0.018682 | -185.1407 | -0.020139 | -205.4511 | 0.078404 | 0.017542 | 0.081487 | 0.019007 | 0.063754 | 0.017542 | 0.068483 | 0.019007 | 0.048725 | 0.017542 | 0.050634 | 0.019007 | 0.025737 | 0.017542 | 0.034483 | 0.017023 | 0.063754 | 0.0077587 | 0.061634 | 0.010391 | 0.025737 | 0.0077587 | 0.034483 | 0.0084066
10 | Riverside - 100oF | /Fixture | 0.060992 | 286.8168 | 0.062713 | 293.6151 | 0.046475 | 215.4433 | 0.049947 | 227.5937 | 0.031219 | 147.5605 | 0.03169 | 149.8192 | 0.0082315 | 39.2921 | 0.0087121 | 41.5887 | 0.032138 | 71.507 | 0.030542 | 61.1301 | 0.056324 | 257.6935 | 0.060666 | 270.8691 | 0.018081 | 83.9865 | 0.019431 | 88.8124 | 0.019841 | 89.3679 | 0.022432 | 97.5058 | -0.018862 | -187.6234 | -0.020458 | -209.6446 | 0.078652 | 0.01766 | 0.081932 | 0.019219 | 0.064135 | 0.01766 | 0.069166 | 0.019219 | 0.048879 | 0.01766 | 0.050909 | 0.019219 | 0.025892 | 0.01766 | 0.035166 | 0.017117 | 0.064135 | 0.0078109 | 0.061909 | 0.010602 | 0.025892 | 0.0078109 | 0.035166 | 0.0085002
11 | Red Bluff - 104oF | /Fixture | 0.061126 | 287.382 | 0.062963 | 294.6183 | 0.046745 | 216.358 | 0.050451 | 229.2317 | 0.031255 | 147.8563 | 0.031759 | 150.3277 | 0.0082689 | 39.5899 | 0.0087818 | 42.1011 | 0.032014 | 71.5958 | 0.030311 | 61.1434 | 0.056662 | 258.6366 | 0.061295 | 272.5662 | 0.018186 | 84.3545 | 0.019626 | 89.4706 | 0.020043 | 89.9703 | 0.022808 | 98.5862 | -0.018986 | -187.8575 | -0.020689 | -210.3024 | 0.078907 | 0.017781 | 0.082408 | 0.019445 | 0.064526 | 0.017781 | 0.069895 | 0.019445 | 0.049037 | 0.017781 | 0.051203 | 0.019445 | 0.02605 | 0.017781 | 0.035895 | 0.017217 | 0.064526 | 0.0078645 | 0.062203 | 0.010828 | 0.02605 | 0.0078645 | 0.035895 | 0.0086001
12 | Sacramento - 100oF | /Fixture | 0.060992 | 286.2259 | 0.062713 | 292.6606 | 0.046475 | 214.4791 | 0.049947 | 226.0361 | 0.031219 | 147.2603 | 0.03169 | 149.3342 | 0.0082315 | 38.9896 | 0.0087121 | 41.1 | 0.032138 | 71.4931 | 0.030542 | 61.1077 | 0.056324 | 256.6948 | 0.060666 | 269.2558 | 0.018081 | 83.599 | 0.019431 | 88.1865 | 0.019841 | 88.732 | 0.022432 | 96.4785 | -0.018862 | -187.246 | -0.020458 | -209.035 | 0.078652 | 0.01766 | 0.081932 | 0.019219 | 0.064135 | 0.01766 | 0.069166 | 0.019219 | 0.048879 | 0.01766 | 0.050909 | 0.019219 | 0.025892 | 0.01766 | 0.035166 | 0.017117 | 0.064135 | 0.0078109 | 0.061909 | 0.010602 | 0.025892 | 0.0078109 | 0.035166 | 0.0085002
13 | Fresno - 101oF | /Fixture | 0.061025 | 286.5111 | 0.062774 | 293.1398 | 0.03931 | 193.5977 | 0.05007 | 226.9394 | 0.031228 | 147.3224 | 0.031707 | 149.4405 | 0.0082408 | 39.0537 | 0.0087291 | 41.2095 | 0.032107 | 70.7703 | 0.030486 | 59.9098 | 0.056407 | 257.2936 | 0.060819 | 270.2592 | 0.018107 | 83.8115 | 0.019478 | 88.5429 | 0.019891 | 89.0958 | 0.022524 | 97.0885 | -0.018893 | -188.6523 | -0.020514 | -211.3699 | 0.078715 | 0.01769 | 0.082048 | 0.019274 | 0.057 | 0.01769 | 0.069344 | 0.019274 | 0.048918 | 0.01769 | 0.050981 | 0.019274 | 0.025931 | 0.01769 | 0.035344 | 0.017141 | 0.064231 | 0.0078241 | 0.061981 | 0.010657 | 0.025931 | 0.0078241 | 0.035344 | 0.0085246
14 | Palmdale - 103⁰F | /Fixture | 0.061092 | 287.1681 | 0.062899 | 294.2467 | 0.046676 | 216.0703 | 0.050322 | 228.7212 | 0.031246 | 147.6781 | 0.031741 | 150.0305 | 0.0082594 | 39.4117 | 0.0087639 | 41.8035 | 0.031885 | 69.7952 | 0.030066 | 58.0528 | 0.056576 | 258.373 | 0.061134 | 272.091 | 0.018159 | 84.2355 | 0.019576 | 89.2603 | 0.020252 | 90.7166 | 0.023205 | 99.9291 | -0.019115 | -191.2599 | -0.020934 | -216.1812 | 0.078842 | 0.017751 | 0.082286 | 0.019387 | 0.064427 | 0.017751 | 0.069709 | 0.019387 | 0.048997 | 0.017751 | 0.051128 | 0.019387 | 0.02601 | 0.017751 | 0.035709 | 0.017191 | 0.064427 | 0.0078509 | 0.062128 | 0.01077 | 0.02601 | 0.0078509 | 0.035709 | 0.0085745
15 | Palm Springs-Intl - 113⁰F | /Fixture | 0.06145 | 288.2032 | 0.063575 | 296.1821 | 0.047398 | 218.4057 | 0.051685 | 232.9772 | 0.031344 | 147.4732 | 0.031926 | 149.7725 | 0.0083593 | 39.218 | 0.0089526 | 41.5652 | 0.031783 | 65.1838 | 0.029875 | 50.3811 | 0.057479 | 261.1532 | 0.062838 | 277.1128 | 0.01844 | 85.1393 | 0.020106 | 90.9116 | 0.020416 | 91.0054 | 0.023516 | 100.4935 | -0.019217 | -198.9531 | -0.021125 | -229.0328 | 0.079524 | 0.018075 | 0.083574 | 0.019999 | 0.065473 | 0.018075 | 0.071683 | 0.019999 | 0.049419 | 0.018075 | 0.051925 | 0.019999 | 0.026434 | 0.018075 | 0.037683 | 0.017462 | 0.065473 | 0.0079942 | 0.062925 | 0.011382 | 0.026434 | 0.0079942 | 0.037683 | 0.0088451
16 | Blue Canyon - 85⁰F | /Fixture | 0.060517 | 285.8238 | 0.06192 | 292.0908 | 0.045516 | 213.181 | 0.048347 | 224.0779 | 0.031089 | 147.7818 | 0.031473 | 150.2075 | 0.0080989 | 39.5024 | 0.0084906 | 41.9596 | 0.032464 | 77.2232 | 0.031102 | 70.3837 | 0.055126 | 254.9915 | 0.058664 | 266.6527 | 0.017708 | 83.1119 | 0.018808 | 87.4548 | 0.019311 | 88.5309 | 0.021523 | 96.132 | -0.018536 | -177.7857 | -0.019898 | -193.7071 | 0.077747 | 0.01723 | 0.08042 | 0.0185 | 0.062746 | 0.01723 | 0.066847 | 0.0185 | 0.048319 | 0.01723 | 0.049973 | 0.0185 | 0.025329 | 0.01723 | 0.032847 | 0.016799 | 0.062746 | 0.0076206 | 0.060973 | 0.0098836 | 0.025329 | 0.0076206 | 0.032847 | 0.0081824
[39 empty] | LT-49651 | [7 empty] | LT-58674 | [7 empty] | LT-65612 |  |  |  | LT-75912
|  |  | #REF! | #REF! | [22 empty] | #REF! | #REF! |  |  | #REF! | #REF! |  |  | #REF! | #REF! |  |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf
|  |  | #REF! | #REF! | [22 empty] | #REF! | #REF! |  |  | #REF! | #REF! |  |  | #REF! | #REF! |  |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT
|  | Single | [36 empty] | Base 3' (2)T12 | Measure 3' LED | Base 3' (2)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED
|  | 1 | [36 empty] | 0.079016 | 0.017833 | 0.082158 | 0.019326 | 0.066763 | 0.018474 | 0.069512 | 0.019326 | 0.049104 | 0.017833 | 0.049818 | 0.018381 | 0.026118 | 0.017833 | 0.032462 | 0.016746 | 0.064693 | 0.0078874 | 0.060818 | 0.0097643 | 0.026118 | 0.0078874
|  | 2 | [24 empty] | 16.6 | 26.56 | [10 empty] | 0.08141 | 0.018971 | 0.08177 | 0.019142 | 0.066345 | 0.018345 | 0.068917 | 0.019142 | 0.050586 | 0.018971 | 0.051934 | 0.020006 | 0.027606 | 0.018971 | 0.037706 | 0.017465 | 0.068365 | 0.0083904 | 0.062934 | 0.011389 | 0.027606 | 0.0083904
|  | 3 | [24 empty] | 6 | 9.6 | [10 empty] | 0.080655 | 0.018612 | 0.082563 | 0.019519 | 0.067207 | 0.018612 | 0.070134 | 0.019519 | 0.050119 | 0.018612 | 0.0513 | 0.019519 | 0.027137 | 0.018612 | 0.036134 | 0.017249 | 0.067207 | 0.0082318 | 0.0623 | 0.010902 | 0.027137 | 0.0082318 |  | RFF | Restaurant - Fast-Food
|  | 4 | [36 empty] | 0.080557 | 0.018565 | 0.083589 | 0.020006 | 0.068365 | 0.018971 | 0.071706 | 0.020006 | 0.050058 | 0.018565 | 0.051215 | 0.019453 | 0.027076 | 0.018565 | 0.035924 | 0.017221 | 0.067056 | 0.0082111 | 0.062215 | 0.010837 | 0.027076 | 0.0082111 |  | RtS | Retail - Small
|  | 5 | [36 empty] | 0.080093 | 0.018345 | 0.084233 | 0.020312 | 0.069114 | 0.019203 | 0.072694 | 0.020312 | 0.049771 | 0.018345 | 0.050809 | 0.019142 | 0.026788 | 0.018345 | 0.034917 | 0.017083 | 0.066345 | 0.0081137 | 0.061809 | 0.010525 | 0.026788 | 0.0081137 |  | Ofs | Office Small
|  | 6 | [36 empty] | 0.080365 | 0.018474 | 0.084929 | 0.020642 | 0.06994 | 0.019458 | 0.073762 | 0.020642 | 0.049939 | 0.018474 | 0.051049 | 0.019326 | 0.026957 | 0.018474 | 0.035512 | 0.017164 | 0.066763 | 0.0081709 | 0.062049 | 0.010709 | 0.026957 | 0.0081709
|  | 7 | [36 empty] | 0.080093 | 0.018345 | 0.084233 | 0.020312 | 0.069114 | 0.019203 | 0.072694 | 0.020312 | 0.049771 | 0.018345 | 0.050809 | 0.019142 | 0.026788 | 0.018345 | 0.034917 | 0.017083 | 0.066345 | 0.0081137 | 0.061809 | 0.010525 | 0.026788 | 0.0081137
|  | 8 | [36 empty] | 0.080655 | 0.018612 | 0.084401 | 0.020392 | 0.057 | 0.019264 | 0.072953 | 0.020392 | 0.050119 | 0.018612 | 0.0513 | 0.019519 | 0.027137 | 0.018612 | 0.036134 | 0.017249 | 0.067207 | 0.0082318 | 0.0623 | 0.010902 | 0.027137 | 0.0082318
|  | 9 | [36 empty] | 0.08141 | 0.018971 | 0.084749 | 0.020557 | 0.069725 | 0.019392 | 0.073487 | 0.020557 | 0.050586 | 0.018971 | 0.051934 | 0.020006 | 0.027606 | 0.018971 | 0.037706 | 0.017465 | 0.068365 | 0.0083904 | 0.062934 | 0.011389 | 0.027606 | 0.0083904
|  | 10 | [36 empty] | 0.081898 | 0.019203 | 0.086752 | 0.021509 | 0.07214 | 0.02014 | 0.076559 | 0.021509 | 0.050888 | 0.019203 | 0.052333 | 0.020312 | 0.02791 | 0.019203 | 0.038694 | 0.0176 | 0.069114 | 0.0084931 | 0.063333 | 0.011695 | 0.02791 | 0.0084931
|  | 11 | [36 empty] | 0.082437 | 0.019458 | 0.082027 | 0.019264 | 0.066621 | 0.01843 | 0.069311 | 0.019264 | 0.051221 | 0.019458 | 0.052764 | 0.020642 | 0.028244 | 0.019458 | 0.039762 | 0.017747 | 0.06994 | 0.0086062 | 0.063764 | 0.012026 | 0.028244 | 0.0086062
|  | 12 | [36 empty] | 0.081898 | 0.019203 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050888 | 0.019203 | 0.052333 | 0.020312 | 0.02791 | 0.019203 | 0.038694 | 0.0176 | 0.069114 | 0.0084931 | 0.063333 | 0.011695 | 0.02791 | 0.0084931
|  | 13 | [36 empty] | 0.082028 | 0.019264 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050968 | 0.019264 | 0.052437 | 0.020392 | 0.02799 | 0.019264 | 0.038953 | 0.017636 | 0.069313 | 0.0085203 | 0.063437 | 0.011775 | 0.02799 | 0.0085203 |  | Gro | Grocery
|  | 14 | [36 empty] | 0.082297 | 0.019392 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051135 | 0.019392 | 0.052652 | 0.020557 | 0.028158 | 0.019392 | 0.039487 | 0.017709 | 0.069725 | 0.0085768 | 0.063652 | 0.01194 | 0.028158 | 0.0085768 |  | RSD | Restaurant - Sit-Down
|  | 15 | [36 empty] | 0.083871 | 0.02014 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052109 | 0.02014 | 0.053892 | 0.021509 | 0.029136 | 0.02014 | 0.042559 | 0.01813 | 0.07214 | 0.0089076 | 0.064892 | 0.012892 | 0.029136 | 0.0089076 |  | Rt3 | Retail - Multistory Large
|  | 16 | [36 empty] | 0.080273 | 0.01843 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049882 | 0.01843 | 0.050968 | 0.019264 | 0.026899 | 0.01843 | 0.035311 | 0.017137 | 0.066621 | 0.0081515 | 0.061968 | 0.010647 | 0.026899 | 0.0081515 |  | RtL | Retail - Single-Story Large
[62 empty] | WRf | Warehouse - Refrigerated
[39 empty] | LT-49651 | [7 empty] | LT-58674 | [7 empty] | LT65612 |  |  |  | LT-75912
[39 empty] | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf
[39 empty] | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT
[39 empty] | Base 3' (2)T12 | Measure 3' LED | Base 3' (2)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (2)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T12 | Measure 3' LED | Base 3' (1)T8 | Measure 3' LED
|  | 1 | [36 empty] | 0.076866 | 0.016812 | 0.079241 | 0.01794 | 0.061396 | 0.016812 | 0.065038 | 0.01794 | 0.047774 | 0.016812 | 0.049244 | 0.01794 | 0.024782 | 0.016812 | 0.031038 | 0.016551 | 0.061396 | 0.0074357 | 0.060244 | 0.0093234 | 0.024782 | 0.0074357
|  | 2 | [36 empty] | 0.078404 | 0.017542 | 0.081487 | 0.019007 | 0.063754 | 0.017542 | 0.068483 | 0.019007 | 0.048725 | 0.017542 | 0.050634 | 0.019007 | 0.025737 | 0.017542 | 0.034483 | 0.017023 | 0.063754 | 0.0077587 | 0.061634 | 0.010391 | 0.025737 | 0.0077587
|  | 3 | [36 empty] | 0.077981 | 0.017342 | 0.080782 | 0.018672 | 0.063107 | 0.017342 | 0.067402 | 0.018672 | 0.048464 | 0.017342 | 0.050197 | 0.018672 | 0.025475 | 0.017342 | 0.033402 | 0.016875 | 0.063107 | 0.00767 | 0.061197 | 0.010055 | 0.025475 | 0.00767
|  | 4 | [36 empty] | 0.077922 | 0.017314 | 0.080689 | 0.018628 | 0.063016 | 0.017314 | 0.067259 | 0.018628 | 0.048427 | 0.017314 | 0.050139 | 0.018628 | 0.025438 | 0.017314 | 0.033259 | 0.016856 | 0.063016 | 0.0076576 | 0.061139 | 0.010011 | 0.025438 | 0.0076576
|  | 5 | [36 empty] | 0.077631 | 0.017175 | 0.08025 | 0.018419 | 0.062569 | 0.017175 | 0.066586 | 0.018419 | 0.048247 | 0.017175 | 0.049868 | 0.018419 | 0.025257 | 0.017175 | 0.032586 | 0.016763 | 0.062569 | 0.0075964 | 0.060868 | 0.0098028 | 0.025257 | 0.0075964
|  | 6 | [36 empty] | 0.077805 | 0.017258 | 0.080508 | 0.018542 | 0.062836 | 0.017258 | 0.066981 | 0.018542 | 0.048355 | 0.017258 | 0.050028 | 0.018542 | 0.025365 | 0.017258 | 0.032981 | 0.016818 | 0.062836 | 0.0076329 | 0.061028 | 0.0099253 | 0.025365 | 0.0076329
|  | 7 | [36 empty] | 0.077631 | 0.017175 | 0.08025 | 0.018419 | 0.062569 | 0.017175 | 0.066586 | 0.018419 | 0.048247 | 0.017175 | 0.049868 | 0.018419 | 0.025257 | 0.017175 | 0.032586 | 0.016763 | 0.062569 | 0.0075964 | 0.060868 | 0.0098028 | 0.025257 | 0.0075964
|  | 8 | [36 empty] | 0.078281 | 0.017484 | 0.081276 | 0.018907 | 0.063567 | 0.017484 | 0.068159 | 0.018907 | 0.04865 | 0.017484 | 0.050503 | 0.018907 | 0.025661 | 0.017484 | 0.034159 | 0.016979 | 0.063567 | 0.007733 | 0.061503 | 0.01029 | 0.025661 | 0.007733
|  | 9 | [36 empty] | 0.078404 | 0.017542 | 0.081487 | 0.019007 | 0.063754 | 0.017542 | 0.068483 | 0.019007 | 0.048725 | 0.017542 | 0.050634 | 0.019007 | 0.025737 | 0.017542 | 0.034483 | 0.017023 | 0.063754 | 0.0077587 | 0.061634 | 0.010391 | 0.025737 | 0.0077587
|  | 10 | [36 empty] | 0.078652 | 0.01766 | 0.081932 | 0.019219 | 0.064135 | 0.01766 | 0.069166 | 0.019219 | 0.048879 | 0.01766 | 0.050909 | 0.019219 | 0.025892 | 0.01766 | 0.035166 | 0.017117 | 0.064135 | 0.0078109 | 0.061909 | 0.010602 | 0.025892 | 0.0078109
|  | 11 | [36 empty] | 0.078907 | 0.017781 | 0.082408 | 0.019445 | 0.064526 | 0.017781 | 0.069895 | 0.019445 | 0.049037 | 0.017781 | 0.051203 | 0.019445 | 0.02605 | 0.017781 | 0.035895 | 0.017217 | 0.064526 | 0.0078645 | 0.062203 | 0.010828 | 0.02605 | 0.0078645
|  | 12 | [36 empty] | 0.078652 | 0.01766 | 0.081932 | 0.019219 | 0.064135 | 0.01766 | 0.069166 | 0.019219 | 0.048879 | 0.01766 | 0.050909 | 0.019219 | 0.025892 | 0.01766 | 0.035166 | 0.017117 | 0.064135 | 0.0078109 | 0.061909 | 0.010602 | 0.025892 | 0.0078109
|  | 13 | [36 empty] | 0.078715 | 0.01769 | 0.082048 | 0.019274 | 0.057 | 0.01769 | 0.069344 | 0.019274 | 0.048918 | 0.01769 | 0.050981 | 0.019274 | 0.025931 | 0.01769 | 0.035344 | 0.017141 | 0.064231 | 0.0078241 | 0.061981 | 0.010657 | 0.025931 | 0.0078241
|  | 14 | [36 empty] | 0.078842 | 0.017751 | 0.082286 | 0.019387 | 0.064427 | 0.017751 | 0.069709 | 0.019387 | 0.048997 | 0.017751 | 0.051128 | 0.019387 | 0.02601 | 0.017751 | 0.035709 | 0.017191 | 0.064427 | 0.0078509 | 0.062128 | 0.01077 | 0.02601 | 0.0078509
|  | 15 | [36 empty] | 0.079524 | 0.018075 | 0.083574 | 0.019999 | 0.065473 | 0.018075 | 0.071683 | 0.019999 | 0.049419 | 0.018075 | 0.051925 | 0.019999 | 0.026434 | 0.018075 | 0.037683 | 0.017462 | 0.065473 | 0.0079942 | 0.062925 | 0.011382 | 0.026434 | 0.0079942
|  | 16 | [36 empty] | 0.077747 | 0.01723 | 0.08042 | 0.0185 | 0.062746 | 0.01723 | 0.066847 | 0.0185 | 0.048319 | 0.01723 | 0.049973 | 0.0185 | 0.025329 | 0.01723 | 0.032847 | 0.016799 | 0.062746 | 0.0076206 | 0.060973 | 0.0098836 | 0.025329 | 0.0076206

## Calc Template Form
|  | Single Compressor |  |  | Multiplex Compressor
Solution Code | Climate Zone | Base Watts | Measure Watts | Watts Saved | Base Watts | Measure Watts | Watts Saved | Average Watts Saved
LT-49651 | 1 | 0.079016 | 0.017833 | 0.061183 | 0.076866 | 0.016812 | 0.060055 | 0.060619
LT-49651 | 2 | 0.08141 | 0.018971 | 0.062439 | 0.078404 | 0.017542 | 0.060861 | 0.06165
LT-49651 | 3 | 0.080655 | 0.018612 | 0.062043 | 0.077981 | 0.017342 | 0.06064 | 0.061342
LT-49651 | 4 | 0.080557 | 0.018565 | 0.061991 | 0.077922 | 0.017314 | 0.060609 | 0.0613
LT-49651 | 5 | 0.080093 | 0.018345 | 0.061748 | 0.077631 | 0.017175 | 0.060456 | 0.061102
LT-49651 | 6 | 0.080365 | 0.018474 | 0.061891 | 0.077805 | 0.017258 | 0.060547 | 0.061219
LT-49651 | 7 | 0.080093 | 0.018345 | 0.061748 | 0.077631 | 0.017175 | 0.060456 | 0.061102
LT-49651 | 8 | 0.080655 | 0.018612 | 0.062043 | 0.078281 | 0.017484 | 0.060797 | 0.06142
LT-49651 | 9 | 0.08141 | 0.018971 | 0.062439 | 0.078404 | 0.017542 | 0.060861 | 0.06165
LT-49651 | 10 | 0.081898 | 0.019203 | 0.062696 | 0.078652 | 0.01766 | 0.060992 | 0.061844
LT-49651 | 11 | 0.082437 | 0.019458 | 0.062978 | 0.078907 | 0.017781 | 0.061126 | 0.062052
LT-49651 | 12 | 0.081898 | 0.019203 | 0.062696 | 0.078652 | 0.01766 | 0.060992 | 0.061844
LT-49651 | 13 | 0.082028 | 0.019264 | 0.062764 | 0.078715 | 0.01769 | 0.061025 | 0.061894
LT-49651 | 14 | 0.082297 | 0.019392 | 0.062905 | 0.078842 | 0.017751 | 0.061092 | 0.061998
LT-49651 | 15 | 0.083871 | 0.02014 | 0.063731 | 0.079524 | 0.018075 | 0.06145 | 0.06259
LT-49651 | 16 | 0.080273 | 0.01843 | 0.061842 | 0.077747 | 0.01723 | 0.060517 | 0.06118
LT-58674 | 1 | 0.049104 | 0.017833 | 0.031271 | 0.047774 | 0.016812 | 0.030962 | 0.031117
LT-58674 | 2 | 0.050586 | 0.018971 | 0.031615 | 0.048725 | 0.017542 | 0.031183 | 0.031399
LT-58674 | 3 | 0.050119 | 0.018612 | 0.031507 | 0.048464 | 0.017342 | 0.031122 | 0.031315
LT-58674 | 4 | 0.050058 | 0.018565 | 0.031493 | 0.048427 | 0.017314 | 0.031114 | 0.031303
LT-58674 | 5 | 0.049771 | 0.018345 | 0.031426 | 0.048247 | 0.017175 | 0.031072 | 0.031249
LT-58674 | 6 | 0.049939 | 0.018474 | 0.031465 | 0.048355 | 0.017258 | 0.031097 | 0.031281
LT-58674 | 7 | 0.049771 | 0.018345 | 0.031426 | 0.048247 | 0.017175 | 0.031072 | 0.031249
LT-58674 | 8 | 0.050119 | 0.018612 | 0.031507 | 0.04865 | 0.017484 | 0.031166 | 0.031336
LT-58674 | 9 | 0.050586 | 0.018971 | 0.031615 | 0.048725 | 0.017542 | 0.031183 | 0.031399
LT-58674 | 10 | 0.050888 | 0.019203 | 0.031686 | 0.048879 | 0.01766 | 0.031219 | 0.031452
LT-58674 | 11 | 0.051221 | 0.019458 | 0.031763 | 0.049037 | 0.017781 | 0.031255 | 0.031509
LT-58674 | 12 | 0.050888 | 0.019203 | 0.031686 | 0.048879 | 0.01766 | 0.031219 | 0.031452
LT-58674 | 13 | 0.050968 | 0.019264 | 0.031704 | 0.048918 | 0.01769 | 0.031228 | 0.031466
LT-58674 | 14 | 0.051135 | 0.019392 | 0.031743 | 0.048997 | 0.017751 | 0.031246 | 0.031494
LT-58674 | 15 | 0.052109 | 0.02014 | 0.031969 | 0.049419 | 0.018075 | 0.031344 | 0.031657
LT-58674 | 16 | 0.049882 | 0.01843 | 0.031452 | 0.048319 | 0.01723 | 0.031089 | 0.03127
LT-65612 | 1 | 0.064693 | 0.0078874 | 0.056806 | 0.061396 | 0.0074357 | 0.053961 | 0.055383
LT-65612 | 2 | 0.068365 | 0.0083904 | 0.059974 | 0.063754 | 0.0077587 | 0.055995 | 0.057985
LT-65612 | 3 | 0.067207 | 0.0082318 | 0.058976 | 0.063107 | 0.00767 | 0.055437 | 0.057206
LT-65612 | 4 | 0.067056 | 0.0082111 | 0.058845 | 0.063016 | 0.0076576 | 0.055358 | 0.057102
LT-65612 | 5 | 0.066345 | 0.0081137 | 0.058232 | 0.062569 | 0.0075964 | 0.054973 | 0.056602
LT-65612 | 6 | 0.066763 | 0.0081709 | 0.058592 | 0.062836 | 0.0076329 | 0.055203 | 0.056897
LT-65612 | 7 | 0.066345 | 0.0081137 | 0.058232 | 0.062569 | 0.0075964 | 0.054973 | 0.056602
LT-65612 | 8 | 0.067207 | 0.0082318 | 0.058976 | 0.063567 | 0.007733 | 0.055834 | 0.057405
LT-65612 | 9 | 0.068365 | 0.0083904 | 0.059974 | 0.063754 | 0.0077587 | 0.055995 | 0.057985
LT-65612 | 10 | 0.069114 | 0.0084931 | 0.060621 | 0.064135 | 0.0078109 | 0.056324 | 0.058473
LT-65612 | 11 | 0.06994 | 0.0086062 | 0.061333 | 0.064526 | 0.0078645 | 0.056662 | 0.058998
LT-65612 | 12 | 0.069114 | 0.0084931 | 0.060621 | 0.064135 | 0.0078109 | 0.056324 | 0.058473
LT-65612 | 13 | 0.069313 | 0.0085203 | 0.060793 | 0.064231 | 0.0078241 | 0.056407 | 0.0586
LT-65612 | 14 | 0.069725 | 0.0085768 | 0.061149 | 0.064427 | 0.0078509 | 0.056576 | 0.058862
LT-65612 | 15 | 0.07214 | 0.0089076 | 0.063232 | 0.065473 | 0.0079942 | 0.057479 | 0.060356
LT-65612 | 16 | 0.066621 | 0.0081515 | 0.058469 | 0.062746 | 0.0076206 | 0.055126 | 0.056798
LT-75912 | 1 | 0.026118 | 0.0078874 | 0.018231 | 0.024782 | 0.0074357 | 0.017346 | 0.017788
LT-75912 | 2 | 0.027606 | 0.0083904 | 0.019216 | 0.025737 | 0.0077587 | 0.017979 | 0.018597
LT-75912 | 3 | 0.027137 | 0.0082318 | 0.018905 | 0.025475 | 0.00767 | 0.017805 | 0.018355
LT-75912 | 4 | 0.027076 | 0.0082111 | 0.018865 | 0.025438 | 0.0076576 | 0.017781 | 0.018323
LT-75912 | 5 | 0.026788 | 0.0081137 | 0.018674 | 0.025257 | 0.0075964 | 0.017661 | 0.018167
LT-75912 | 6 | 0.026957 | 0.0081709 | 0.018786 | 0.025365 | 0.0076329 | 0.017732 | 0.018259
LT-75912 | 7 | 0.026788 | 0.0081137 | 0.018674 | 0.025257 | 0.0075964 | 0.017661 | 0.018167
LT-75912 | 8 | 0.027137 | 0.0082318 | 0.018905 | 0.025661 | 0.007733 | 0.017928 | 0.018417
LT-75912 | 9 | 0.027606 | 0.0083904 | 0.019216 | 0.025737 | 0.0077587 | 0.017979 | 0.018597
LT-75912 | 10 | 0.02791 | 0.0084931 | 0.019417 | 0.025892 | 0.0078109 | 0.018081 | 0.018749
LT-75912 | 11 | 0.028244 | 0.0086062 | 0.019638 | 0.02605 | 0.0078645 | 0.018186 | 0.018912
LT-75912 | 12 | 0.02791 | 0.0084931 | 0.019417 | 0.025892 | 0.0078109 | 0.018081 | 0.018749
LT-75912 | 13 | 0.02799 | 0.0085203 | 0.01947 | 0.025931 | 0.0078241 | 0.018107 | 0.018788
LT-75912 | 14 | 0.028158 | 0.0085768 | 0.019581 | 0.02601 | 0.0078509 | 0.018159 | 0.01887
LT-75912 | 15 | 0.029136 | 0.0089076 | 0.020229 | 0.026434 | 0.0079942 | 0.01844 | 0.019334
LT-75912 | 16 | 0.026899 | 0.0081515 | 0.018748 | 0.025329 | 0.0076206 | 0.017708 | 0.018228