## Cooling Load
Electrical Specifications
Key Parameters | 2 - 4' T12 | 1 - 4' T12HO | 2 - 4' T8 | 1 - 4' T8 | 4' Canopy (2) | 4' Canopy (1) | 4' Shelf (1) | Cold Cathode
Lamp description type | F42EIS F48T12/ES | F42SHS F48T12/HO | F42ILL | F42ILL
Lamps per ballast | 2 | 2 | 2 | 2
Minimum starting temp. (F)
Input volts | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Ballast factor
Power factor
Input power (W) | 82 | 145 | 59 | 59
Direct power (W/lamp) | 41 | 72.5 | 29.5 | 29.5 | 18.6667 | 18.6667 | 9.6 | 39.6
Power (kW) and Energy (kWh) Consumptions
Key Parameters | 2 - 4' T12 | 1 - 4' T12HO | 2 - 4' T8 | 1 - 4' T8 | 4' Canopy (2) | 4' Canopy (1) | 4' Shelf (1) | Cold Cathode
Direct power (kW/lamp) | 0.041 | 0.0725 | 0.0295 | 0.0295 | 0.018667 | 0.018667 | 0.0096 | 0.0396
Direct power (kW/fixt) | 0.082 | 0.0725 | 0.059 | 0.0295 | 0.018667 | 0.018667 | 0.0096 | 0.0396
Lighting power savings T12 base (kW/fixt) | --- | --- | --- |  | 0.063333 | 0.053833 | 0.0629 | 0.0424
Lighting power savings T8 base(kW/fixt) | --- | --- | --- | --- | 0.040333 | 0.010833 | 0.0199 | -0.0101
Daily hours of operation | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 12.9041 | 18
Annual hours of operation | 4710 | 4710 | 4710 | 4710 | 4710 | 4710 | 4710 | 6570
Direct annual energy (kWh/fixt/year)* | 386.22 | 341.475 | 277.89 | 138.945 | 87.92 | 87.92 | 45.216 | 260.172
Annual lighting energy savings T12 base (kWh/fixt/year) | --- | --- | --- |  | 298.3 | 253.555 | 296.259 | 126.048
Annual lighting energy savings T8 base (kWh/fixt/year) | --- | --- | --- | --- | 189.97 | 51.025 | 93.729 | -121.227
% of heat entering cold space | 70.31% | 70% | 70% | 70.31% | 80% | 80% | 80% | 70%
Cooling load due to lighting system (Btu/hr/door) | 52.8998 | 93.1299 | 37.8942 | 38.0621 | 27.4037 | 27.4037 | 14.0934 | 70.9563
Change in cooling load T12 base (Btu/hr/door) | --- | --- | --- |  | 25.4961 | 65.7262 | 79.0365 | -18.0565
Change in cooling load T8 base (Btu/hr/door) | --- | --- | --- | --- | 10.4905 | 10.6583 | 23.9687 | -32.8942
Cooling Load (Btu/hr/door) | 52.8998 | 93.1299 | 37.8942 | 38.0621 | 27.4037 | 27.4037 | 14.0934 | 70.9563
COP @ -20F using ARI 1200 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 3.02 | 2.02 | 3.02
Indirect refrig power (kW/lamp) | 0.020297 | 0.035891 | 0.014604 | 0.014604 | 0.0092409 | 0.006181 | 0.0047525 | 0.013113
TOTAL elect. power (kW/lamp) | 0.061297 | 0.10839 | 0.044104 | 0.044104 | 0.027908 | 0.024848 | 0.014352 | 0.052713
TOTAL elect. power (kW/door)* | 0.073556 | 0.13007 | 0.052925 | 0.052925 | 0.027908 | 0.024848 | 0.0047842 | 0.017571
Annual Energy Use (kWh/yr/door) | 346.4508 | 612.6264 | 249.2756 | 249.2756 | 131.4448 | 117.0326 | 22.5334 | 115.4406
*5-door display case equipped with 6 T8 or T12 lamps
Note on J29: Devin Rauss: This number seems high… It seems to be set to the same value as the fluorescent, but these operate at lower temp, so I would think less heat should enter.

## LED Watts
| Replacing | Typical Wattage | Quant. | Length | Brand | Product Code | LED Replacement |  | Wattage Saved | % saved
[7 empty] | Lumens | Wattage |  |  | PDF
Undershelf | 1-48"T12 | 51 | 1 | 46" | LEDPower | SB8-1/4W-46”-xxx-24V | 558 | 10.5 | 40.5 | 79.41% | LEDPower SB Series Horizontal
Undershelf | 1-48"T12 | 51 | 1 | 46" | GE | GE-MT304840USL | 521 | 7.1 | 43.9 | 86.08% | GE led horizontal application
Undershelf | 1-48"T12 | 51 | 1 | 47" | Philps | LCM310 | 800 | 10 | 41 | 80.39% | Philips shelf lighting
Undershelf | 1-48"T12 | 51 | 1 | 48" | Sylvania | LSX/Strip/24V/840 | 660 | 10.8 | 40.2 | 78.82% | sylvania shelf lighting
[7 empty] | Average | 9.6
Undershelf | 1-48"T8 | 32 | 1 | 46" | LEDPower | SB8-1/4W-46”-xxx-24V | 558 | 10.5 | 21.5 | 67.19% | LEDPower SB Series Horizontal
Undershelf | 1-48"T8 | 32 | 1 | 46" | GE | GE-MT304840USL | 521 | 7.1 | 24.9 | 77.81% | GE led horizontal application
Undershelf | 1-48"T8 | 32 | 1 | 47" | Philps | LCM310 | 800 | 10 | 22 | 68.75% | Philips shelf lighting
Undershelf | 1-48"T8 | 32 | 1 | 48" | Sylvania | LSX/Strip/24V/840 | 660 | 10.8 | 21.2 | 66.25% | sylvania shelf lighting
[7 empty] | Average | 9.6
| Replacing | Typical Wattage | Quant. | Length | Brand | Product Code | LED Replacement Savings |  | Wattage Saved | %
Canopy | 1-48"T12HO | 62 | 1 | 46" | LEDPower | SB8-1/2W-46”-xxx-24V | 876.8571 | 16.5 | 45.5 | 73.39% | LEDPower SB Series Horizontal
Canopy | 1-48"T12HO | 62 | 1 | 46" | GE | GE-MT304840CAN | 1511 | 21.5 | 40.5 | 65.32% | GE led horizontal application
Canopy | 1-48"T12HO | 62 | 1 | 47" | Philps | LDM422 47 Value plus | 1300 | 18 | 44 | 70.97% | Philips Canopy Lighting
Canopy | 1-48"T12HO | 62 |  |  | Sylvania | N/A
[7 empty] | Average | 18.6667
Canopy | 2-48"T12 | 87 | 1 | 46" | LEDPower | SB8-1/2W-46”-xxx-24V | 882 | 16.5 | 70.5 | 81.03% | LEDPower SB Series Horizontal
Canopy | 2-48"T12 | 87 | 1 | 46" | GE | GE-MT304840CAN | 1511 | 21.5 | 65.5 | 75.29% | GE led horizontal application
Canopy | 2-48"T12 | 87 | 1 | 47" | Philps | LDM422 47 Value plus | 1300 | 18 | 69 | 79.31% | Philips Canopy Lighting
Canopy | 2-48"T12 | 87 |  |  | Sylvania | N/A
[7 empty] | Average | 18.6667
Canopy | 2-48"T8 | 58 | 1 | 46" | LEDPower | SB8-1/2W-46”-xxx-24V | 882 | 16.5 | 41.5 | 71.55% | LEDPower SB Series Horizontal
Canopy | 2-48"T8 | 58 | 1 | 46" | GE | GE-MT304840CAN | 1511 | 21.5 | 36.5 | 62.93% | GE led horizontal application
Canopy | 2-48"T8 | 58 | 1 | 47" | Philps | LDM422 47 Value plus | 1300 | 18 | 40 | 68.97% | Philips Canopy Lighting
Canopy | 2-48"T8 | 58 |  |  | Sylvania | N/A
[7 empty] | Average | 18.6667

## DI_EEM_Savings_16CTZ
Y = a+b*x1+c*x2+d*x1^2+e*x2^2+f*x1*x2+g*x1^3+h*x2^3+i*x1*x2^2+j*x1^2*x2
[6 empty] | MT | LT
[5 empty] | a | 3.7535 | 9.8665
[5 empty] | b | -0.049642 | -0.23036
[5 empty] | c | 29.459 | 22.9056
|  | MT | LT |  | d | 0.00034207 | 0.0021889 | [7 empty] | CTZ1 | CTZ2 | CTZ3 | CTZ4 | CTZ5 | CTZ6 | CTZ7 | CTZ8 | CTZ9 | CTZ10 | CTZ11 | CTZ12 | CTZ13 | CTZ14 | CTZ15 | CTZ16
| Oversizing Factor (OS) | 13.04% | 13.04% |  | e | -11.7706 | -2.4887 | [5 empty] | Weather Factor |  | 74.26% | 74.8% | 76.05% | 77.87% | 76.26% | 78.9% | 79.73% | 79.38% | 78.58% | 77.74% | 74.95% | 76.13% | 77.88% | 77.03% | 85% | 71.04%
| Defrost Factor | 5% | 10% |  | f | -0.21294 | -0.24805 | [5 empty] | Overall Duty Cycle Factor | MT | 61.34% | 61.79% | 62.82% | 64.33% | 63% | 65.18% | 65.86% | 65.57% | 64.91% | 64.22% | 61.92% | 62.89% | 64.34% | 63.63% | 70.22% | 58.69%
| Weather Div. Factor | 85% | 85% |  | g | -1.4661e-06 | -7.575e-06 | [6 empty] | LT | 58.12% | 58.54% | 59.51% | 60.94% | 59.68% | 61.75% | 62.39% | 62.12% | 61.5% | 60.84% | 58.66% | 59.58% | 60.95% | 60.28% | 66.52% | 55.6%
| Overall Duty Cycle Factor | 70.22% | 66.52% |  | h | 6.8017 | 2.0361 | [5 empty] | EFLH | MT | 2889.3124 | 2910.4544 | 2958.8601 | 3029.8603 | 2967.2949 | 3069.8738 | 3102.0385 | 3088.4402 | 3057.3864 | 3024.6053 | 2916.2404 | 2962.0643 | 3030.2387 | 2997.0853 | 3307.2391 | 2764.0656
| Total Hours | 4710 | 4710 |  | i | -0.020187 | -0.021477 | [6 empty] | LT | 2737.2433 | 2757.2726 | 2803.1306 | 2870.394 | 2811.1215 | 2908.3015 | 2938.7733 | 2925.8907 | 2896.4713 | 2865.4156 | 2762.7541 | 2806.1662 | 2870.7525 | 2839.344 | 3133.1739 | 2618.5885
| EFLH | 3307.2391 | 3133.1739 |  | j | 0.00065794 | 0.00093831
Measure | Measure Unit | Total Unit | Box Temp | SET | Baseline Cooling Load | Compressor Capacity (Baseline Cooling Load with 15% OS) | Post Retrofit Cooling Load | Direct Power Reduction | Direct Energy Reduction | Part-Load-Ratio (Post Retrofit / Comp Cap) | Post Retrofit Duty Cycle Factor w/o Weather Factor Term | CTZ 1 - Arcata Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [69oF] |  |  | CTZ9: CTZ 2 - Santa Rosa Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] |  |  |  | CTZ 3 - Oakland Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [89oF] | [10 empty] | CTZ 4 - Sunnyvale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [88oF] | [10 empty] | CTZ 5 - Santa Maria Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 6 - Torrance Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [86oF] | [10 empty] | CTZ 7 - San Diego Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 8 - Fullerton Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [94oF] | [10 empty] | CTZ 9 - Burbank - Glendale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] | [10 empty] | CTZ 10 - Riverside Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 11 - Red Bluff Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [104oF] | [10 empty] | CTZ 12 - Sacramento Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 13 - Fresno Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [101oF] | [10 empty] | CTZ 14 - Palmdale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [103oF] | [10 empty] | CTZ 15 - Palm Springs Intl Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [113oF] | [10 empty] | CTZ 16 - Blue Canyon Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [85oF]
[12 empty] | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit
|  |  | [oF] | [oF] | [Btu/hr] | [Btu/hr] | [Btu/hr] | [kW] | [kWh] |  |  | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit]
[15 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T12 Baseline)
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (2)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 52.8998 | 60.8348 | 27.4037 | 0.063333 | 298.3 | 0.45046 | 42.79% | 84 | 9.5174 | 0.0055582 | 9.5174 | 0.0028793 | 0.066012 | 0.066012 | 16.0594 | 4.3096 | 310.0498 | 310.0498 | 111 | 6.4426 | 0.008211 | 6.4426 | 0.0042535 | 0.067291 | 0.067291 | 23.8977 | 6.4131 | 315.7846 | 315.7846 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0038203 | 0.066888 | 0.066888 | 21.3078 | 5.8557 | 313.7521 | 313.7521 | 103 | 7.2811 | 0.0072654 | 7.2811 | 0.0037637 | 0.066835 | 0.066835 | 21.4972 | 5.9073 | 313.8899 | 313.8899 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0034977 | 0.066588 | 0.066588 | 20.4572 | 5.3764 | 313.3807 | 313.3807 | 101 | 7.4998 | 0.0070535 | 7.4998 | 0.0036539 | 0.066733 | 0.066733 | 20.9299 | 5.8108 | 313.4191 | 313.4191 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0034977 | 0.066588 | 0.066588 | 20.7273 | 5.6206 | 313.4068 | 313.4068 | 109 | 6.6469 | 0.0079585 | 6.6469 | 0.0041228 | 0.067169 | 0.067169 | 24.6877 | 6.5961 | 316.3917 | 316.3917 | 111 | 6.4426 | 0.008211 | 6.4426 | 0.0042535 | 0.067291 | 0.067291 | 25.3591 | 6.7368 | 316.9223 | 316.9223 | 115 | 6.044 | 0.0087524 | 6.044 | 0.004534 | 0.067552 | 0.067552 | 26.7594 | 7.1041 | 317.9554 | 317.9554 | 119 | 5.6586 | 0.0093486 | 5.6586 | 0.0048429 | 0.067839 | 0.067839 | 28.2758 | 7.3161 | 319.2597 | 319.2597 | 115 | 6.044 | 0.0087524 | 6.044 | 0.004534 | 0.067552 | 0.067552 | 25.5241 | 6.9572 | 316.8669 | 316.8669 | 116 | 5.9465 | 0.008896 | 5.9465 | 0.0046084 | 0.067621 | 0.067621 | 26.3505 | 7.2341 | 317.4164 | 317.4164 | 118 | 5.7538 | 0.009194 | 5.7538 | 0.0047628 | 0.067765 | 0.067765 | 27.8599 | 7.3946 | 318.7653 | 318.7653 | 128 | 4.8362 | 0.010938 | 4.8362 | 0.0056664 | 0.068605 | 0.068605 | 32.7832 | 9.708 | 321.3752 | 321.3752 | 100 | 7.6105 | 0.0069509 | 7.6105 | 0.0036008 | 0.066683 | 0.066683 | 22.9882 | 5.1558 | 316.1324 | 316.1324
LT, (2)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 52.8998 | 60.8348 | 27.4037 | 0.063333 | 298.3 | 0.45046 | 40.54% | 79 | 7.7386 | 0.0068358 | 7.7386 | 0.0035412 | 0.066628 | 0.066628 | 18.7113 | 5.0213 | 311.99 | 311.99 | 106 | 4.9788 | 0.010625 | 4.9788 | 0.0055041 | 0.068454 | 0.068454 | 29.2963 | 7.8619 | 319.7345 | 319.7345 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.0049157 | 0.067907 | 0.067907 | 25.9741 | 7.1381 | 317.136 | 317.136 | 98 | 5.6656 | 0.009337 | 5.6656 | 0.0048369 | 0.067833 | 0.067833 | 26.1729 | 7.1922 | 317.2807 | 317.2807 | 93 | 6.144 | 0.0086101 | 6.144 | 0.0044603 | 0.067483 | 0.067483 | 24.7142 | 6.4953 | 316.519 | 316.519 | 96 | 5.852 | 0.0090397 | 5.852 | 0.0046828 | 0.06769 | 0.06769 | 25.4116 | 7.0551 | 316.6565 | 316.6565 | 93 | 6.144 | 0.0086101 | 6.144 | 0.0044603 | 0.067483 | 0.067483 | 25.0406 | 6.7902 | 316.5504 | 316.5504 | 104 | 5.1424 | 0.010287 | 5.1424 | 0.005329 | 0.068291 | 0.068291 | 30.2311 | 8.0771 | 320.454 | 320.454 | 106 | 4.9788 | 0.010625 | 4.9788 | 0.0055041 | 0.068454 | 0.068454 | 31.0879 | 8.2588 | 321.1292 | 321.1292 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.0058738 | 0.068798 | 0.068798 | 32.8424 | 8.719 | 322.4234 | 322.4234 | 114 | 4.3682 | 0.01211 | 4.3682 | 0.0062735 | 0.06917 | 0.06917 | 34.7008 | 8.9785 | 324.0223 | 324.0223 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.0058738 | 0.068798 | 0.068798 | 31.3262 | 8.5387 | 321.0875 | 321.0875 | 111 | 4.5897 | 0.011526 | 4.5897 | 0.0059707 | 0.068888 | 0.068888 | 32.3433 | 8.8793 | 321.764 | 321.764 | 113 | 4.4411 | 0.011911 | 4.4411 | 0.0061704 | 0.069074 | 0.069074 | 34.1944 | 9.0759 | 323.4185 | 323.4185 | 123 | 3.7435 | 0.014131 | 3.7435 | 0.0073203 | 0.070144 | 0.070144 | 40.1227 | 11.8814 | 326.5413 | 326.5413 | 95 | 5.9476 | 0.0088943 | 5.9476 | 0.0046075 | 0.06762 | 0.06762 | 27.8675 | 6.2502 | 319.9173 | 319.9173
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 93.1299 | 107.0994 | 27.4037 | 0.053833 | 253.555 | 0.25587 | 24.31% | 84 | 9.5174 | 0.0097852 | 9.5174 | 0.0028793 | 0.060739 | 0.060739 | 28.2725 | 2.448 | 279.3795 | 279.3795 | 111 | 6.4426 | 0.014455 | 6.4426 | 0.0042535 | 0.064035 | 0.064035 | 42.0717 | 3.6428 | 291.984 | 291.984 | 104 | 7.1731 | 0.012983 | 7.1731 | 0.0038203 | 0.062996 | 0.062996 | 37.5124 | 3.3262 | 287.7412 | 287.7412 | 103 | 7.2811 | 0.012791 | 7.2811 | 0.0037637 | 0.06286 | 0.06286 | 37.8457 | 3.3555 | 288.0453 | 288.0453 | 98 | 7.8349 | 0.011887 | 7.8349 | 0.0034977 | 0.062222 | 0.062222 | 36.0148 | 3.0539 | 286.5158 | 286.5158 | 101 | 7.4998 | 0.012418 | 7.4998 | 0.0036539 | 0.062597 | 0.062597 | 36.847 | 3.3007 | 287.1013 | 287.1013 | 98 | 7.8349 | 0.011887 | 7.8349 | 0.0034977 | 0.062222 | 0.062222 | 36.4904 | 3.1926 | 286.8528 | 286.8528 | 109 | 6.6469 | 0.014011 | 6.6469 | 0.0041228 | 0.063722 | 0.063722 | 43.4626 | 3.7467 | 293.2709 | 293.2709 | 111 | 6.4426 | 0.014455 | 6.4426 | 0.0042535 | 0.064035 | 0.064035 | 44.6446 | 3.8267 | 294.3729 | 294.3729 | 115 | 6.044 | 0.015409 | 6.044 | 0.004534 | 0.064708 | 0.064708 | 47.1099 | 4.0353 | 296.6296 | 296.6296 | 119 | 5.6586 | 0.016458 | 5.6586 | 0.0048429 | 0.065449 | 0.065449 | 49.7794 | 4.1557 | 299.1787 | 299.1787 | 115 | 6.044 | 0.015409 | 6.044 | 0.004534 | 0.064708 | 0.064708 | 44.935 | 3.9518 | 294.5382 | 294.5382 | 116 | 5.9465 | 0 | 5.9465 | 0.0046084 | 0.049225 | 0.049225 | 0 | 4.1091 | 249.4459 | 249.4459 | 118 | 5.7538 | 0.016186 | 5.7538 | 0.0047628 | 0.065257 | 0.065257 | 49.0472 | 4.2003 | 298.402 | 298.402 | 128 | 4.8362 | 0.019257 | 4.8362 | 0.0056664 | 0.067424 | 0.067424 | 57.7148 | 5.5144 | 305.7554 | 305.7554 | 100 | 7.6105 | 0.012237 | 7.6105 | 0.0036008 | 0.06247 | 0.06247 | 40.4707 | 2.9286 | 291.0971 | 291.0971
LT, (1)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 93.1299 | 107.0994 | 27.4037 | 0.053833 | 253.555 | 0.25587 | 23.03% | 79 | 7.7386 | 0.012034 | 7.7386 | 0.0035412 | 0.062327 | 0.062327 | 32.9412 | 2.8522 | 283.644 | 283.644 | 106 | 4.9788 | 0.018705 | 4.9788 | 0.0055041 | 0.067035 | 0.067035 | 51.5761 | 4.4657 | 300.6654 | 300.6654 | 99 | 5.5748 | 0.016706 | 5.5748 | 0.0049157 | 0.065623 | 0.065623 | 45.7273 | 4.0546 | 295.2277 | 295.2277 | 98 | 5.6656 | 0.016438 | 5.6656 | 0.0048369 | 0.065434 | 0.065434 | 46.0773 | 4.0853 | 295.5469 | 295.5469 | 93 | 6.144 | 0.015158 | 6.144 | 0.0044603 | 0.064531 | 0.064531 | 43.5093 | 3.6895 | 293.3749 | 293.3749 | 96 | 5.852 | 0.015914 | 5.852 | 0.0046828 | 0.065065 | 0.065065 | 44.7371 | 4.0075 | 294.2846 | 294.2846 | 93 | 6.144 | 0.015158 | 6.144 | 0.0044603 | 0.064531 | 0.064531 | 44.0839 | 3.857 | 293.7819 | 293.7819 | 104 | 5.1424 | 0.01811 | 5.1424 | 0.005329 | 0.066615 | 0.066615 | 53.2217 | 4.588 | 302.1888 | 302.1888 | 106 | 4.9788 | 0.018705 | 4.9788 | 0.0055041 | 0.067035 | 0.067035 | 54.7302 | 4.6911 | 303.594 | 303.594 | 110 | 4.6654 | 0.019962 | 4.6654 | 0.0058738 | 0.067921 | 0.067921 | 57.8189 | 4.9526 | 306.4214 | 306.4214 | 114 | 4.3682 | 0.02132 | 4.3682 | 0.0062735 | 0.06888 | 0.06888 | 61.0906 | 5.1 | 309.5456 | 309.5456 | 110 | 4.6654 | 0.019962 | 4.6654 | 0.0058738 | 0.067921 | 0.067921 | 55.1497 | 4.8502 | 303.8545 | 303.8545 | 111 | 4.5897 | 0.020291 | 4.5897 | 0.0059707 | 0.068154 | 0.068154 | 56.9402 | 5.0436 | 305.4516 | 305.4516 | 113 | 4.4411 | 0.02097 | 4.4411 | 0.0061704 | 0.068633 | 0.068633 | 60.1992 | 5.1553 | 308.5989 | 308.5989 | 123 | 3.7435 | 0.024878 | 3.7435 | 0.0073203 | 0.071391 | 0.071391 | 70.6359 | 6.7489 | 317.442 | 317.442 | 95 | 5.9476 | 0.015658 | 5.9476 | 0.0046075 | 0.064884 | 0.064884 | 49.0606 | 3.5502 | 299.0654 | 299.0654
MT, (2)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 37.8942 | 43.5784 | 27.4037 | 0.040333 | 189.97 | 0.62884 | 59.74% | 84 | 9.5174 | 0.0039816 | 9.5174 | 0.0028793 | 0.041436 | 0.041436 | 11.504 | 6.0162 | 195.4578 | 195.4578 | 111 | 6.4426 | 0.0058818 | 6.4426 | 0.0042535 | 0.041962 | 0.041962 | 17.1188 | 8.9526 | 198.1363 | 198.1363 | 104 | 7.1731 | 0.0052828 | 7.1731 | 0.0038203 | 0.041796 | 0.041796 | 15.2636 | 8.1745 | 197.0591 | 197.0591 | 103 | 7.2811 | 0.0052045 | 7.2811 | 0.0037637 | 0.041774 | 0.041774 | 15.3993 | 8.2466 | 197.1227 | 197.1227 | 98 | 7.8349 | 0.0048366 | 7.8349 | 0.0034977 | 0.041672 | 0.041672 | 14.6543 | 7.5054 | 197.1188 | 197.1188 | 101 | 7.4998 | 0.0050527 | 7.4998 | 0.0036539 | 0.041732 | 0.041732 | 14.9929 | 8.1118 | 196.8511 | 196.8511 | 98 | 7.8349 | 0.0048366 | 7.8349 | 0.0034977 | 0.041672 | 0.041672 | 14.8478 | 7.8463 | 196.9716 | 196.9716 | 109 | 6.6469 | 0.005701 | 6.6469 | 0.0041228 | 0.041912 | 0.041912 | 17.6848 | 9.208 | 198.4468 | 198.4468 | 111 | 6.4426 | 0.0058818 | 6.4426 | 0.0042535 | 0.041962 | 0.041962 | 18.1657 | 9.4045 | 198.7312 | 198.7312 | 115 | 6.044 | 0.0062697 | 6.044 | 0.004534 | 0.042069 | 0.042069 | 19.1688 | 9.9172 | 199.2217 | 199.2217 | 119 | 5.6586 | 0.0066968 | 5.6586 | 0.0048429 | 0.042187 | 0.042187 | 20.2551 | 10.2132 | 200.0119 | 200.0119 | 115 | 6.044 | 0.0062697 | 6.044 | 0.004534 | 0.042069 | 0.042069 | 18.2839 | 9.7121 | 198.5418 | 198.5418 | 116 | 5.9465 | 0.0063726 | 5.9465 | 0.0046084 | 0.042097 | 0.042097 | 18.8759 | 10.0987 | 198.7473 | 198.7473 | 118 | 5.7538 | 0.006586 | 5.7538 | 0.0047628 | 0.042157 | 0.042157 | 19.9572 | 10.3227 | 199.6044 | 199.6044 | 128 | 4.8362 | 0.0078356 | 4.8362 | 0.0056664 | 0.042503 | 0.042503 | 23.4839 | 13.5522 | 199.9017 | 199.9017 | 100 | 7.6105 | 0.0049792 | 7.6105 | 0.0036008 | 0.041712 | 0.041712 | 16.4674 | 7.1975 | 199.2399 | 199.2399
LT, (2)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 37.8942 | 43.5784 | 27.4037 | 0.040333 | 189.97 | 0.62884 | 56.6% | 79 | 7.7386 | 0.0048968 | 7.7386 | 0.0035412 | 0.041689 | 0.041689 | 13.4036 | 7.0097 | 196.364 | 196.364 | 106 | 4.9788 | 0.0076112 | 4.9788 | 0.0055041 | 0.04244 | 0.04244 | 20.9861 | 10.975 | 199.9811 | 199.9811 | 99 | 5.5748 | 0.0067974 | 5.5748 | 0.0049157 | 0.042215 | 0.042215 | 18.6063 | 9.9647 | 198.6116 | 198.6116 | 98 | 5.6656 | 0.0066885 | 5.6656 | 0.0048369 | 0.042185 | 0.042185 | 18.7487 | 10.0402 | 198.6785 | 198.6785 | 93 | 6.144 | 0.0061677 | 6.144 | 0.0044603 | 0.042041 | 0.042041 | 17.7038 | 9.0673 | 198.6065 | 198.6065 | 96 | 5.852 | 0.0064755 | 5.852 | 0.0046828 | 0.042126 | 0.042126 | 18.2034 | 9.8488 | 198.3245 | 198.3245 | 93 | 6.144 | 0.0061677 | 6.144 | 0.0044603 | 0.042041 | 0.042041 | 17.9376 | 9.479 | 198.4286 | 198.4286 | 104 | 5.1424 | 0.007369 | 5.1424 | 0.005329 | 0.042373 | 0.042373 | 21.6557 | 11.2756 | 200.3502 | 200.3502 | 106 | 4.9788 | 0.0076112 | 4.9788 | 0.0055041 | 0.04244 | 0.04244 | 22.2695 | 11.5291 | 200.7104 | 200.7104 | 110 | 4.6654 | 0.0081224 | 4.6654 | 0.0058738 | 0.042582 | 0.042582 | 23.5263 | 12.1716 | 201.3248 | 201.3248 | 114 | 4.3682 | 0.008675 | 4.3682 | 0.0062735 | 0.042735 | 0.042735 | 24.8576 | 12.5339 | 202.2937 | 202.2937 | 110 | 4.6654 | 0.0081224 | 4.6654 | 0.0058738 | 0.042582 | 0.042582 | 22.4402 | 11.9199 | 200.4903 | 200.4903 | 111 | 4.5897 | 0.0082564 | 4.5897 | 0.0059707 | 0.042619 | 0.042619 | 23.1688 | 12.3954 | 200.7434 | 200.7434 | 113 | 4.4411 | 0.0085325 | 4.4411 | 0.0061704 | 0.042695 | 0.042695 | 24.4948 | 12.6698 | 201.795 | 201.795 | 123 | 3.7435 | 0.010123 | 3.7435 | 0.0073203 | 0.043136 | 0.043136 | 28.7415 | 16.5863 | 202.1252 | 202.1252 | 95 | 5.9476 | 0.0063714 | 5.9476 | 0.0046075 | 0.042097 | 0.042097 | 19.9626 | 8.7252 | 201.2074 | 201.2074
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 38.0621 | 43.7714 | 27.4037 | 0.010833 | 51.025 | 0.62607 | 59.48% | 84 | 9.5174 | 0.0039992 | 9.5174 | 0.0028793 | 0.011953 | 0.011953 | 11.5549 | 5.9897 | 56.5903 | 56.5903 | 111 | 6.4426 | 0.0059079 | 6.4426 | 0.0042535 | 0.012488 | 0.012488 | 17.1947 | 8.9131 | 59.3066 | 59.3066 | 104 | 7.1731 | 0.0053062 | 7.1731 | 0.0038203 | 0.012319 | 0.012319 | 15.3312 | 8.1385 | 58.2178 | 58.2178 | 103 | 7.2811 | 0.0052275 | 7.2811 | 0.0037637 | 0.012297 | 0.012297 | 15.4675 | 8.2102 | 58.2823 | 58.2823 | 98 | 7.8349 | 0.004858 | 7.8349 | 0.0034977 | 0.012194 | 0.012194 | 14.7192 | 7.4724 | 58.2718 | 58.2718 | 101 | 7.4998 | 0.0050751 | 7.4998 | 0.0036539 | 0.012254 | 0.012254 | 15.0593 | 8.0761 | 58.0082 | 58.0082 | 98 | 7.8349 | 0.004858 | 7.8349 | 0.0034977 | 0.012194 | 0.012194 | 14.9136 | 7.8117 | 58.1269 | 58.1269 | 109 | 6.6469 | 0.0057263 | 6.6469 | 0.0041228 | 0.012437 | 0.012437 | 17.7631 | 9.1674 | 59.6207 | 59.6207 | 111 | 6.4426 | 0.0059079 | 6.4426 | 0.0042535 | 0.012488 | 0.012488 | 18.2462 | 9.3631 | 59.9081 | 59.9081 | 115 | 6.044 | 0.0062974 | 6.044 | 0.004534 | 0.012597 | 0.012597 | 19.2537 | 9.8734 | 60.4053 | 60.4053 | 119 | 5.6586 | 0.0067264 | 5.6586 | 0.0048429 | 0.012717 | 0.012717 | 20.3448 | 10.1682 | 61.2016 | 61.2016 | 115 | 6.044 | 0.0062974 | 6.044 | 0.004534 | 0.012597 | 0.012597 | 18.3649 | 9.6693 | 59.7206 | 59.7206 | 116 | 5.9465 | 0.0064008 | 5.9465 | 0.0046084 | 0.012626 | 0.012626 | 18.9595 | 10.0541 | 59.9304 | 59.9304 | 118 | 5.7538 | 0.0066152 | 5.7538 | 0.0047628 | 0.012686 | 0.012686 | 20.0455 | 10.2772 | 60.7933 | 60.7933 | 128 | 4.8362 | 0.0078703 | 4.8362 | 0.0056664 | 0.013037 | 0.013037 | 23.5879 | 13.4925 | 61.1205 | 61.1205 | 100 | 7.6105 | 0.0050012 | 7.6105 | 0.0036008 | 0.012234 | 0.012234 | 16.5403 | 7.1658 | 60.3996 | 60.3996
LT, (1)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 38.0621 | 43.7714 | 27.4037 | 0.010833 | 51.025 | 0.62607 | 56.35% | 79 | 7.7386 | 0.0049185 | 7.7386 | 0.0035412 | 0.012211 | 0.012211 | 13.463 | 6.9787 | 57.5093 | 57.5093 | 106 | 4.9788 | 0.0076449 | 4.9788 | 0.0055041 | 0.012974 | 0.012974 | 21.0791 | 10.9266 | 61.1774 | 61.1774 | 99 | 5.5748 | 0.0068275 | 5.5748 | 0.0049157 | 0.012745 | 0.012745 | 18.6887 | 9.9207 | 59.7929 | 59.7929 | 98 | 5.6656 | 0.0067181 | 5.6656 | 0.0048369 | 0.012715 | 0.012715 | 18.8317 | 9.9959 | 59.8608 | 59.8608 | 93 | 6.144 | 0.006195 | 6.144 | 0.0044603 | 0.012568 | 0.012568 | 17.7822 | 9.0273 | 59.7799 | 59.7799 | 96 | 5.852 | 0.0065042 | 5.852 | 0.0046828 | 0.012655 | 0.012655 | 18.284 | 9.8054 | 59.5036 | 59.5036 | 93 | 6.144 | 0.006195 | 6.144 | 0.0044603 | 0.012568 | 0.012568 | 18.017 | 9.4372 | 59.6048 | 59.6048 | 104 | 5.1424 | 0.0074016 | 5.1424 | 0.005329 | 0.012906 | 0.012906 | 21.7516 | 11.2259 | 61.5508 | 61.5508 | 106 | 4.9788 | 0.0076449 | 4.9788 | 0.0055041 | 0.012974 | 0.012974 | 22.3681 | 11.4783 | 61.9149 | 61.9149 | 110 | 4.6654 | 0.0081584 | 4.6654 | 0.0058738 | 0.013118 | 0.013118 | 23.6305 | 12.1179 | 62.5376 | 62.5376 | 114 | 4.3682 | 0.0087134 | 4.3682 | 0.0062735 | 0.013273 | 0.013273 | 24.9677 | 12.4787 | 63.514 | 63.514 | 110 | 4.6654 | 0.0081584 | 4.6654 | 0.0058738 | 0.013118 | 0.013118 | 22.5396 | 11.8673 | 61.6973 | 61.6973 | 111 | 4.5897 | 0.0082929 | 4.5897 | 0.0059707 | 0.013156 | 0.013156 | 23.2714 | 12.3407 | 61.9557 | 61.9557 | 113 | 4.4411 | 0.0085703 | 4.4411 | 0.0061704 | 0.013233 | 0.013233 | 24.6033 | 12.614 | 63.0144 | 63.0144 | 123 | 3.7435 | 0.010167 | 3.7435 | 0.0073203 | 0.01368 | 0.01368 | 28.8688 | 16.5132 | 63.3806 | 63.3806 | 95 | 5.9476 | 0.0063996 | 5.9476 | 0.0046075 | 0.012625 | 0.012625 | 20.051 | 8.6867 | 62.3893 | 62.3893
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T12 to CC retrofit | /Fixture | 1 | 38 | 28 | 52.8998 | 60.8348 | 70.9563 | 0.0424 | 126.048 | 1.1664 | 110.8% | 84 | 9.5174 | 0.0055582 | 9.5174 | 0.0074554 | 0.040503 | 0.040503 | 16.0594 | 28.8937 | 113.2137 | 113.2137 | 111 | 6.4426 | 0.008211 | 6.4426 | 0.011014 | 0.039597 | 0.039597 | 23.8977 | 42.9961 | 106.9496 | 106.9496 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | 0.039883 | 0.039883 | 21.3078 | 39.2593 | 108.0965 | 108.0965 | 103 | 7.2811 | 0.0072654 | 7.2811 | 0.0097453 | 0.03992 | 0.03992 | 21.4972 | 39.6053 | 107.9399 | 107.9399 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0090565 | 0.040095 | 0.040095 | 20.4572 | 36.046 | 110.4592 | 110.4592 | 99 | 7.7222 | 0.0068504 | 7.7222 | 0.0091886 | 0.040062 | 0.040062 | 20.327 | 37.8361 | 108.5389 | 108.5389 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0090565 | 0.040095 | 0.040095 | 20.7273 | 37.6829 | 109.0925 | 109.0925 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | 0.039883 | 0.039883 | 22.8766 | 40.9786 | 107.946 | 107.946 | 109 | 6.6469 | 0.0079585 | 6.6469 | 0.010675 | 0.039683 | 0.039683 | 24.5795 | 43.7782 | 106.8493 | 106.8493 | 115 | 6.044 | 0.0087524 | 6.044 | 0.01174 | 0.039413 | 0.039413 | 26.7594 | 47.6287 | 105.1787 | 105.1787 | 119 | 5.6586 | 0.0093486 | 5.6586 | 0.01254 | 0.039209 | 0.039209 | 28.2758 | 49.0505 | 105.2734 | 105.2734 | 115 | 6.044 | 0.0087524 | 6.044 | 0.01174 | 0.039413 | 0.039413 | 25.5241 | 46.6438 | 104.9282 | 104.9282 | 116 | 5.9465 | 0.008896 | 5.9465 | 0.011932 | 0.039364 | 0.039364 | 26.3505 | 48.5003 | 103.8982 | 103.8982 | 123 | 5.2856 | 0.010008 | 5.2856 | 0.013424 | 0.038984 | 0.038984 | 30.3273 | 53.9672 | 102.4081 | 102.4081 | 126 | 5.0138 | 0.010551 | 5.0138 | 0.014152 | 0.038799 | 0.038799 | 31.6219 | 62.7809 | 94.889 | 94.889 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | 0.039883 | 0.039883 | 24.3899 | 36.6747 | 113.7632 | 113.7632
LT, T12 to CC retrofit | /Fixture | 1 | 0 | -10 | 52.8998 | 60.8348 | 70.9563 | 0.0424 | 126.048 | 1.1664 | 105% | 79 | 7.7386 | 0.0068358 | 7.7386 | 0.0091691 | 0.040067 | 0.040067 | 18.7113 | 33.6649 | 111.0944 | 111.0944 | 106 | 4.9788 | 0.010625 | 4.9788 | 0.014252 | 0.038773 | 0.038773 | 29.2963 | 52.7092 | 102.6351 | 102.6351 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | 0.039161 | 0.039161 | 25.9741 | 47.8568 | 104.1653 | 104.1653 | 98 | 5.6656 | 0.009337 | 5.6656 | 0.012524 | 0.039213 | 0.039213 | 26.1729 | 48.2196 | 104.0013 | 104.0013 | 93 | 6.144 | 0.0086101 | 6.144 | 0.011549 | 0.039461 | 0.039461 | 24.7142 | 43.5471 | 107.2152 | 107.2152 | 94 | 6.0449 | 0.0087511 | 6.0449 | 0.011738 | 0.039413 | 0.039413 | 24.6005 | 45.7907 | 104.8578 | 104.8578 | 93 | 6.144 | 0.0086101 | 6.144 | 0.011549 | 0.039461 | 0.039461 | 25.0406 | 45.5245 | 105.5641 | 105.5641 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | 0.039161 | 0.039161 | 27.8864 | 49.9526 | 103.9818 | 103.9818 | 104 | 5.1424 | 0.010287 | 5.1424 | 0.013798 | 0.038889 | 0.038889 | 30.0986 | 53.6081 | 102.5385 | 102.5385 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.015209 | 0.03853 | 0.03853 | 32.8424 | 58.4557 | 100.4347 | 100.4347 | 114 | 4.3682 | 0.01211 | 4.3682 | 0.016244 | 0.038266 | 0.038266 | 34.7008 | 60.196 | 100.5528 | 100.5528 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.015209 | 0.03853 | 0.03853 | 31.3262 | 57.247 | 100.1272 | 100.1272 | 111 | 4.5897 | 0.011526 | 4.5897 | 0.01546 | 0.038466 | 0.038466 | 32.3433 | 59.5305 | 98.8607 | 98.8607 | 118 | 4.0843 | 0.012952 | 4.0843 | 0.017373 | 0.037979 | 0.037979 | 37.1824 | 66.1657 | 97.0647 | 97.0647 | 121 | 3.8782 | 0.01364 | 3.8782 | 0.018296 | 0.037744 | 0.037744 | 38.729 | 76.8912 | 87.8858 | 87.8858 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | 0.039161 | 0.039161 | 29.7311 | 44.7062 | 111.073 | 111.073
| /Fixture | [13 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T8 Baseline) | /Fixture
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Shelf | /Fixture | 1 | 38 | 28 | 93.1299 | 107.0994 | 14.0934 | 0.0629 | 296.259 | 0.13159 | 12.5% | 84 | 9.5174 | 0.0097852 | 9.5174 | 0.0014808 | 0.071204 | 0.071204 | 28.2725 | 0.64746 | 323.884 | 323.884 | 111 | 6.4426 | 0.014455 | 6.4426 | 0.0021875 | 0.075168 | 0.075168 | 42.0717 | 0.96348 | 337.3673 | 337.3673 | 104 | 7.1731 | 0.012983 | 7.1731 | 0.0019647 | 0.073918 | 0.073918 | 37.5124 | 0.87974 | 332.8916 | 332.8916 | 103 | 7.2811 | 0.012791 | 7.2811 | 0.0019356 | 0.073755 | 0.073755 | 37.8457 | 0.88749 | 333.2173 | 333.2173 | 98 | 7.8349 | 0.011887 | 7.8349 | 0.0017988 | 0.072988 | 0.072988 | 36.0148 | 0.80774 | 331.466 | 331.466 | 101 | 7.4998 | 0.012418 | 7.4998 | 0.0018792 | 0.073439 | 0.073439 | 36.847 | 0.873 | 332.233 | 332.233 | 98 | 7.8349 | 0.011887 | 7.8349 | 0.0017988 | 0.072988 | 0.072988 | 36.4904 | 0.84441 | 331.905 | 331.905 | 109 | 6.6469 | 0.014011 | 6.6469 | 0.0021203 | 0.074791 | 0.074791 | 43.4626 | 0.99097 | 338.7307 | 338.7307 | 111 | 6.4426 | 0.014455 | 6.4426 | 0.0021875 | 0.075168 | 0.075168 | 44.6446 | 1.0121 | 339.8915 | 339.8915 | 115 | 6.044 | 0.015409 | 6.044 | 0.0023318 | 0.075977 | 0.075977 | 47.1099 | 1.0673 | 342.3016 | 342.3016 | 119 | 5.6586 | 0.016458 | 5.6586 | 0.0024906 | 0.076868 | 0.076868 | 49.7794 | 1.0991 | 344.9393 | 344.9393 | 115 | 6.044 | 0.015409 | 6.044 | 0.0023318 | 0.075977 | 0.075977 | 44.935 | 1.0452 | 340.1488 | 340.1488 | 116 | 5.9465 | 0.015661 | 5.9465 | 0.00237 | 0.076191 | 0.076191 | 46.3899 | 1.0868 | 341.5621 | 341.5621 | 118 | 5.7538 | 0.016186 | 5.7538 | 0.0024494 | 0.076637 | 0.076637 | 49.0472 | 1.1109 | 344.1953 | 344.1953 | 128 | 4.8362 | 0.019257 | 4.8362 | 0.0029142 | 0.079243 | 0.079243 | 57.7148 | 1.4585 | 352.5153 | 352.5153 | 100 | 7.6105 | 0.012237 | 7.6105 | 0.0018518 | 0.073285 | 0.073285 | 40.4707 | 0.77459 | 335.9551 | 335.9551
LT, (1)T12 to LED Shelf | /Fixture | 1 | 0 | -10 | 93.1299 | 107.0994 | 14.0934 | 0.0629 | 296.259 | 0.13159 | 11.84% | 79 | 7.7386 | 0.012034 | 7.7386 | 0.0018212 | 0.073113 | 0.073113 | 32.9412 | 0.75438 | 328.4458 | 328.4458 | 106 | 4.9788 | 0.018705 | 4.9788 | 0.0028307 | 0.078775 | 0.078775 | 51.5761 | 1.1811 | 346.6539 | 346.6539 | 99 | 5.5748 | 0.016706 | 5.5748 | 0.0025281 | 0.077078 | 0.077078 | 45.7273 | 1.0724 | 340.9139 | 340.9139 | 98 | 5.6656 | 0.016438 | 5.6656 | 0.0024875 | 0.07685 | 0.07685 | 46.0773 | 1.0805 | 341.2557 | 341.2557 | 93 | 6.144 | 0.015158 | 6.144 | 0.0022939 | 0.075764 | 0.075764 | 43.5093 | 0.97582 | 338.7925 | 338.7925 | 96 | 5.852 | 0.015914 | 5.852 | 0.0024083 | 0.076406 | 0.076406 | 44.7371 | 1.0599 | 339.9361 | 339.9361 | 93 | 6.144 | 0.015158 | 6.144 | 0.0022939 | 0.075764 | 0.075764 | 44.0839 | 1.0201 | 339.3228 | 339.3228 | 104 | 5.1424 | 0.01811 | 5.1424 | 0.0027406 | 0.07827 | 0.07827 | 53.2217 | 1.2135 | 348.2673 | 348.2673 | 106 | 4.9788 | 0.018705 | 4.9788 | 0.0028307 | 0.078775 | 0.078775 | 54.7302 | 1.2408 | 349.7484 | 349.7484 | 110 | 4.6654 | 0.019962 | 4.6654 | 0.0030208 | 0.079841 | 0.079841 | 57.8189 | 1.3099 | 352.768 | 352.768 | 114 | 4.3682 | 0.02132 | 4.3682 | 0.0032264 | 0.080994 | 0.080994 | 61.0906 | 1.3489 | 356.0007 | 356.0007 | 110 | 4.6654 | 0.019962 | 4.6654 | 0.0030208 | 0.079841 | 0.079841 | 55.1497 | 1.2828 | 350.1259 | 350.1259 | 111 | 4.5897 | 0.020291 | 4.5897 | 0.0030707 | 0.08012 | 0.08012 | 56.9402 | 1.334 | 351.8652 | 351.8652 | 113 | 4.4411 | 0.02097 | 4.4411 | 0.0031734 | 0.080696 | 0.080696 | 60.1992 | 1.3635 | 355.0947 | 355.0947 | 123 | 3.7435 | 0.024878 | 3.7435 | 0.0037647 | 0.084013 | 0.084013 | 70.6359 | 1.785 | 365.1099 | 365.1099 | 95 | 5.9476 | 0.015658 | 5.9476 | 0.0023696 | 0.076189 | 0.076189 | 49.0606 | 0.939 | 344.3806 | 344.3806
MT, (1)T8 to LED Shelf | /Fixture | 1 | 38 | 28 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 30.59% | 84 | 9.5174 | 0.0039992 | 9.5174 | 0.0014808 | 0.022418 | 0.022418 | 11.5549 | 1.5842 | 103.6997 | 103.6997 | 111 | 6.4426 | 0.0059079 | 6.4426 | 0.0021875 | 0.02362 | 0.02362 | 17.1947 | 2.3574 | 108.5662 | 108.5662 | 104 | 7.1731 | 0.0053062 | 7.1731 | 0.0019647 | 0.023241 | 0.023241 | 15.3312 | 2.1525 | 106.9077 | 106.9077 | 103 | 7.2811 | 0.0052275 | 7.2811 | 0.0019356 | 0.023192 | 0.023192 | 15.4675 | 2.1715 | 107.025 | 107.025 | 98 | 7.8349 | 0.004858 | 7.8349 | 0.0017988 | 0.022959 | 0.022959 | 14.7192 | 1.9764 | 106.4718 | 106.4718 | 101 | 7.4998 | 0.0050751 | 7.4998 | 0.0018792 | 0.023096 | 0.023096 | 15.0593 | 2.136 | 106.6523 | 106.6523 | 98 | 7.8349 | 0.004858 | 7.8349 | 0.0017988 | 0.022959 | 0.022959 | 14.9136 | 2.0661 | 106.5765 | 106.5765 | 109 | 6.6469 | 0.0057263 | 6.6469 | 0.0021203 | 0.023506 | 0.023506 | 17.7631 | 2.4247 | 109.0674 | 109.0674 | 111 | 6.4426 | 0.0059079 | 6.4426 | 0.0021875 | 0.02362 | 0.02362 | 18.2462 | 2.4764 | 109.4987 | 109.4987 | 115 | 6.044 | 0.0062974 | 6.044 | 0.0023318 | 0.023866 | 0.023866 | 19.2537 | 2.6114 | 110.3713 | 110.3713 | 119 | 5.6586 | 0.0067264 | 5.6586 | 0.0024906 | 0.024136 | 0.024136 | 20.3448 | 2.6894 | 111.3844 | 111.3844 | 115 | 6.044 | 0.0062974 | 6.044 | 0.0023318 | 0.023866 | 0.023866 | 18.3649 | 2.5574 | 109.5364 | 109.5364 | 116 | 5.9465 | 0.0064008 | 5.9465 | 0.00237 | 0.023931 | 0.023931 | 18.9595 | 2.6592 | 110.0293 | 110.0293 | 118 | 5.7538 | 0.0066152 | 5.7538 | 0.0024494 | 0.024066 | 0.024066 | 20.0455 | 2.7182 | 111.0563 | 111.0563 | 128 | 4.8362 | 0.0078703 | 4.8362 | 0.0029142 | 0.024856 | 0.024856 | 23.5879 | 3.5686 | 113.7483 | 113.7483 | 100 | 7.6105 | 0.0050012 | 7.6105 | 0.0018518 | 0.023049 | 0.023049 | 16.5403 | 1.8953 | 108.3741 | 108.3741
LT, (1)T8 to LED Shelf | /Fixture | 1 | 0 | -10 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 28.98% | 79 | 7.7386 | 0.0049185 | 7.7386 | 0.0018212 | 0.022997 | 0.022997 | 13.463 | 1.8458 | 105.3462 | 105.3462 | 106 | 4.9788 | 0.0076449 | 4.9788 | 0.0028307 | 0.024714 | 0.024714 | 21.0791 | 2.89 | 111.9181 | 111.9181 | 99 | 5.5748 | 0.0068275 | 5.5748 | 0.0025281 | 0.024199 | 0.024199 | 18.6887 | 2.6239 | 109.7937 | 109.7937 | 98 | 5.6656 | 0.0067181 | 5.6656 | 0.0024875 | 0.024131 | 0.024131 | 18.8317 | 2.6438 | 109.9169 | 109.9169 | 93 | 6.144 | 0.006195 | 6.144 | 0.0022939 | 0.023801 | 0.023801 | 17.7822 | 2.3876 | 109.1236 | 109.1236 | 96 | 5.852 | 0.0065042 | 5.852 | 0.0024083 | 0.023996 | 0.023996 | 18.284 | 2.5934 | 109.4195 | 109.4195 | 93 | 6.144 | 0.006195 | 6.144 | 0.0022939 | 0.023801 | 0.023801 | 18.017 | 2.4961 | 109.25 | 109.25 | 104 | 5.1424 | 0.0074016 | 5.1424 | 0.0027406 | 0.024561 | 0.024561 | 21.7516 | 2.9691 | 112.5115 | 112.5115 | 106 | 4.9788 | 0.0076449 | 4.9788 | 0.0028307 | 0.024714 | 0.024714 | 22.3681 | 3.0359 | 113.0613 | 113.0613 | 110 | 4.6654 | 0.0081584 | 4.6654 | 0.0030208 | 0.025038 | 0.025038 | 23.6305 | 3.2051 | 114.1545 | 114.1545 | 114 | 4.3682 | 0.0087134 | 4.3682 | 0.0032264 | 0.025387 | 0.025387 | 24.9677 | 3.3005 | 115.3962 | 115.3962 | 110 | 4.6654 | 0.0081584 | 4.6654 | 0.0030208 | 0.025038 | 0.025038 | 22.5396 | 3.1388 | 113.1298 | 113.1298 | 111 | 4.5897 | 0.0082929 | 4.5897 | 0.0030707 | 0.025122 | 0.025122 | 23.2714 | 3.264 | 113.7364 | 113.7364 | 113 | 4.4411 | 0.0085703 | 4.4411 | 0.0031734 | 0.025297 | 0.025297 | 24.6033 | 3.3363 | 114.9961 | 114.9961 | 123 | 3.7435 | 0.010167 | 3.7435 | 0.0037647 | 0.026303 | 0.026303 | 28.8688 | 4.3676 | 118.2302 | 118.2302 | 95 | 5.9476 | 0.0063996 | 5.9476 | 0.0023696 | 0.02393 | 0.02393 | 20.051 | 2.2975 | 111.4825 | 111.4825
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to FO retrofit | /Door | 1 | 38 | 28 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 30.59% | 84 | 9.5174 | 0.0055582 | 9.5174 | 0.0014808 | 0.023977 | 0.023977 | 16.0594 | 1.5842 | 108.2042 | 108.2042 | 111 | 6.4426 | 0.008211 | 6.4426 | 0.0021875 | 0.025923 | 0.025923 | 23.8977 | 2.3574 | 115.2692 | 115.2692 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0019647 | 0.02531 | 0.02531 | 21.3078 | 2.1525 | 112.8843 | 112.8843 | 103 | 7.2811 | 0.0072654 | 7.2811 | 0.0019356 | 0.02523 | 0.02523 | 21.4972 | 2.1715 | 113.0547 | 113.0547 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0017988 | 0.024853 | 0.024853 | 20.4572 | 1.9764 | 112.2098 | 112.2098 | 99 | 7.7222 | 0.0068504 | 7.7222 | 0.001825 | 0.024925 | 0.024925 | 20.327 | 2.0745 | 111.9815 | 111.9815 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0017988 | 0.024853 | 0.024853 | 20.7273 | 2.0661 | 112.3902 | 112.3902 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0019647 | 0.02531 | 0.02531 | 22.8766 | 2.2468 | 114.3588 | 114.3588 | 109 | 6.6469 | 0.0079585 | 6.6469 | 0.0021203 | 0.025738 | 0.025738 | 24.5795 | 2.4003 | 115.9082 | 115.9082 | 115 | 6.044 | 0.0087524 | 6.044 | 0.0023318 | 0.026321 | 0.026321 | 26.7594 | 2.6114 | 117.877 | 117.877 | 119 | 5.6586 | 0.0093486 | 5.6586 | 0.0024906 | 0.026758 | 0.026758 | 28.2758 | 2.6894 | 119.3154 | 119.3154 | 115 | 6.044 | 0.0087524 | 6.044 | 0.0023318 | 0.026321 | 0.026321 | 25.5241 | 2.5574 | 116.6956 | 116.6956 | 116 | 5.9465 | 0.008896 | 5.9465 | 0.00237 | 0.026426 | 0.026426 | 26.3505 | 2.6592 | 117.4203 | 117.4203 | 123 | 5.2856 | 0.010008 | 5.2856 | 0.0026664 | 0.027242 | 0.027242 | 30.3273 | 2.959 | 121.0974 | 121.0974 | 126 | 5.0138 | 0.010551 | 5.0138 | 0.0028109 | 0.02764 | 0.02764 | 31.6219 | 3.4422 | 121.9087 | 121.9087 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0019647 | 0.02531 | 0.02531 | 24.3899 | 2.0108 | 116.1081 | 116.1081
LT, T8 to FO retrofit | /Door | 1 | 0 | -10 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 28.98% | 79 | 7.7386 | 0.0068358 | 7.7386 | 0.0018212 | 0.024915 | 0.024915 | 18.7113 | 1.8458 | 110.5945 | 110.5945 | 106 | 4.9788 | 0.010625 | 4.9788 | 0.0028307 | 0.027694 | 0.027694 | 29.2963 | 2.89 | 120.1353 | 120.1353 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.0025281 | 0.026861 | 0.026861 | 25.9741 | 2.6239 | 117.0791 | 117.0791 | 98 | 5.6656 | 0.009337 | 5.6656 | 0.0024875 | 0.026749 | 0.026749 | 26.1729 | 2.6438 | 117.2581 | 117.2581 | 93 | 6.144 | 0.0086101 | 6.144 | 0.0022939 | 0.026216 | 0.026216 | 24.7142 | 2.3876 | 116.0556 | 116.0556 | 94 | 6.0449 | 0.0087511 | 6.0449 | 0.0023314 | 0.02632 | 0.02632 | 24.6005 | 2.5107 | 115.8189 | 115.8189 | 93 | 6.144 | 0.0086101 | 6.144 | 0.0022939 | 0.026216 | 0.026216 | 25.0406 | 2.4961 | 116.2736 | 116.2736 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.0025281 | 0.026861 | 0.026861 | 27.8864 | 2.7388 | 118.8766 | 118.8766 | 104 | 5.1424 | 0.010287 | 5.1424 | 0.0027406 | 0.027446 | 0.027446 | 30.0986 | 2.9393 | 120.8883 | 120.8883 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.0030208 | 0.028218 | 0.028218 | 32.8424 | 3.2051 | 123.3664 | 123.3664 | 114 | 4.3682 | 0.01211 | 4.3682 | 0.0032264 | 0.028784 | 0.028784 | 34.7008 | 3.3005 | 125.1293 | 125.1293 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.0030208 | 0.028218 | 0.028218 | 31.3262 | 3.1388 | 121.9164 | 121.9164 | 111 | 4.5897 | 0.011526 | 4.5897 | 0.0030707 | 0.028355 | 0.028355 | 32.3433 | 3.264 | 122.8083 | 122.8083 | 118 | 4.0843 | 0.012952 | 4.0843 | 0.0034507 | 0.029401 | 0.029401 | 37.1824 | 3.6278 | 127.2836 | 127.2836 | 121 | 3.8782 | 0.01364 | 3.8782 | 0.003634 | 0.029906 | 0.029906 | 38.729 | 4.2159 | 128.2422 | 128.2422 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.0025281 | 0.026861 | 0.026861 | 29.7311 | 2.4512 | 121.0089 | 121.0089
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to CC retrofit | /Door | 1 | 38 | 28 | 38.0621 | 43.7714 | 70.9563 | -0.0101 | -121.227 | 1.6211 | 154% | 84 | 9.5174 | 0.0055582 | 9.5174 | 0.0074554 | -0.011997 | -0.011997 | 16.0594 | 40.1573 | -145.3249 | -145.3249 | 111 | 6.4426 | 0.008211 | 6.4426 | 0.011014 | -0.012903 | -0.012903 | 23.8977 | 59.7573 | -157.0866 | -157.0866 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | -0.012617 | -0.012617 | 21.3078 | 54.5638 | -154.4829 | -154.4829 | 103 | 7.2811 | 0.0072654 | 7.2811 | 0.0097453 | -0.01258 | -0.01258 | 21.4972 | 55.0447 | -154.7745 | -154.7745 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0090565 | -0.012405 | -0.012405 | 20.4572 | 50.0979 | -150.8677 | -150.8677 | 99 | 7.7222 | 0.0068504 | 7.7222 | 0.0091886 | -0.012438 | -0.012438 | 20.327 | 52.5858 | -153.4858 | -153.4858 | 98 | 7.8349 | 0.0067519 | 7.8349 | 0.0090565 | -0.012405 | -0.012405 | 20.7273 | 52.3728 | -152.8724 | -152.8724 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | -0.012617 | -0.012617 | 22.8766 | 56.9533 | -155.3037 | -155.3037 | 109 | 6.6469 | 0.0079585 | 6.6469 | 0.010675 | -0.012817 | -0.012817 | 24.5795 | 60.8442 | -157.4917 | -157.4917 | 115 | 6.044 | 0.0087524 | 6.044 | 0.01174 | -0.013087 | -0.013087 | 26.7594 | 66.1958 | -160.6634 | -160.6634 | 119 | 5.6586 | 0.0093486 | 5.6586 | 0.01254 | -0.013291 | -0.013291 | 28.2758 | 68.1718 | -161.123 | -161.123 | 115 | 6.044 | 0.0087524 | 6.044 | 0.01174 | -0.013087 | -0.013087 | 25.5241 | 64.827 | -160.53 | -160.53 | 116 | 5.9465 | 0.008896 | 5.9465 | 0.011932 | -0.013136 | -0.013136 | 26.3505 | 67.4072 | -162.2837 | -162.2837 | 123 | 5.2856 | 0.010008 | 5.2856 | 0.013424 | -0.013516 | -0.013516 | 30.3273 | 75.0053 | -165.9049 | -165.9049 | 126 | 5.0138 | 0.010551 | 5.0138 | 0.014152 | -0.013701 | -0.013701 | 31.6219 | 87.2548 | -176.8599 | -176.8599 | 104 | 7.1731 | 0.0073747 | 7.1731 | 0.0098919 | -0.012617 | -0.012617 | 24.3899 | 50.9716 | -147.8087 | -147.8087
LT, T8 to CC retrofit | /Door | 1 | 0 | -10 | 38.0621 | 43.7714 | 70.9563 | -0.0101 | -121.227 | 1.6211 | 145.9% | 79 | 7.7386 | 0.0068358 | 7.7386 | 0.0091691 | -0.012433 | -0.012433 | 18.7113 | 46.7885 | -149.3042 | -149.3042 | 106 | 4.9788 | 0.010625 | 4.9788 | 0.014252 | -0.013727 | -0.013727 | 29.2963 | 73.2569 | -165.1876 | -165.1876 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | -0.013339 | -0.013339 | 25.9741 | 66.5128 | -161.7657 | -161.7657 | 98 | 5.6656 | 0.009337 | 5.6656 | 0.012524 | -0.013287 | -0.013287 | 26.1729 | 67.017 | -162.0711 | -162.0711 | 93 | 6.144 | 0.0086101 | 6.144 | 0.011549 | -0.013039 | -0.013039 | 24.7142 | 60.523 | -157.0358 | -157.0358 | 94 | 6.0449 | 0.0087511 | 6.0449 | 0.011738 | -0.013087 | -0.013087 | 24.6005 | 63.6414 | -160.2678 | -160.2678 | 93 | 6.144 | 0.0086101 | 6.144 | 0.011549 | -0.013039 | -0.013039 | 25.0406 | 63.2714 | -159.4577 | -159.4577 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | -0.013339 | -0.013339 | 27.8864 | 69.4257 | -162.7662 | -162.7662 | 104 | 5.1424 | 0.010287 | 5.1424 | 0.013798 | -0.013611 | -0.013611 | 30.0986 | 74.5062 | -165.6346 | -165.6346 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.015209 | -0.01397 | -0.01397 | 32.8424 | 81.2435 | -169.6281 | -169.6281 | 114 | 4.3682 | 0.01211 | 4.3682 | 0.016244 | -0.014234 | -0.014234 | 34.7008 | 83.6622 | -170.1884 | -170.1884 | 110 | 4.6654 | 0.011339 | 4.6654 | 0.015209 | -0.01397 | -0.01397 | 31.3262 | 79.5636 | -169.4644 | -169.4644 | 111 | 4.5897 | 0.011526 | 4.5897 | 0.01546 | -0.014034 | -0.014034 | 32.3433 | 82.7374 | -171.6211 | -171.6211 | 118 | 4.0843 | 0.012952 | 4.0843 | 0.017373 | -0.014521 | -0.014521 | 37.1824 | 91.9591 | -176.0037 | -176.0037 | 121 | 3.8782 | 0.01364 | 3.8782 | 0.018296 | -0.014756 | -0.014756 | 38.729 | 106.8657 | -189.3637 | -189.3637 | 99 | 5.5748 | 0.0094891 | 5.5748 | 0.012728 | -0.013339 | -0.013339 | 29.7311 | 62.134 | -153.6299 | -153.6299
Change reference after Copy/paste
53.4894
0
22.1792
27.1593
0
-36.2647
-44.4076
0

## Multiplex_EEM_Savings_16CTZ
Y = a+b*x1+c*x2+d*x1^2+e*x2^2+f*x1*x2+g*x1^3+h*x2^3+i*x1*x2^2+j*x1^2*x2
[6 empty] | MT | LT
[5 empty] | a | 3.7535 | 9.8665
[5 empty] | b | -0.049642 | -0.23036
[5 empty] | c | 29.459 | 22.9056
|  | MT | LT |  | d | 0.00034207 | 0.0021889 | [7 empty] | CTZ1 | CTZ2 | CTZ3 | CTZ4 | CTZ5 | CTZ6 | CTZ7 | CTZ8 | CTZ9 | CTZ10 | CTZ11 | CTZ12 | CTZ13 | CTZ14 | CTZ15 | CTZ16
| Oversizing Factor (OS) | 13.04% | 13.04% |  | e | -11.7706 | -2.4887 | [5 empty] | Weather Factor |  | 74.26% | 74.8% | 76.05% | 77.87% | 76.26% | 78.9% | 79.73% | 79.38% | 78.58% | 77.74% | 74.95% | 76.13% | 77.88% | 77.03% | 85% | 71.04%
| Defrost Factor | 5% | 10% |  | f | -0.21294 | -0.24805 | [5 empty] | Overall Duty Cycle Factor | MT | 61.34% | 61.79% | 62.82% | 64.33% | 63% | 65.18% | 65.86% | 65.57% | 64.91% | 64.22% | 61.92% | 62.89% | 64.34% | 63.63% | 70.22% | 58.69%
| Weather Div. Factor | 85% | 85% |  | g | -1.4661e-06 | -7.575e-06 | [6 empty] | LT | 58.12% | 58.54% | 59.51% | 60.94% | 59.68% | 61.75% | 62.39% | 62.12% | 61.5% | 60.84% | 58.66% | 59.58% | 60.95% | 60.28% | 66.52% | 55.6%
| Overall Duty Cycle Factor | 70.22% | 66.52% |  | h | 6.8017 | 2.0361 | [5 empty] | EFLH | MT | 2889.3124 | 2910.4544 | 2958.8601 | 3029.8603 | 2967.2949 | 3069.8738 | 3102.0385 | 3088.4402 | 3057.3864 | 3024.6053 | 2916.2404 | 2962.0643 | 3030.2387 | 2997.0853 | 3307.2391 | 2764.0656
| Total Hours | 4710 | 4710 |  | i | -0.020187 | -0.021477 | [6 empty] | LT | 2737.2433 | 2757.2726 | 2803.1306 | 2870.394 | 2811.1215 | 2908.3015 | 2938.7733 | 2925.8907 | 2896.4713 | 2865.4156 | 2762.7541 | 2806.1662 | 2870.7525 | 2839.344 | 3133.1739 | 2618.5885
| EFLH | 3307.2391 | 3133.1739 |  | j | 0.00065794 | 0.00093831
Measure | Measure Unit | Total Unit | Box Temp | SET | Baseline Cooling Load | Compressor Capacity (Baseline Cooling Load with 15% OS) | Post Retrofit Cooling Load | Direct Power Reduction | Direct Energy Reduction | Part-Load-Ratio (Post Retrofit / Comp Cap) | Post Retrofit Duty Cycle Factor w/o Weather Factor Term | CTZ 1 - Arcata Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [69oF] |  |  | CTZ9: CTZ 2 - Santa Rosa Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] |  |  |  | CTZ 3 - Oakland Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [89oF] | [10 empty] | CTZ 4 - Sunnyvale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [88oF] | [10 empty] | CTZ 5 - Santa Maria Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 6 - Torrance Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [86oF] | [10 empty] | CTZ 7 - San Diego Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [83oF] | [10 empty] | CTZ 8 - Fullerton Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [94oF] | [10 empty] | CTZ 9 - Burbank - Glendale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [96oF] | [10 empty] | CTZ 10 - Riverside Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 11 - Red Bluff Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [104oF] | [10 empty] | CTZ 12 - Sacramento Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [100oF] | [10 empty] | CTZ 13 - Fresno Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [101oF] | [10 empty] | CTZ 14 - Palmdale Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [103oF] | [10 empty] | CTZ 15 - Palm Springs Intl Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [113oF] | [10 empty] | CTZ 16 - Blue Canyon Summer Design Dry Bulb (ASHRAE Climatic Region X Data, 0.5% Column) [85oF]
[12 empty] | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit | SCT | Baseline Comp EER | Comp kW (baseline) | Post Retrofit Comp EER | Post Retrofit Comp kW | Demand Savings | Demand Savings per Unit | Annual Energy (Old Syst.) | Annual Energy (New Syst.) | Annual Energy Savings | Annual Energy Savings per Unit
|  |  | [oF] | [oF] | [Btu/hr] | [Btu/hr] | [Btu/hr] | [kW] | [kWh] |  |  | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit] | [oF] | [Btu/hr/watts] | [kW] | [Btu/hr/watts] | [kW] | [DkW] | [DkW/unit] | [kWh] | [kWh] | [DkWh] | [DkWh/unit]
[15 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
Lighting Retrofits for Reach-ins (T12 Baseline)
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (2)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 52.8998 | 60.8348 | 27.4037 | 0.063333 | 298.3 | 0.45046 | 42.79% | 84 | 16.6547 | 0.0031763 | 16.6547 | 0.0016454 | 0.064864 | 0.064864 | 9.1773 | 2.4628 | 305.0145 | 305.0145 | 111 | 10.841 | 0.0048796 | 10.841 | 0.0025278 | 0.065685 | 0.065685 | 14.2019 | 3.8112 | 308.6907 | 308.6907 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0022855 | 0.06546 | 0.06546 | 12.7474 | 3.5032 | 307.5442 | 307.5442 | 103 | 12.1711 | 0.0043464 | 12.1711 | 0.0022515 | 0.065428 | 0.065428 | 12.8603 | 3.5339 | 307.6263 | 307.6263 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.0020844 | 0.065273 | 0.065273 | 12.191 | 3.204 | 307.287 | 307.287 | 101 | 12.5467 | 0.0042162 | 12.5467 | 0.0021841 | 0.065365 | 0.065365 | 12.5108 | 3.4734 | 307.3374 | 307.3374 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.0020844 | 0.065273 | 0.065273 | 12.352 | 3.3495 | 307.3025 | 307.3025 | 109 | 11.15 | 0.0047444 | 11.15 | 0.0024577 | 0.06562 | 0.06562 | 14.7172 | 3.9321 | 309.085 | 309.085 | 111 | 10.841 | 0.0048796 | 10.841 | 0.0025278 | 0.065685 | 0.065685 | 15.0704 | 4.0036 | 309.3668 | 309.3668 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0026703 | 0.065818 | 0.065818 | 15.7599 | 4.1839 | 309.876 | 309.876 | 119 | 9.7287 | 0.0054375 | 9.7287 | 0.0028168 | 0.065954 | 0.065954 | 16.4463 | 4.2554 | 310.491 | 310.491 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0026703 | 0.065818 | 0.065818 | 15.0324 | 4.0974 | 309.235 | 309.235 | 116 | 10.1252 | 0.0052246 | 10.1252 | 0.0027065 | 0.065851 | 0.065851 | 15.4756 | 4.2486 | 309.527 | 309.527 | 118 | 9.8584 | 0.0053659 | 9.8584 | 0.0027797 | 0.06592 | 0.06592 | 16.2601 | 4.3158 | 310.2443 | 310.2443 | 128 | 8.6415 | 0.0061216 | 8.6415 | 0.0031712 | 0.066284 | 0.066284 | 18.3469 | 5.433 | 311.2139 | 311.2139 | 100 | 12.7418 | 0.0041517 | 12.7418 | 0.0021507 | 0.065334 | 0.065334 | 13.7306 | 3.0795 | 308.9511 | 308.9511
LT, (2)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 52.8998 | 60.8348 | 27.4037 | 0.063333 | 298.3 | 0.45046 | 40.54% | 79 | 9.1087 | 0.0058076 | 9.1087 | 0.0030085 | 0.066132 | 0.066132 | 15.8969 | 4.266 | 309.9309 | 309.9309 | 106 | 6.3763 | 0.0082964 | 6.3763 | 0.0042978 | 0.067332 | 0.067332 | 22.8753 | 6.1387 | 315.0366 | 315.0366 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.003893 | 0.066955 | 0.066955 | 20.5703 | 5.653 | 313.2172 | 313.2172 | 98 | 7.1373 | 0.0074117 | 7.1373 | 0.0038395 | 0.066906 | 0.066906 | 20.776 | 5.7092 | 313.3668 | 313.3668 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0035877 | 0.066671 | 0.066671 | 19.8794 | 5.2246 | 312.9548 | 312.9548 | 96 | 7.3357 | 0.0072113 | 7.3357 | 0.0037357 | 0.066809 | 0.066809 | 20.2719 | 5.6282 | 312.9438 | 312.9438 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0035877 | 0.066671 | 0.066671 | 20.1419 | 5.4618 | 312.9801 | 312.9801 | 104 | 6.5612 | 0.0080625 | 6.5612 | 0.0041766 | 0.067219 | 0.067219 | 23.6938 | 6.3305 | 315.6633 | 315.6633 | 106 | 6.3763 | 0.0082964 | 6.3763 | 0.0042978 | 0.067332 | 0.067332 | 24.2743 | 6.4486 | 316.1256 | 316.1256 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.0045534 | 0.06757 | 0.06757 | 25.4592 | 6.7589 | 317.0003 | 317.0003 | 114 | 5.6781 | 0.0093165 | 5.6781 | 0.0048262 | 0.067824 | 0.067824 | 26.6957 | 6.9073 | 318.0884 | 318.0884 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.0045534 | 0.06757 | 0.06757 | 24.2839 | 6.6191 | 315.9647 | 315.9647 | 111 | 5.9316 | 0.0089184 | 5.9316 | 0.00462 | 0.067632 | 0.067632 | 25.0264 | 6.8706 | 316.4558 | 316.4558 | 113 | 5.7614 | 0.0091818 | 5.7614 | 0.0047565 | 0.067759 | 0.067759 | 26.3586 | 6.9961 | 317.6625 | 317.6625 | 123 | 4.9865 | 0.010609 | 4.9865 | 0.0054956 | 0.068446 | 0.068446 | 30.1214 | 8.9198 | 319.5016 | 319.5016 | 95 | 7.4359 | 0.0071141 | 7.4359 | 0.0036854 | 0.066762 | 0.066762 | 22.2899 | 4.9992 | 315.5907 | 315.5907
Grocery | /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Canopy | /Fixture | 1 | 38 | 28 | 93.1299 | 107.0994 | 27.4037 | 0.053833 | 253.555 | 0.25587 | 24.31% | 84 | 16.6547 | 0.0055918 | 16.6547 | 0.0016454 | 0.05778 | 0.05778 | 16.1565 | 1.3989 | 268.3126 | 268.3126 | 111 | 10.841 | 0.0085906 | 10.841 | 0.0025278 | 0.059896 | 0.059896 | 25.0024 | 2.1648 | 276.3926 | 276.3926 | 104 | 11.9903 | 0.0077671 | 11.9903 | 0.0022855 | 0.059315 | 0.059315 | 22.4417 | 1.9899 | 274.0068 | 274.0068 | 103 | 12.1711 | 0.0076517 | 12.1711 | 0.0022515 | 0.059234 | 0.059234 | 22.6404 | 2.0074 | 274.1881 | 274.1881 | 98 | 13.1473 | 0.0070836 | 13.1473 | 0.0020844 | 0.058833 | 0.058833 | 21.4622 | 1.8199 | 273.1973 | 273.1973 | 101 | 12.5467 | 0.0074227 | 12.5467 | 0.0021841 | 0.059072 | 0.059072 | 22.0252 | 1.973 | 273.6073 | 273.6073 | 98 | 13.1473 | 0.0070836 | 13.1473 | 0.0020844 | 0.058833 | 0.058833 | 21.7456 | 1.9026 | 273.3981 | 273.3981 | 109 | 11.15 | 0.0083524 | 11.15 | 0.0024577 | 0.059728 | 0.059728 | 25.9095 | 2.2335 | 277.231 | 277.231 | 111 | 10.841 | 0.0085906 | 10.841 | 0.0025278 | 0.059896 | 0.059896 | 26.5314 | 2.2741 | 277.8123 | 277.8123 | 115 | 10.2624 | 0.0090749 | 10.2624 | 0.0026703 | 0.060238 | 0.060238 | 27.7453 | 2.3766 | 278.9238 | 278.9238 | 119 | 9.7287 | 0.0095727 | 9.7287 | 0.0028168 | 0.060589 | 0.060589 | 28.9537 | 2.4171 | 280.0916 | 280.0916 | 115 | 10.2624 | 0.0090749 | 10.2624 | 0.0026703 | 0.060238 | 0.060238 | 26.4644 | 2.3274 | 277.692 | 277.692 | 116 | 10.1252 | 0 | 10.1252 | 0.0027065 | 0.051127 | 0.051127 | 0 | 2.4133 | 251.1417 | 251.1417 | 118 | 9.8584 | 0.0094467 | 9.8584 | 0.0027797 | 0.0605 | 0.0605 | 28.6258 | 2.4514 | 279.7294 | 279.7294 | 128 | 8.6415 | 0.010777 | 8.6415 | 0.0031712 | 0.061439 | 0.061439 | 32.2997 | 3.0861 | 282.7686 | 282.7686 | 100 | 12.7418 | 0.007309 | 12.7418 | 0.0021507 | 0.058992 | 0.058992 | 24.1727 | 1.7492 | 275.9784 | 275.9784
LT, (1)T12 to LED Canopy | /Fixture | 1 | 0 | -10 | 93.1299 | 107.0994 | 27.4037 | 0.053833 | 253.555 | 0.25587 | 23.03% | 79 | 9.1087 | 0.010224 | 9.1087 | 0.0030085 | 0.061049 | 0.061049 | 27.9865 | 2.4232 | 279.1183 | 279.1183 | 106 | 6.3763 | 0.014606 | 6.3763 | 0.0042978 | 0.064141 | 0.064141 | 40.272 | 3.4869 | 290.34 | 290.34 | 99 | 7.0393 | 0.01323 | 7.0393 | 0.003893 | 0.06317 | 0.06317 | 36.2139 | 3.211 | 286.5578 | 286.5578 | 98 | 7.1373 | 0.013048 | 7.1373 | 0.0038395 | 0.063042 | 0.063042 | 36.576 | 3.2429 | 286.8881 | 286.8881 | 93 | 7.6382 | 0.012193 | 7.6382 | 0.0035877 | 0.062438 | 0.062438 | 34.9976 | 2.9677 | 285.5849 | 285.5849 | 96 | 7.3357 | 0.012696 | 7.3357 | 0.0037357 | 0.062793 | 0.062793 | 35.6886 | 3.1969 | 286.0467 | 286.0467 | 93 | 7.6382 | 0.012193 | 7.6382 | 0.0035877 | 0.062438 | 0.062438 | 35.4598 | 3.1024 | 285.9124 | 285.9124 | 104 | 6.5612 | 0.014194 | 6.5612 | 0.0041766 | 0.063851 | 0.063851 | 41.7129 | 3.5959 | 291.672 | 291.672 | 106 | 6.3763 | 0.014606 | 6.3763 | 0.0042978 | 0.064141 | 0.064141 | 42.7347 | 3.663 | 292.6268 | 292.6268 | 110 | 6.0184 | 0.015474 | 6.0184 | 0.0045534 | 0.064754 | 0.064754 | 44.8209 | 3.8392 | 294.5367 | 294.5367 | 114 | 5.6781 | 0.016402 | 5.6781 | 0.0048262 | 0.065409 | 0.065409 | 46.9977 | 3.9235 | 296.6292 | 296.6292 | 110 | 6.0184 | 0.015474 | 6.0184 | 0.0045534 | 0.064754 | 0.064754 | 42.7517 | 3.7598 | 292.5469 | 292.5469 | 111 | 5.9316 | 0.015701 | 5.9316 | 0.00462 | 0.064914 | 0.064914 | 44.0589 | 3.9026 | 293.7112 | 293.7112 | 113 | 5.7614 | 0.016165 | 5.7614 | 0.0047565 | 0.065241 | 0.065241 | 46.4043 | 3.9739 | 295.9853 | 295.9853 | 123 | 4.9865 | 0.018676 | 4.9865 | 0.0054956 | 0.067014 | 0.067014 | 53.0286 | 5.0666 | 301.517 | 301.517 | 95 | 7.4359 | 0.012524 | 7.4359 | 0.0036854 | 0.062672 | 0.062672 | 39.2412 | 2.8397 | 289.9566 | 289.9566
MT, (2)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 37.8942 | 43.5784 | 27.4037 | 0.040333 | 189.97 | 0.62884 | 59.74% | 84 | 16.6547 | 0.0022753 | 16.6547 | 0.0016454 | 0.040963 | 0.040963 | 6.574 | 3.438 | 193.106 | 193.106 | 111 | 10.841 | 0.0034955 | 10.841 | 0.0025278 | 0.041301 | 0.041301 | 10.1734 | 5.3203 | 194.8231 | 194.8231 | 104 | 11.9903 | 0.0031604 | 11.9903 | 0.0022855 | 0.041208 | 0.041208 | 9.1314 | 4.8904 | 194.2111 | 194.2111 | 103 | 12.1711 | 0.0031135 | 12.1711 | 0.0022515 | 0.041195 | 0.041195 | 9.2123 | 4.9333 | 194.249 | 194.249 | 98 | 13.1473 | 0.0028823 | 13.1473 | 0.0020844 | 0.041131 | 0.041131 | 8.7329 | 4.4727 | 194.2302 | 194.2302 | 101 | 12.5467 | 0.0030203 | 12.5467 | 0.0021841 | 0.041169 | 0.041169 | 8.962 | 4.8488 | 194.0832 | 194.0832 | 98 | 13.1473 | 0.0028823 | 13.1473 | 0.0020844 | 0.041131 | 0.041131 | 8.8482 | 4.6758 | 194.1424 | 194.1424 | 109 | 11.15 | 0.0033986 | 11.15 | 0.0024577 | 0.041274 | 0.041274 | 10.5425 | 5.4892 | 195.0233 | 195.0233 | 111 | 10.841 | 0.0034955 | 10.841 | 0.0025278 | 0.041301 | 0.041301 | 10.7955 | 5.5889 | 195.1766 | 195.1766 | 115 | 10.2624 | 0.0036925 | 10.2624 | 0.0026703 | 0.041356 | 0.041356 | 11.2895 | 5.8407 | 195.4188 | 195.4188 | 119 | 9.7287 | 0.0038951 | 9.7287 | 0.0028168 | 0.041412 | 0.041412 | 11.7812 | 5.9404 | 195.8108 | 195.8108 | 115 | 10.2624 | 0.0036925 | 10.2624 | 0.0026703 | 0.041356 | 0.041356 | 10.7683 | 5.7199 | 195.0184 | 195.0184 | 116 | 10.1252 | 0.0037426 | 10.1252 | 0.0027065 | 0.041369 | 0.041369 | 11.0858 | 5.9309 | 195.1249 | 195.1249 | 118 | 9.8584 | 0.0038438 | 9.8584 | 0.0027797 | 0.041397 | 0.041397 | 11.6477 | 6.0247 | 195.593 | 195.593 | 128 | 8.6415 | 0.0043851 | 8.6415 | 0.0031712 | 0.041547 | 0.041547 | 13.1426 | 7.5844 | 195.5282 | 195.5282 | 100 | 12.7418 | 0.002974 | 12.7418 | 0.0021507 | 0.041157 | 0.041157 | 9.8358 | 4.299 | 195.5068 | 195.5068
LT, (2)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 37.8942 | 43.5784 | 27.4037 | 0.040333 | 189.97 | 0.62884 | 56.6% | 79 | 9.1087 | 0.0041602 | 9.1087 | 0.0030085 | 0.041485 | 0.041485 | 11.3876 | 5.9553 | 195.4023 | 195.4023 | 106 | 6.3763 | 0.005943 | 6.3763 | 0.0042978 | 0.041979 | 0.041979 | 16.3865 | 8.5696 | 197.7869 | 197.7869 | 99 | 7.0393 | 0.0053833 | 7.0393 | 0.003893 | 0.041824 | 0.041824 | 14.7353 | 7.8915 | 196.8137 | 196.8137 | 98 | 7.1373 | 0.0053093 | 7.1373 | 0.0038395 | 0.041803 | 0.041803 | 14.8827 | 7.9699 | 196.8828 | 196.8828 | 93 | 7.6382 | 0.0049611 | 7.6382 | 0.0035877 | 0.041707 | 0.041707 | 14.2404 | 7.2935 | 196.9169 | 196.9169 | 96 | 7.3357 | 0.0051658 | 7.3357 | 0.0037357 | 0.041763 | 0.041763 | 14.5216 | 7.8568 | 196.6348 | 196.6348 | 93 | 7.6382 | 0.0049611 | 7.6382 | 0.0035877 | 0.041707 | 0.041707 | 14.4285 | 7.6247 | 196.7738 | 196.7738 | 104 | 6.5612 | 0.0057755 | 6.5612 | 0.0041766 | 0.041932 | 0.041932 | 16.9728 | 8.8373 | 198.1055 | 198.1055 | 106 | 6.3763 | 0.005943 | 6.3763 | 0.0042978 | 0.041979 | 0.041979 | 17.3886 | 9.0022 | 198.3564 | 198.3564 | 110 | 6.0184 | 0.0062964 | 6.0184 | 0.0045534 | 0.042076 | 0.042076 | 18.2375 | 9.4353 | 198.7721 | 198.7721 | 114 | 5.6781 | 0.0066738 | 5.6781 | 0.0048262 | 0.042181 | 0.042181 | 19.1232 | 9.6425 | 199.4507 | 199.4507 | 110 | 6.0184 | 0.0062964 | 6.0184 | 0.0045534 | 0.042076 | 0.042076 | 17.3955 | 9.2402 | 198.1253 | 198.1253 | 111 | 5.9316 | 0.0063886 | 5.9316 | 0.00462 | 0.042102 | 0.042102 | 17.9274 | 9.5912 | 198.3062 | 198.3062 | 113 | 5.7614 | 0.0065773 | 5.7614 | 0.0047565 | 0.042154 | 0.042154 | 18.8817 | 9.7665 | 199.0853 | 199.0853 | 123 | 4.9865 | 0.0075993 | 4.9865 | 0.0054956 | 0.042437 | 0.042437 | 21.5772 | 12.4519 | 199.0953 | 199.0953 | 95 | 7.4359 | 0.0050961 | 7.4359 | 0.0036854 | 0.041744 | 0.041744 | 15.9671 | 6.9788 | 198.9583 | 198.9583
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T8 to LED Canopy | /Fixture | 1 | 38 | 28 | 38.0621 | 43.7714 | 27.4037 | 0.010833 | 51.025 | 0.62607 | 59.48% | 84 | 16.6547 | 0.0022854 | 16.6547 | 0.0016454 | 0.011473 | 0.011473 | 6.6031 | 3.4228 | 54.2053 | 54.2053 | 111 | 10.841 | 0.0035109 | 10.841 | 0.0025278 | 0.011816 | 0.011816 | 10.2185 | 5.2969 | 55.9466 | 55.9466 | 104 | 11.9903 | 0.0031744 | 11.9903 | 0.0022855 | 0.011722 | 0.011722 | 9.1719 | 4.8688 | 55.3281 | 55.3281 | 103 | 12.1711 | 0.0031273 | 12.1711 | 0.0022515 | 0.011709 | 0.011709 | 9.2531 | 4.9116 | 55.3665 | 55.3665 | 98 | 13.1473 | 0.002895 | 13.1473 | 0.0020844 | 0.011644 | 0.011644 | 8.7716 | 4.453 | 55.3436 | 55.3436 | 101 | 12.5467 | 0.0030336 | 12.5467 | 0.0021841 | 0.011683 | 0.011683 | 9.0017 | 4.8275 | 55.1992 | 55.1992 | 98 | 13.1473 | 0.002895 | 13.1473 | 0.0020844 | 0.011644 | 0.011644 | 8.8874 | 4.6552 | 55.2572 | 55.2572 | 109 | 11.15 | 0.0034136 | 11.15 | 0.0024577 | 0.011789 | 0.011789 | 10.5892 | 5.465 | 56.1492 | 56.1492 | 111 | 10.841 | 0.0035109 | 10.841 | 0.0025278 | 0.011816 | 0.011816 | 10.8434 | 5.5643 | 56.3041 | 56.3041 | 115 | 10.2624 | 0.0037089 | 10.2624 | 0.0026703 | 0.011872 | 0.011872 | 11.3395 | 5.815 | 56.5495 | 56.5495 | 119 | 9.7287 | 0.0039124 | 9.7287 | 0.0028168 | 0.011929 | 0.011929 | 11.8333 | 5.9142 | 56.9441 | 56.9441 | 115 | 10.2624 | 0.0037089 | 10.2624 | 0.0026703 | 0.011872 | 0.011872 | 10.816 | 5.6947 | 56.1463 | 56.1463 | 116 | 10.1252 | 0.0037592 | 10.1252 | 0.0027065 | 0.011886 | 0.011886 | 11.1349 | 5.9048 | 56.2551 | 56.2551 | 118 | 9.8584 | 0.0038609 | 9.8584 | 0.0027797 | 0.011914 | 0.011914 | 11.6993 | 5.9982 | 56.7262 | 56.7262 | 128 | 8.6415 | 0.0044046 | 8.6415 | 0.0031712 | 0.012067 | 0.012067 | 13.2008 | 7.551 | 56.6749 | 56.6749 | 100 | 12.7418 | 0.0029872 | 12.7418 | 0.0021507 | 0.01167 | 0.01167 | 9.8793 | 4.28 | 56.6243 | 56.6243
LT, (1)T8 to LED Canopy | /Fixture | 1 | 0 | -10 | 38.0621 | 43.7714 | 27.4037 | 0.010833 | 51.025 | 0.62607 | 56.35% | 79 | 9.1087 | 0.0041787 | 9.1087 | 0.0030085 | 0.012003 | 0.012003 | 11.438 | 5.9291 | 56.534 | 56.534 | 106 | 6.3763 | 0.0059693 | 6.3763 | 0.0042978 | 0.012505 | 0.012505 | 16.4591 | 8.5318 | 58.9523 | 58.9523 | 99 | 7.0393 | 0.0054071 | 7.0393 | 0.003893 | 0.012347 | 0.012347 | 14.8005 | 7.8568 | 57.9688 | 57.9688 | 98 | 7.1373 | 0.0053328 | 7.1373 | 0.0038395 | 0.012327 | 0.012327 | 14.9486 | 7.9348 | 58.0388 | 58.0388 | 93 | 7.6382 | 0.0049831 | 7.6382 | 0.0035877 | 0.012229 | 0.012229 | 14.3035 | 7.2613 | 58.0672 | 58.0672 | 96 | 7.3357 | 0.0051886 | 7.3357 | 0.0037357 | 0.012286 | 0.012286 | 14.5859 | 7.8222 | 57.7887 | 57.7887 | 93 | 7.6382 | 0.0049831 | 7.6382 | 0.0035877 | 0.012229 | 0.012229 | 14.4924 | 7.591 | 57.9263 | 57.9263 | 104 | 6.5612 | 0.0058011 | 6.5612 | 0.0041766 | 0.012458 | 0.012458 | 17.048 | 8.7983 | 59.2747 | 59.2747 | 106 | 6.3763 | 0.0059693 | 6.3763 | 0.0042978 | 0.012505 | 0.012505 | 17.4656 | 8.9625 | 59.5281 | 59.5281 | 110 | 6.0184 | 0.0063243 | 6.0184 | 0.0045534 | 0.012604 | 0.012604 | 18.3182 | 9.3937 | 59.9495 | 59.9495 | 114 | 5.6781 | 0.0067034 | 5.6781 | 0.0048262 | 0.01271 | 0.01271 | 19.2079 | 9.6 | 60.6329 | 60.6329 | 110 | 6.0184 | 0.0063243 | 6.0184 | 0.0045534 | 0.012604 | 0.012604 | 17.4725 | 9.1995 | 59.2981 | 59.2981 | 111 | 5.9316 | 0.0064169 | 5.9316 | 0.00462 | 0.01263 | 0.01263 | 18.0068 | 9.5489 | 59.4829 | 59.4829 | 113 | 5.7614 | 0.0066064 | 5.7614 | 0.0047565 | 0.012683 | 0.012683 | 18.9654 | 9.7234 | 60.267 | 60.267 | 123 | 4.9865 | 0.007633 | 4.9865 | 0.0054956 | 0.012971 | 0.012971 | 21.6727 | 12.397 | 60.3008 | 60.3008 | 95 | 7.4359 | 0.0051187 | 7.4359 | 0.0036854 | 0.012267 | 0.012267 | 16.0378 | 6.9481 | 60.1148 | 60.1148
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| /Fixture | 1 | 38 | 28 | 52.8998 | 60.8348 | 70.9563 | 0.0424 | 126.048 | 1.1664 | 110.8% | 84 | 16.6547 | 0.0031763 | 16.6547 | 0.0042604 | 0.041316 | 0.041316 | 9.1773 | 16.5115 | 118.7138 | 118.7138 | 111 | 10.841 | 0.0048796 | 10.841 | 0.0065452 | 0.040734 | 0.040734 | 14.2019 | 25.5517 | 114.6982 | 114.6982 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | 0.040894 | 0.040894 | 12.7474 | 23.4868 | 115.3086 | 115.3086 | 103 | 12.1711 | 0.0043464 | 12.1711 | 0.0058299 | 0.040916 | 0.040916 | 12.8603 | 23.6931 | 115.2152 | 115.2152 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.005397 | 0.041027 | 0.041027 | 12.191 | 21.4808 | 116.7582 | 116.7582 | 99 | 12.942 | 0.0040875 | 12.942 | 0.0054827 | 0.041005 | 0.041005 | 12.1287 | 22.5761 | 115.6007 | 115.6007 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.005397 | 0.041027 | 0.041027 | 12.352 | 22.4562 | 115.9438 | 115.9438 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | 0.040894 | 0.040894 | 13.6859 | 24.5154 | 115.2185 | 115.2185 | 109 | 11.15 | 0.0047444 | 11.15 | 0.0063638 | 0.040781 | 0.040781 | 14.6527 | 26.0976 | 114.603 | 114.603 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0069142 | 0.040641 | 0.040641 | 15.7599 | 28.0509 | 113.7571 | 113.7571 | 119 | 9.7287 | 0.0054375 | 9.7287 | 0.0072935 | 0.040544 | 0.040544 | 16.4463 | 28.5297 | 113.9646 | 113.9646 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0069142 | 0.040641 | 0.040641 | 15.0324 | 27.4709 | 113.6095 | 113.6095 | 116 | 10.1252 | 0.0052246 | 10.1252 | 0.0070079 | 0.040617 | 0.040617 | 15.4756 | 28.4841 | 113.0395 | 113.0395 | 123 | 9.2301 | 0.0057312 | 9.2301 | 0.0076875 | 0.040444 | 0.040444 | 17.367 | 30.9045 | 112.5105 | 112.5105 | 126 | 8.8734 | 0.0059616 | 8.8734 | 0.0079965 | 0.040365 | 0.040365 | 17.8675 | 35.4736 | 108.442 | 108.442 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | 0.040894 | 0.040894 | 14.5912 | 21.9405 | 118.6987 | 118.6987
| /Fixture | 1 | 0 | -10 | 52.8998 | 60.8348 | 70.9563 | 0.0424 | 126.048 | 1.1664 | 105% | 79 | 9.1087 | 0.0058076 | 9.1087 | 0.00779 | 0.040418 | 0.040418 | 15.8969 | 28.6013 | 113.3436 | 113.3436 | 106 | 6.3763 | 0.0082964 | 6.3763 | 0.011128 | 0.039568 | 0.039568 | 22.8753 | 41.1568 | 107.7666 | 107.7666 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | 0.039835 | 0.039835 | 20.5703 | 37.9003 | 108.7179 | 108.7179 | 98 | 7.1373 | 0.0074117 | 7.1373 | 0.0099416 | 0.03987 | 0.03987 | 20.776 | 38.2766 | 108.5474 | 108.5474 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0092896 | 0.040036 | 0.040036 | 19.8794 | 35.028 | 110.8994 | 110.8994 | 94 | 7.5367 | 0.0070189 | 7.5367 | 0.0094147 | 0.040004 | 0.040004 | 19.7311 | 36.7269 | 109.0522 | 109.0522 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0092896 | 0.040036 | 0.040036 | 20.1419 | 36.6186 | 109.5714 | 109.5714 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | 0.039835 | 0.039835 | 22.0847 | 39.5601 | 108.5726 | 108.5726 | 104 | 6.5612 | 0.0080625 | 6.5612 | 0.010814 | 0.039648 | 0.039648 | 23.59 | 42.0157 | 107.6222 | 107.6222 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.01179 | 0.0394 | 0.0394 | 25.4592 | 45.3145 | 106.1927 | 106.1927 | 114 | 5.6781 | 0.0093165 | 5.6781 | 0.012497 | 0.03922 | 0.03922 | 26.6957 | 46.3094 | 106.4343 | 106.4343 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.01179 | 0.0394 | 0.0394 | 24.2839 | 44.3775 | 105.9544 | 105.9544 | 111 | 5.9316 | 0.0089184 | 5.9316 | 0.011962 | 0.039356 | 0.039356 | 25.0264 | 46.0632 | 105.0112 | 105.0112 | 118 | 5.3573 | 0.0098744 | 5.3573 | 0.013245 | 0.03903 | 0.03903 | 28.347 | 50.4433 | 103.9517 | 103.9517 | 121 | 5.1306 | 0.010311 | 5.1306 | 0.01383 | 0.038881 | 0.038881 | 29.2757 | 58.1228 | 97.2008 | 97.2008 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | 0.039835 | 0.039835 | 23.5457 | 35.4052 | 114.1885 | 114.1885
| /Fixture | [13 empty] | CTZ3: incl. direct; CTZ7: incl. direct; CTZ14: incl. direct |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct | [6 empty] | incl. direct |  |  |  | incl. direct
/Fixture
| /Fixture | [186 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, (1)T12 to LED Shelf | /Fixture | 1 | 38 | 28 | 93.1299 | 107.0994 | 14.0934 | 0.0629 | 296.259 | 0.13159 | 12.5% | 84 | 16.6547 | 0.0055918 | 16.6547 | 0.00084621 | 0.067646 | 0.067646 | 16.1565 | 0.37 | 312.0455 | 312.0455 | 111 | 10.841 | 0.0085906 | 10.841 | 0.0013 | 0.070191 | 0.070191 | 25.0024 | 0.57258 | 320.6889 | 320.6889 | 104 | 11.9903 | 0.0077671 | 11.9903 | 0.0011754 | 0.069492 | 0.069492 | 22.4417 | 0.5263 | 318.1744 | 318.1744 | 103 | 12.1711 | 0.0076517 | 12.1711 | 0.0011579 | 0.069394 | 0.069394 | 22.6404 | 0.53093 | 318.3685 | 318.3685 | 98 | 13.1473 | 0.0070836 | 13.1473 | 0.001072 | 0.068912 | 0.068912 | 21.4622 | 0.48135 | 317.2398 | 317.2398 | 101 | 12.5467 | 0.0074227 | 12.5467 | 0.0011233 | 0.069199 | 0.069199 | 22.0252 | 0.52183 | 317.7624 | 317.7624 | 98 | 13.1473 | 0.0070836 | 13.1473 | 0.001072 | 0.068912 | 0.068912 | 21.7456 | 0.50321 | 317.5014 | 317.5014 | 109 | 11.15 | 0.0083524 | 11.15 | 0.001264 | 0.069988 | 0.069988 | 25.9095 | 0.59075 | 321.5778 | 321.5778 | 111 | 10.841 | 0.0085906 | 10.841 | 0.0013 | 0.070191 | 0.070191 | 26.5314 | 0.60148 | 322.1889 | 322.1889 | 115 | 10.2624 | 0.0090749 | 10.2624 | 0.0013733 | 0.070602 | 0.070602 | 27.7453 | 0.62858 | 323.3758 | 323.3758 | 119 | 9.7287 | 0.0095727 | 9.7287 | 0.0014486 | 0.071024 | 0.071024 | 28.9537 | 0.63931 | 324.5734 | 324.5734 | 115 | 10.2624 | 0.0090749 | 10.2624 | 0.0013733 | 0.070602 | 0.070602 | 26.4644 | 0.61558 | 322.1079 | 322.1079 | 116 | 10.1252 | 0.0091979 | 10.1252 | 0.0013919 | 0.070706 | 0.070706 | 27.2447 | 0.63828 | 322.8654 | 322.8654 | 118 | 9.8584 | 0.0094467 | 9.8584 | 0.0014296 | 0.070917 | 0.070917 | 28.6258 | 0.64838 | 324.2364 | 324.2364 | 128 | 8.6415 | 0.010777 | 8.6415 | 0.0016309 | 0.072046 | 0.072046 | 32.2997 | 0.81623 | 327.7425 | 327.7425 | 100 | 12.7418 | 0.007309 | 12.7418 | 0.0011061 | 0.069103 | 0.069103 | 24.1727 | 0.46266 | 319.969 | 319.969
LT, (1)T12 to LED Shelf | /Fixture | 1 | 0 | -10 | 93.1299 | 107.0994 | 14.0934 | 0.0629 | 296.259 | 0.13159 | 11.84% | 79 | 9.1087 | 0.010224 | 9.1087 | 0.0015472 | 0.071577 | 0.071577 | 27.9865 | 0.64091 | 323.6045 | 323.6045 | 106 | 6.3763 | 0.014606 | 6.3763 | 0.0022103 | 0.075295 | 0.075295 | 40.272 | 0.92226 | 335.6087 | 335.6087 | 99 | 7.0393 | 0.01323 | 7.0393 | 0.0020021 | 0.074128 | 0.074128 | 36.2139 | 0.84929 | 331.6236 | 331.6236 | 98 | 7.1373 | 0.013048 | 7.1373 | 0.0019746 | 0.073974 | 0.073974 | 36.576 | 0.85772 | 331.9773 | 331.9773 | 93 | 7.6382 | 0.012193 | 7.6382 | 0.0018451 | 0.073248 | 0.073248 | 34.9976 | 0.78492 | 330.4717 | 330.4717 | 96 | 7.3357 | 0.012696 | 7.3357 | 0.0019212 | 0.073674 | 0.073674 | 35.6886 | 0.84555 | 331.1021 | 331.1021 | 93 | 7.6382 | 0.012193 | 7.6382 | 0.0018451 | 0.073248 | 0.073248 | 35.4598 | 0.82057 | 330.8983 | 330.8983 | 104 | 6.5612 | 0.014194 | 6.5612 | 0.002148 | 0.074946 | 0.074946 | 41.7129 | 0.95107 | 337.0208 | 337.0208 | 106 | 6.3763 | 0.014606 | 6.3763 | 0.0022103 | 0.075295 | 0.075295 | 42.7347 | 0.96882 | 338.0249 | 338.0249 | 110 | 6.0184 | 0.015474 | 6.0184 | 0.0023417 | 0.076033 | 0.076033 | 44.8209 | 1.0154 | 340.0644 | 340.0644 | 114 | 5.6781 | 0.016402 | 5.6781 | 0.0024821 | 0.07682 | 0.07682 | 46.9977 | 1.0377 | 342.219 | 342.219 | 110 | 6.0184 | 0.015474 | 6.0184 | 0.0023417 | 0.076033 | 0.076033 | 42.7517 | 0.99443 | 338.0162 | 338.0162 | 111 | 5.9316 | 0.015701 | 5.9316 | 0.002376 | 0.076225 | 0.076225 | 44.0589 | 1.0322 | 339.2857 | 339.2857 | 113 | 5.7614 | 0.016165 | 5.7614 | 0.0024462 | 0.076618 | 0.076618 | 46.4043 | 1.0511 | 341.6122 | 341.6122 | 123 | 4.9865 | 0.018676 | 4.9865 | 0.0028263 | 0.07875 | 0.07875 | 53.0286 | 1.3401 | 347.9475 | 347.9475 | 95 | 7.4359 | 0.012524 | 7.4359 | 0.0018953 | 0.073529 | 0.073529 | 39.2412 | 0.75106 | 334.7492 | 334.7492
MT, (1)T8 to LED Shelf | /Fixture | 1 | 38 | 28 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 30.59% | 84 | 16.6547 | 0.0022854 | 16.6547 | 0.00084621 | 0.021339 | 0.021339 | 6.6031 | 0.90531 | 99.4268 | 99.4268 | 111 | 10.841 | 0.0035109 | 10.841 | 0.0013 | 0.022111 | 0.022111 | 10.2185 | 1.401 | 102.5465 | 102.5465 | 104 | 11.9903 | 0.0031744 | 11.9903 | 0.0011754 | 0.021899 | 0.021899 | 9.1719 | 1.2878 | 101.6131 | 101.6131 | 103 | 12.1711 | 0.0031273 | 12.1711 | 0.0011579 | 0.021869 | 0.021869 | 9.2531 | 1.2991 | 101.683 | 101.683 | 98 | 13.1473 | 0.002895 | 13.1473 | 0.001072 | 0.021723 | 0.021723 | 8.7716 | 1.1778 | 101.3228 | 101.3228 | 101 | 12.5467 | 0.0030336 | 12.5467 | 0.0011233 | 0.02181 | 0.02181 | 9.0017 | 1.2768 | 101.4539 | 101.4539 | 98 | 13.1473 | 0.002895 | 13.1473 | 0.001072 | 0.021723 | 0.021723 | 8.8874 | 1.2312 | 101.3852 | 101.3852 | 109 | 11.15 | 0.0034136 | 11.15 | 0.001264 | 0.02205 | 0.02205 | 10.5892 | 1.4454 | 102.8728 | 102.8728 | 111 | 10.841 | 0.0035109 | 10.841 | 0.0013 | 0.022111 | 0.022111 | 10.8434 | 1.4717 | 103.1007 | 103.1007 | 115 | 10.2624 | 0.0037089 | 10.2624 | 0.0013733 | 0.022236 | 0.022236 | 11.3395 | 1.538 | 103.5305 | 103.5305 | 119 | 9.7287 | 0.0039124 | 9.7287 | 0.0014486 | 0.022364 | 0.022364 | 11.8333 | 1.5643 | 103.9981 | 103.9981 | 115 | 10.2624 | 0.0037089 | 10.2624 | 0.0013733 | 0.022236 | 0.022236 | 10.816 | 1.5062 | 103.0388 | 103.0388 | 116 | 10.1252 | 0.0037592 | 10.1252 | 0.0013919 | 0.022267 | 0.022267 | 11.1349 | 1.5617 | 103.3021 | 103.3021 | 118 | 9.8584 | 0.0038609 | 9.8584 | 0.0014296 | 0.022331 | 0.022331 | 11.6993 | 1.5865 | 103.8419 | 103.8419 | 128 | 8.6415 | 0.0044046 | 8.6415 | 0.0016309 | 0.022674 | 0.022674 | 13.2008 | 1.9972 | 104.9327 | 104.9327 | 100 | 12.7418 | 0.0029872 | 12.7418 | 0.0011061 | 0.021781 | 0.021781 | 9.8793 | 1.132 | 102.4763 | 102.4763
LT, (1)T8 to LED Shelf | /Fixture | 1 | 0 | -10 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 28.98% | 79 | 9.1087 | 0.0041787 | 9.1087 | 0.0015472 | 0.022531 | 0.022531 | 11.438 | 1.5682 | 103.5988 | 103.5988 | 106 | 6.3763 | 0.0059693 | 6.3763 | 0.0022103 | 0.023659 | 0.023659 | 16.4591 | 2.2566 | 107.9315 | 107.9315 | 99 | 7.0393 | 0.0054071 | 7.0393 | 0.0020021 | 0.023305 | 0.023305 | 14.8005 | 2.078 | 106.4515 | 106.4515 | 98 | 7.1373 | 0.0053328 | 7.1373 | 0.0019746 | 0.023258 | 0.023258 | 14.9486 | 2.0987 | 106.5789 | 106.5789 | 93 | 7.6382 | 0.0049831 | 7.6382 | 0.0018451 | 0.023038 | 0.023038 | 14.3035 | 1.9205 | 106.1119 | 106.1119 | 96 | 7.3357 | 0.0051886 | 7.3357 | 0.0019212 | 0.023167 | 0.023167 | 14.5859 | 2.0689 | 106.246 | 106.246 | 93 | 7.6382 | 0.0049831 | 7.6382 | 0.0018451 | 0.023038 | 0.023038 | 14.4924 | 2.0078 | 106.2136 | 106.2136 | 104 | 6.5612 | 0.0058011 | 6.5612 | 0.002148 | 0.023553 | 0.023553 | 17.048 | 2.3271 | 108.4499 | 108.4499 | 106 | 6.3763 | 0.0059693 | 6.3763 | 0.0022103 | 0.023659 | 0.023659 | 17.4656 | 2.3705 | 108.8241 | 108.8241 | 110 | 6.0184 | 0.0063243 | 6.0184 | 0.0023417 | 0.023883 | 0.023883 | 18.3182 | 2.4845 | 109.5627 | 109.5627 | 114 | 5.6781 | 0.0067034 | 5.6781 | 0.0024821 | 0.024121 | 0.024121 | 19.2079 | 2.5391 | 110.3978 | 110.3978 | 110 | 6.0184 | 0.0063243 | 6.0184 | 0.0023417 | 0.023883 | 0.023883 | 17.4725 | 2.4332 | 108.7684 | 108.7684 | 111 | 5.9316 | 0.0064169 | 5.9316 | 0.002376 | 0.023941 | 0.023941 | 18.0068 | 2.5256 | 109.2102 | 109.2102 | 113 | 5.7614 | 0.0066064 | 5.7614 | 0.0024462 | 0.02406 | 0.02406 | 18.9654 | 2.5717 | 110.1226 | 110.1226 | 123 | 4.9865 | 0.007633 | 4.9865 | 0.0028263 | 0.024707 | 0.024707 | 21.6727 | 3.2789 | 112.1228 | 112.1228 | 95 | 7.4359 | 0.0051187 | 7.4359 | 0.0018953 | 0.023123 | 0.023123 | 16.0378 | 1.8377 | 107.9291 | 107.9291
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to FO retrofit | /Door | 1 | 38 | 28 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 30.59% | 84 | 16.6547 | 0.0031763 | 16.6547 | 0.00084621 | 0.02223 | 0.02223 | 9.1773 | 0.90531 | 102.001 | 102.001 | 111 | 10.841 | 0.0048796 | 10.841 | 0.0013 | 0.02348 | 0.02348 | 14.2019 | 1.401 | 106.53 | 106.53 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0011754 | 0.023136 | 0.023136 | 12.7474 | 1.2878 | 105.1886 | 105.1886 | 103 | 12.1711 | 0.0043464 | 12.1711 | 0.0011579 | 0.023088 | 0.023088 | 12.8603 | 1.2991 | 105.2902 | 105.2902 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.001072 | 0.022852 | 0.022852 | 12.191 | 1.1778 | 104.7422 | 104.7422 | 99 | 12.942 | 0.0040875 | 12.942 | 0.001089 | 0.022898 | 0.022898 | 12.1287 | 1.2378 | 104.6199 | 104.6199 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.001072 | 0.022852 | 0.022852 | 12.352 | 1.2312 | 104.8497 | 104.8497 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0011754 | 0.023136 | 0.023136 | 13.6859 | 1.3441 | 106.0707 | 106.0707 | 109 | 11.15 | 0.0047444 | 11.15 | 0.001264 | 0.02338 | 0.02338 | 14.6527 | 1.4309 | 106.9508 | 106.9508 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0013733 | 0.023681 | 0.023681 | 15.7599 | 1.538 | 107.951 | 107.951 | 119 | 9.7287 | 0.0054375 | 9.7287 | 0.0014486 | 0.023889 | 0.023889 | 16.4463 | 1.5643 | 108.6111 | 108.6111 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0013733 | 0.023681 | 0.023681 | 15.0324 | 1.5062 | 107.2552 | 107.2552 | 116 | 10.1252 | 0.0052246 | 10.1252 | 0.0013919 | 0.023733 | 0.023733 | 15.4756 | 1.5617 | 107.6428 | 107.6428 | 123 | 9.2301 | 0.0057312 | 9.2301 | 0.0015269 | 0.024104 | 0.024104 | 17.367 | 1.6945 | 109.4016 | 109.4016 | 126 | 8.8734 | 0.0059616 | 8.8734 | 0.0015883 | 0.024273 | 0.024273 | 17.8675 | 1.945 | 109.6516 | 109.6516 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0011754 | 0.023136 | 0.023136 | 14.5912 | 1.203 | 107.1172 | 107.1172
LT, T8 to FO retrofit | /Door | 1 | 0 | -10 | 38.0621 | 43.7714 | 14.0934 | 0.0199 | 93.729 | 0.32198 | 28.98% | 79 | 9.1087 | 0.0058076 | 9.1087 | 0.0015472 | 0.02416 | 0.02416 | 15.8969 | 1.5682 | 108.0577 | 108.0577 | 106 | 6.3763 | 0.0082964 | 6.3763 | 0.0022103 | 0.025986 | 0.025986 | 22.8753 | 2.2566 | 114.3478 | 114.3478 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.0020021 | 0.025413 | 0.025413 | 20.5703 | 2.078 | 112.2212 | 112.2212 | 98 | 7.1373 | 0.0074117 | 7.1373 | 0.0019746 | 0.025337 | 0.025337 | 20.776 | 2.0987 | 112.4063 | 112.4063 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0018451 | 0.024981 | 0.024981 | 19.8794 | 1.9205 | 111.6879 | 111.6879 | 94 | 7.5367 | 0.0070189 | 7.5367 | 0.00187 | 0.025049 | 0.025049 | 19.7311 | 2.0137 | 111.4464 | 111.4464 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0018451 | 0.024981 | 0.024981 | 20.1419 | 2.0078 | 111.8632 | 111.8632 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.0020021 | 0.025413 | 0.025413 | 22.0847 | 2.169 | 113.6447 | 113.6447 | 104 | 6.5612 | 0.0080625 | 6.5612 | 0.002148 | 0.025815 | 0.025815 | 23.59 | 2.3037 | 115.0153 | 115.0153 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.0023417 | 0.026348 | 0.026348 | 25.4592 | 2.4845 | 116.7037 | 116.7037 | 114 | 5.6781 | 0.0093165 | 5.6781 | 0.0024821 | 0.026734 | 0.026734 | 26.6957 | 2.5391 | 117.8856 | 117.8856 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.0023417 | 0.026348 | 0.026348 | 24.2839 | 2.4332 | 115.5797 | 115.5797 | 111 | 5.9316 | 0.0089184 | 5.9316 | 0.002376 | 0.026442 | 0.026442 | 25.0264 | 2.5256 | 116.2298 | 116.2298 | 118 | 5.3573 | 0.0098744 | 5.3573 | 0.0026307 | 0.027144 | 0.027144 | 28.347 | 2.7657 | 119.3103 | 119.3103 | 121 | 5.1306 | 0.010311 | 5.1306 | 0.0027469 | 0.027464 | 0.027464 | 29.2757 | 3.1868 | 119.8179 | 119.8179 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.0020021 | 0.025413 | 0.025413 | 23.5457 | 1.9412 | 115.3334 | 115.3334
Grocery | [187 empty] | Freezer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
MT, T8 to CC retrofit | /Door | 1 | 38 | 28 | 38.0621 | 43.7714 | 70.9563 | -0.0101 | -121.227 | 1.6211 | 154% | 84 | 16.6547 | 0.0031763 | 16.6547 | 0.0042604 | -0.011184 | -0.011184 | 9.1773 | 22.9482 | -134.9979 | -134.9979 | 111 | 10.841 | 0.0048796 | 10.841 | 0.0065452 | -0.011766 | -0.011766 | 14.2019 | 35.5126 | -142.5377 | -142.5377 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | -0.011606 | -0.011606 | 12.7474 | 32.6426 | -141.1223 | -141.1223 | 103 | 12.1711 | 0.0043464 | 12.1711 | 0.0058299 | -0.011584 | -0.011584 | 12.8603 | 32.9294 | -141.2961 | -141.2961 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.005397 | -0.011473 | -0.011473 | 12.191 | 29.8547 | -138.8907 | -138.8907 | 99 | 12.942 | 0.0040875 | 12.942 | 0.0054827 | -0.011495 | -0.011495 | 12.1287 | 31.3769 | -140.4752 | -140.4752 | 98 | 13.1473 | 0.0040236 | 13.1473 | 0.005397 | -0.011473 | -0.011473 | 12.352 | 31.2104 | -140.0854 | -140.0854 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | -0.011606 | -0.011606 | 13.6859 | 34.0722 | -141.6133 | -141.6133 | 109 | 11.15 | 0.0047444 | 11.15 | 0.0063638 | -0.011719 | -0.011719 | 14.6527 | 36.2713 | -142.8456 | -142.8456 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0069142 | -0.011859 | -0.011859 | 15.7599 | 38.986 | -144.453 | -144.453 | 119 | 9.7287 | 0.0054375 | 9.7287 | 0.0072935 | -0.011956 | -0.011956 | 16.4463 | 39.6515 | -144.4321 | -144.4321 | 115 | 10.2624 | 0.0051547 | 10.2624 | 0.0069142 | -0.011859 | -0.011859 | 15.0324 | 38.1799 | -144.3745 | -144.3745 | 116 | 10.1252 | 0.0052246 | 10.1252 | 0.0070079 | -0.011883 | -0.011883 | 15.4756 | 39.5881 | -145.3395 | -145.3395 | 123 | 9.2301 | 0.0057312 | 9.2301 | 0.0076875 | -0.012056 | -0.012056 | 17.367 | 42.952 | -146.812 | -146.812 | 126 | 8.8734 | 0.0059616 | 8.8734 | 0.0079965 | -0.012135 | -0.012135 | 17.8675 | 49.3022 | -152.6617 | -152.6617 | 104 | 11.9903 | 0.0044119 | 11.9903 | 0.0059178 | -0.011606 | -0.011606 | 14.5912 | 30.4936 | -137.1294 | -137.1294
LT, T8 to CC retrofit | /Door | 1 | 0 | -10 | 38.0621 | 43.7714 | 70.9563 | -0.0101 | -121.227 | 1.6211 | 145.9% | 79 | 9.1087 | 0.0058076 | 9.1087 | 0.00779 | -0.012082 | -0.012082 | 15.8969 | 39.751 | -145.0811 | -145.0811 | 106 | 6.3763 | 0.0082964 | 6.3763 | 0.011128 | -0.012932 | -0.012932 | 22.8753 | 57.2009 | -155.5526 | -155.5526 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | -0.012665 | -0.012665 | 20.5703 | 52.675 | -153.3318 | -153.3318 | 98 | 7.1373 | 0.0074117 | 7.1373 | 0.0099416 | -0.01263 | -0.01263 | 20.776 | 53.198 | -153.649 | -153.649 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0092896 | -0.012464 | -0.012464 | 19.8794 | 48.683 | -150.0305 | -150.0305 | 94 | 7.5367 | 0.0070189 | 7.5367 | 0.0094147 | -0.012496 | -0.012496 | 19.7311 | 51.0442 | -152.5401 | -152.5401 | 93 | 7.6382 | 0.0069257 | 7.6382 | 0.0092896 | -0.012464 | -0.012464 | 20.1419 | 50.8936 | -151.9787 | -151.9787 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | -0.012665 | -0.012665 | 22.0847 | 54.9819 | -154.1241 | -154.1241 | 104 | 6.5612 | 0.0080625 | 6.5612 | 0.010814 | -0.012852 | -0.012852 | 23.59 | 58.3947 | -156.0318 | -156.0318 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.01179 | -0.0131 | -0.0131 | 25.4592 | 62.9794 | -158.7472 | -158.7472 | 114 | 5.6781 | 0.0093165 | 5.6781 | 0.012497 | -0.01328 | -0.01328 | 26.6957 | 64.3623 | -158.8936 | -158.8936 | 110 | 6.0184 | 0.0087897 | 6.0184 | 0.01179 | -0.0131 | -0.0131 | 24.2839 | 61.6772 | -158.6203 | -158.6203 | 111 | 5.9316 | 0.0089184 | 5.9316 | 0.011962 | -0.013144 | -0.013144 | 25.0264 | 64.02 | -160.2207 | -160.2207 | 118 | 5.3573 | 0.0098744 | 5.3573 | 0.013245 | -0.01347 | -0.01347 | 28.347 | 70.1076 | -162.9876 | -162.9876 | 121 | 5.1306 | 0.010311 | 5.1306 | 0.01383 | -0.013619 | -0.013619 | 29.2757 | 80.7809 | -172.7322 | -172.7322 | 99 | 7.0393 | 0.007515 | 7.0393 | 0.01008 | -0.012665 | -0.012665 | 23.5457 | 49.2072 | -146.8886 | -146.8886
Change reference after Copy/paste
41.7659
0
13.2218
21.2863
0
-21.6186
-34.8048
0

## Summary
| Single Compressor System | [41 empty] | Demand w/Interactive Effects
Climate Zone | Representative City and Temperature (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf |  | 1T12 Shelf
|  |  | MT, (2)T12 to LED Canopy |  | LT, (2)T12 to LED Canopy |  | MT, (1)T12 to LED Canopy |  | LT, (1)T12 to LED Canopy |  | MT, (2)T8 to LED Canopy |  | LT, (2)T8 to LED Canopy |  | MT, (1)T8 to LED Canopy |  | LT, (1)T8 to LED Canopy |  | MT, T12 to CC retrofit |  | LT, T12 to CC retrofit |  | MT, (1)T12 to LED Shelf |  | LT, (1)T12 to LED Shelf |  | MT, (1)T8 to LED Shelf |  | LT, (1)T8 to LED Shelf |  | MT, T8 to FO retrofit |  | LT, T8 to FO retrofit |  | MT, T8 to CC retrofit |  | LT, T8 to CC retrofit |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT
|  |  | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Base 4' (2)T12 | Measure 4' LED | Base 4' (2)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED
1 | Arcata - 69oF | /Fixture | 0.066012 | 310.0498 | 0.066628 | 311.99 | 0.060739 | 279.3795 | 0.062327 | 283.644 | 0.041436 | 195.4578 | 0.041689 | 196.364 | 0.011953 | 56.5903 | 0.012211 | 57.5093 | 0.040503 | 113.2137 | 0.040067 | 111.0944 | 0.071204 | 323.884 | 0.073113 | 328.4458 | 0.022418 | 103.6997 | 0.022997 | 105.3462 | 0.023977 | 108.2042 | 0.024915 | 110.5945 | -0.011997 | -145.3249 | -0.012433 | -149.3042 | 0.087558 | 0.021546 | 0.088836 | 0.022208 | 0.082285 | 0.021546 | 0.084534 | 0.022208 | 0.062982 | 0.021546 | 0.063897 | 0.022208 | 0.033499 | 0.021546 | 0.041534 | 0.020488 | 0.082285 | 0.011081 | 0.077397 | 0.013141 | 0.033499 | 0.011081 | 0.041534 | 0.011421
2 | Santa Rosa - 96oF | /Fixture | 0.067291 | 315.7846 | 0.068454 | 319.7345 | 0.064035 | 291.984 | 0.067035 | 300.6654 | 0.041962 | 198.1363 | 0.04244 | 199.9811 | 0.012488 | 59.3066 | 0.012974 | 61.1774 | 0.039597 | 106.9496 | 0.038773 | 102.6351 | 0.075168 | 337.3673 | 0.078775 | 346.6539 | 0.02362 | 108.5662 | 0.024714 | 111.9181 | 0.025923 | 115.2692 | 0.027694 | 120.1353 | -0.012903 | -157.0866 | -0.013727 | -165.1876 | 0.090211 | 0.02292 | 0.092625 | 0.024171 | 0.086955 | 0.02292 | 0.091205 | 0.024171 | 0.064882 | 0.02292 | 0.066611 | 0.024171 | 0.035408 | 0.02292 | 0.048205 | 0.021497 | 0.086955 | 0.011788 | 0.080111 | 0.015104 | 0.035408 | 0.011788 | 0.048205 | 0.012431
3 | Oakland - 89oF | /Fixture | 0.066888 | 313.7521 | 0.067907 | 317.136 | 0.062996 | 287.7412 | 0.065623 | 295.2277 | 0.041796 | 197.0591 | 0.042215 | 198.6116 | 0.012319 | 58.2178 | 0.012745 | 59.7929 | 0.039883 | 108.0965 | 0.039161 | 104.1653 | 0.073918 | 332.8916 | 0.077078 | 340.9139 | 0.023241 | 106.9077 | 0.024199 | 109.7937 | 0.02531 | 112.8843 | 0.026861 | 117.0791 | -0.012617 | -154.4829 | -0.013339 | -161.7657 | 0.089375 | 0.022487 | 0.091489 | 0.023582 | 0.085483 | 0.022487 | 0.089206 | 0.023582 | 0.064283 | 0.022487 | 0.065797 | 0.023582 | 0.034806 | 0.022487 | 0.046206 | 0.021195 | 0.085483 | 0.011565 | 0.079297 | 0.014516 | 0.034806 | 0.011565 | 0.046206 | 0.012128
4 | Sunnyvale - 88oF | /Fixture | 0.066835 | 313.8899 | 0.067833 | 317.2807 | 0.06286 | 288.0453 | 0.065434 | 295.5469 | 0.041774 | 197.1227 | 0.042185 | 198.6785 | 0.012297 | 58.2823 | 0.012715 | 59.8608 | 0.03992 | 107.9399 | 0.039213 | 104.0013 | 0.073755 | 333.2173 | 0.07685 | 341.2557 | 0.023192 | 107.025 | 0.024131 | 109.9169 | 0.02523 | 113.0547 | 0.026749 | 117.2581 | -0.01258 | -154.7745 | -0.013287 | -162.0711 | 0.089265 | 0.02243 | 0.091337 | 0.023504 | 0.085291 | 0.02243 | 0.088938 | 0.023504 | 0.064204 | 0.02243 | 0.065688 | 0.023504 | 0.034728 | 0.02243 | 0.045938 | 0.021154 | 0.085291 | 0.011536 | 0.079188 | 0.014437 | 0.034728 | 0.011536 | 0.045938 | 0.012088
5 | Santa Maria - 83oF | /Fixture | 0.066588 | 313.3807 | 0.067483 | 316.519 | 0.062222 | 286.5158 | 0.064531 | 293.3749 | 0.041672 | 197.1188 | 0.042041 | 198.6065 | 0.012194 | 58.2718 | 0.012568 | 59.7799 | 0.040095 | 110.4592 | 0.039461 | 107.2152 | 0.072988 | 331.466 | 0.075764 | 338.7925 | 0.022959 | 106.4718 | 0.023801 | 109.1236 | 0.024853 | 112.2098 | 0.026216 | 116.0556 | -0.012405 | -150.8677 | -0.013039 | -157.0358 | 0.088752 | 0.022164 | 0.09061 | 0.023127 | 0.084387 | 0.022164 | 0.087658 | 0.023127 | 0.063837 | 0.022164 | 0.065168 | 0.023127 | 0.034358 | 0.022164 | 0.044658 | 0.020961 | 0.084387 | 0.011399 | 0.078668 | 0.01406 | 0.034358 | 0.011399 | 0.044658 | 0.011894
6 | Torrance - 86⁰F | /Fixture | 0.066733 | 313.4191 | 0.06769 | 316.6565 | 0.062597 | 287.1013 | 0.065065 | 294.2846 | 0.041732 | 196.8511 | 0.042126 | 198.3245 | 0.012254 | 58.0082 | 0.012655 | 59.5036 | 0.040062 | 108.5389 | 0.039413 | 104.8578 | 0.073439 | 332.233 | 0.076406 | 339.9361 | 0.023096 | 106.6523 | 0.023996 | 109.4195 | 0.024925 | 111.9815 | 0.02632 | 115.8189 | -0.012438 | -153.4858 | -0.013087 | -160.2678 | 0.089054 | 0.022321 | 0.09104 | 0.023349 | 0.084918 | 0.022321 | 0.088414 | 0.023349 | 0.064053 | 0.022321 | 0.065475 | 0.023349 | 0.034575 | 0.022321 | 0.045414 | 0.021075 | 0.084918 | 0.011479 | 0.078975 | 0.014283 | 0.034575 | 0.011479 | 0.045414 | 0.012008
7 | San Diego - 83oF | /Fixture | 0.066588 | 313.4068 | 0.067483 | 316.5504 | 0.062222 | 286.8528 | 0.064531 | 293.7819 | 0.041672 | 196.9716 | 0.042041 | 198.4286 | 0.012194 | 58.1269 | 0.012568 | 59.6048 | 0.040095 | 109.0925 | 0.039461 | 105.5641 | 0.072988 | 331.905 | 0.075764 | 339.3228 | 0.022959 | 106.5765 | 0.023801 | 109.25 | 0.024853 | 112.3902 | 0.026216 | 116.2736 | -0.012405 | -152.8724 | -0.013039 | -159.4577 | 0.088752 | 0.022164 | 0.09061 | 0.023127 | 0.084387 | 0.022164 | 0.087658 | 0.023127 | 0.063837 | 0.022164 | 0.065168 | 0.023127 | 0.034358 | 0.022164 | 0.044658 | 0.020961 | 0.084387 | 0.011399 | 0.078668 | 0.01406 | 0.034358 | 0.011399 | 0.044658 | 0.011894
8 | Fullerton - 94⁰F | /Fixture | 0.067169 | 316.3917 | 0.068291 | 320.454 | 0.063722 | 293.2709 | 0.066615 | 302.1888 | 0.041912 | 198.4468 | 0.042373 | 200.3502 | 0.012437 | 59.6207 | 0.012906 | 61.5508 | 0.039883 | 107.946 | 0.039161 | 103.9818 | 0.074791 | 338.7307 | 0.07827 | 348.2673 | 0.023506 | 109.0674 | 0.024561 | 112.5115 | 0.02531 | 114.3588 | 0.026861 | 118.8766 | -0.012617 | -155.3037 | -0.013339 | -162.7662 | 0.089959 | 0.022789 | 0.092287 | 0.023996 | 0.086511 | 0.022789 | 0.09061 | 0.023996 | 0.064701 | 0.022789 | 0.066369 | 0.023996 | 0.035226 | 0.022789 | 0.04761 | 0.021407 | 0.086511 | 0.01172 | 0.079869 | 0.014929 | 0.035226 | 0.01172 | 0.04761 | 0.012341
9 | Burbank-Glendale - 96⁰F | /Fixture | 0.067291 | 316.9223 | 0.068454 | 321.1292 | 0.064035 | 294.3729 | 0.067035 | 303.594 | 0.041962 | 198.7312 | 0.04244 | 200.7104 | 0.012488 | 59.9081 | 0.012974 | 61.9149 | 0.039683 | 106.8493 | 0.038889 | 102.5385 | 0.075168 | 339.8915 | 0.078775 | 349.7484 | 0.02362 | 109.4987 | 0.024714 | 113.0613 | 0.025738 | 115.9082 | 0.027446 | 120.8883 | -0.012817 | -157.4917 | -0.013611 | -165.6346 | 0.090211 | 0.02292 | 0.092625 | 0.024171 | 0.086955 | 0.02292 | 0.091205 | 0.024171 | 0.064882 | 0.02292 | 0.066611 | 0.024171 | 0.035408 | 0.02292 | 0.048205 | 0.021497 | 0.086955 | 0.011788 | 0.080111 | 0.015104 | 0.035408 | 0.011788 | 0.048205 | 0.012431
10 | Riverside - 100oF | /Fixture | 0.067552 | 317.9554 | 0.068798 | 322.4234 | 0.064708 | 296.6296 | 0.067921 | 306.4214 | 0.042069 | 199.2217 | 0.042582 | 201.3248 | 0.012597 | 60.4053 | 0.013118 | 62.5376 | 0.039413 | 105.1787 | 0.03853 | 100.4347 | 0.075977 | 342.3016 | 0.079841 | 352.768 | 0.023866 | 110.3713 | 0.025038 | 114.1545 | 0.026321 | 117.877 | 0.028218 | 123.3664 | -0.013087 | -160.6634 | -0.01397 | -169.6281 | 0.090752 | 0.023201 | 0.093339 | 0.024541 | 0.087909 | 0.023201 | 0.092462 | 0.024541 | 0.06527 | 0.023201 | 0.067122 | 0.024541 | 0.035797 | 0.023201 | 0.049462 | 0.021687 | 0.087909 | 0.011932 | 0.080622 | 0.015474 | 0.035797 | 0.011932 | 0.049462 | 0.012621
11 | Red Bluff - 104oF | /Fixture | 0.067839 | 319.2597 | 0.06917 | 324.0223 | 0.065449 | 299.1787 | 0.06888 | 309.5456 | 0.042187 | 200.0119 | 0.042735 | 202.2937 | 0.012717 | 61.2016 | 0.013273 | 63.514 | 0.039209 | 105.2734 | 0.038266 | 100.5528 | 0.076868 | 344.9393 | 0.080994 | 356.0007 | 0.024136 | 111.3844 | 0.025387 | 115.3962 | 0.026758 | 119.3154 | 0.028784 | 125.1293 | -0.013291 | -161.123 | -0.014234 | -170.1884 | 0.091349 | 0.02351 | 0.09411 | 0.02494 | 0.088958 | 0.02351 | 0.09382 | 0.02494 | 0.065697 | 0.02351 | 0.067675 | 0.02494 | 0.036226 | 0.02351 | 0.05082 | 0.021893 | 0.088958 | 0.012091 | 0.081175 | 0.015873 | 0.036226 | 0.012091 | 0.05082 | 0.012826
12 | Sacramento - 100oF | /Fixture | 0.067552 | 316.8669 | 0.068798 | 321.0875 | 0.064708 | 294.5382 | 0.067921 | 303.8545 | 0.042069 | 198.5418 | 0.042582 | 200.4903 | 0.012597 | 59.7206 | 0.013118 | 61.6973 | 0.039413 | 104.9282 | 0.03853 | 100.1272 | 0.075977 | 340.1488 | 0.079841 | 350.1259 | 0.023866 | 109.5364 | 0.025038 | 113.1298 | 0.026321 | 116.6956 | 0.028218 | 121.9164 | -0.013087 | -160.53 | -0.01397 | -169.4644 | 0.090752 | 0.023201 | 0.093339 | 0.024541 | 0.087909 | 0.023201 | 0.092462 | 0.024541 | 0.06527 | 0.023201 | 0.067122 | 0.024541 | 0.035797 | 0.023201 | 0.049462 | 0.021687 | 0.087909 | 0.011932 | 0.080622 | 0.015474 | 0.035797 | 0.011932 | 0.049462 | 0.012621
13 | Fresno - 101oF | /Fixture | 0.067621 | 317.4164 | 0.068888 | 321.764 | 0.049225 | 249.4459 | 0.068154 | 305.4516 | 0.042097 | 198.7473 | 0.042619 | 200.7434 | 0.012626 | 59.9304 | 0.013156 | 61.9557 | 0.039364 | 103.8982 | 0.038466 | 98.8607 | 0.076191 | 341.5621 | 0.08012 | 351.8652 | 0.023931 | 110.0293 | 0.025122 | 113.7364 | 0.026426 | 117.4203 | 0.028355 | 122.8083 | -0.013136 | -162.2837 | -0.014034 | -171.6211 | 0.090896 | 0.023275 | 0.093526 | 0.024637 | 0.0725 | 0.023275 | 0.092791 | 0.024637 | 0.065373 | 0.023275 | 0.067256 | 0.024637 | 0.035901 | 0.023275 | 0.049791 | 0.021737 | 0.088161 | 0.01197 | 0.080756 | 0.015571 | 0.035901 | 0.01197 | 0.049791 | 0.012671
14 | Palmdale - 103⁰F | /Fixture | 0.067765 | 318.7653 | 0.069074 | 323.4185 | 0.065257 | 298.402 | 0.068633 | 308.5989 | 0.042157 | 199.6044 | 0.042695 | 201.795 | 0.012686 | 60.7933 | 0.013233 | 63.0144 | 0.038984 | 102.4081 | 0.037979 | 97.0647 | 0.076637 | 344.1953 | 0.080696 | 355.0947 | 0.024066 | 111.0563 | 0.025297 | 114.9961 | 0.027242 | 121.0974 | 0.029401 | 127.2836 | -0.013516 | -165.9049 | -0.014521 | -176.0037 | 0.091194 | 0.023429 | 0.093911 | 0.024837 | 0.088686 | 0.023429 | 0.09347 | 0.024837 | 0.065586 | 0.023429 | 0.067533 | 0.024837 | 0.036115 | 0.023429 | 0.05047 | 0.02184 | 0.088686 | 0.012049 | 0.081033 | 0.01577 | 0.036115 | 0.012049 | 0.05047 | 0.012773
15 | Palm Springs-Intl - 113⁰F | /Fixture | 0.068605 | 321.3752 | 0.070144 | 326.5413 | 0.067424 | 305.7554 | 0.071391 | 317.442 | 0.042503 | 199.9017 | 0.043136 | 202.1252 | 0.013037 | 61.1205 | 0.01368 | 63.3806 | 0.038799 | 94.889 | 0.037744 | 87.8858 | 0.079243 | 352.5153 | 0.084013 | 365.1099 | 0.024856 | 113.7483 | 0.026303 | 118.2302 | 0.02764 | 121.9087 | 0.029906 | 128.2422 | -0.013701 | -176.8599 | -0.014756 | -189.3637 | 0.092938 | 0.024333 | 0.096131 | 0.025987 | 0.091757 | 0.024333 | 0.097378 | 0.025987 | 0.066836 | 0.024333 | 0.069123 | 0.025987 | 0.03737 | 0.024333 | 0.054378 | 0.022431 | 0.091757 | 0.012514 | 0.082623 | 0.01692 | 0.03737 | 0.012514 | 0.054378 | 0.013365
16 | Blue Canyon - 85⁰F | /Fixture | 0.066683 | 316.1324 | 0.06762 | 319.9173 | 0.06247 | 291.0971 | 0.064884 | 299.0654 | 0.041712 | 199.2399 | 0.042097 | 201.2074 | 0.012234 | 60.3996 | 0.012625 | 62.3893 | 0.039883 | 113.7632 | 0.039161 | 111.073 | 0.073285 | 335.9551 | 0.076189 | 344.3806 | 0.023049 | 108.3741 | 0.02393 | 111.4825 | 0.02531 | 116.1081 | 0.026861 | 121.0089 | -0.012617 | -147.8087 | -0.013339 | -153.6299 | 0.088951 | 0.022267 | 0.090894 | 0.023274 | 0.084737 | 0.022267 | 0.088158 | 0.023274 | 0.063979 | 0.022267 | 0.065371 | 0.023274 | 0.034501 | 0.022267 | 0.045158 | 0.021036 | 0.084737 | 0.011452 | 0.078871 | 0.014208 | 0.034501 | 0.011452 | 0.045158 | 0.01197
|  |  | 0.066012 | 310.0498 | 0.066628 | 311.99 | [20 empty] | 0.022418 | 103.6997 | 0.022997 | 105.3462 | 0.023977 | 108.2042 | 0.024915 | 110.5945 | -0.013701 | -176.8599 | -0.014756 | -189.3637
|  |  | 0.068605 | 321.3752 | 0.070144 | 326.5413 | [20 empty] | 0.024856 | 113.7483 | 0.026303 | 118.2302 | 0.02764 | 121.9087 | 0.029906 | 128.2422 | -0.011997 | -145.3249 | -0.012433 | -149.3042
Multiplex Compressor System
Climate Zone | Representative City and Temperature (Summer Design Dry-Bubl, ASHRAE Climatic Region X Data, 0.5% Column) | Measure Unit | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | Grocery |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf |  | 1T12 Shelf
|  |  | MT, (2)T12 to LED Canopy |  | LT, (2)T12 to LED Canopy |  | MT, (1)T12 to LED Canopy |  | LT, (1)T12 to LED Canopy |  | MT, (2)T8 to LED Canopy |  | LT, (2)T8 to LED Canopy |  | MT, (1)T8 to LED Canopy |  | LT, (1)T8 to LED Canopy |  | MT, T12 to CC retrofit |  | LT, T12 to CC retrofit |  | MT, (1)T12 to LED Shelf |  | LT, (1)T12 to LED Shelf |  | MT, (1)T8 to LED Shelf |  | LT, (1)T8 to LED Shelf |  | MT, T8 to FO retrofit |  | LT, T8 to FO retrofit |  | MT, T8 to CC retrofit |  | LT, T8 to CC retrofit |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT
|  |  | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Demand Savings (DkW/unit) | Energy Savings (DkWh/unit) | Base 4' (2)T12 | Measure 4' LED | Base 4' (2)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED
1 | Arcata - 69oF | /Fixture | 0.064864 | 305.0145 | 0.066132 | 309.9309 | 0.05778 | 268.3126 | 0.061049 | 279.1183 | 0.040963 | 193.106 | 0.041485 | 195.4023 | 0.011473 | 54.2053 | 0.012003 | 56.534 | 0.041316 | 118.7138 | 0.040418 | 113.3436 | 0.067646 | 312.0455 | 0.071577 | 323.6045 | 0.021339 | 99.4268 | 0.022531 | 103.5988 | 0.02223 | 102.001 | 0.02416 | 108.0577 | -0.011184 | -134.9979 | -0.012082 | -145.0811 | 0.085176 | 0.020312 | 0.087808 | 0.021675 | 0.078092 | 0.020312 | 0.082724 | 0.021675 | 0.061275 | 0.020312 | 0.06316 | 0.021675 | 0.031785 | 0.020312 | 0.039724 | 0.020214 | 0.078092 | 0.010446 | 0.07666 | 0.012609 | 0.031785 | 0.010446 | 0.039724 | 0.011147
2 | Santa Rosa - 96oF | /Fixture | 0.065685 | 308.6907 | 0.067332 | 315.0366 | 0.059896 | 276.3926 | 0.064141 | 290.34 | 0.041301 | 194.8231 | 0.041979 | 197.7869 | 0.011816 | 55.9466 | 0.012505 | 58.9523 | 0.040734 | 114.6982 | 0.039568 | 107.7666 | 0.070191 | 320.6889 | 0.075295 | 335.6087 | 0.022111 | 102.5465 | 0.023659 | 107.9315 | 0.02348 | 106.53 | 0.025986 | 114.3478 | -0.011766 | -142.5377 | -0.012932 | -155.5526 | 0.08688 | 0.021194 | 0.090296 | 0.022964 | 0.081091 | 0.021194 | 0.087106 | 0.022964 | 0.062495 | 0.021194 | 0.064943 | 0.022964 | 0.033011 | 0.021194 | 0.044106 | 0.020877 | 0.081091 | 0.0109 | 0.078443 | 0.013898 | 0.033011 | 0.0109 | 0.044106 | 0.01181
3 | Oakland - 89oF | /Fixture | 0.06546 | 307.5442 | 0.066955 | 313.2172 | 0.059315 | 274.0068 | 0.06317 | 286.5578 | 0.041208 | 194.2111 | 0.041824 | 196.8137 | 0.011722 | 55.3281 | 0.012347 | 57.9688 | 0.040894 | 115.3086 | 0.039835 | 108.7179 | 0.069492 | 318.1744 | 0.074128 | 331.6236 | 0.021899 | 101.6131 | 0.023305 | 106.4515 | 0.023136 | 105.1886 | 0.025413 | 112.2212 | -0.011606 | -141.1223 | -0.012665 | -153.3318 | 0.086412 | 0.020952 | 0.089515 | 0.02256 | 0.080267 | 0.020952 | 0.08573 | 0.02256 | 0.06216 | 0.020952 | 0.064383 | 0.02256 | 0.032674 | 0.020952 | 0.04273 | 0.020669 | 0.080267 | 0.010775 | 0.077883 | 0.013493 | 0.032674 | 0.010775 | 0.04273 | 0.011602
4 | Sunnyvale - 88oF | /Fixture | 0.065428 | 307.6263 | 0.066906 | 313.3668 | 0.059234 | 274.1881 | 0.063042 | 286.8881 | 0.041195 | 194.249 | 0.041803 | 196.8828 | 0.011709 | 55.3665 | 0.012327 | 58.0388 | 0.040916 | 115.2152 | 0.03987 | 108.5474 | 0.069394 | 318.3685 | 0.073974 | 331.9773 | 0.021869 | 101.683 | 0.023258 | 106.5789 | 0.023088 | 105.2902 | 0.025337 | 112.4063 | -0.011584 | -141.2961 | -0.01263 | -153.649 | 0.086346 | 0.020918 | 0.089412 | 0.022506 | 0.080152 | 0.020918 | 0.085548 | 0.022506 | 0.062113 | 0.020918 | 0.064309 | 0.022506 | 0.032627 | 0.020918 | 0.042548 | 0.020641 | 0.080152 | 0.010758 | 0.077809 | 0.013439 | 0.032627 | 0.010758 | 0.042548 | 0.011575
5 | Santa Maria - 83oF | /Fixture | 0.065273 | 307.287 | 0.066671 | 312.9548 | 0.058833 | 273.1973 | 0.062438 | 285.5849 | 0.041131 | 194.2302 | 0.041707 | 196.9169 | 0.011644 | 55.3436 | 0.012229 | 58.0672 | 0.041027 | 116.7582 | 0.040036 | 110.8994 | 0.068912 | 317.2398 | 0.073248 | 330.4717 | 0.021723 | 101.3228 | 0.023038 | 106.1119 | 0.022852 | 104.7422 | 0.024981 | 111.6879 | -0.011473 | -138.8907 | -0.012464 | -150.0305 | 0.086024 | 0.020751 | 0.088926 | 0.022254 | 0.079584 | 0.020751 | 0.084693 | 0.022254 | 0.061882 | 0.020751 | 0.063961 | 0.022254 | 0.032395 | 0.020751 | 0.041693 | 0.020512 | 0.079584 | 0.010672 | 0.077461 | 0.013188 | 0.032395 | 0.010672 | 0.041693 | 0.011445
6 | Torrance - 86⁰F | /Fixture | 0.065365 | 307.3374 | 0.066809 | 312.9438 | 0.059072 | 273.6073 | 0.062793 | 286.0467 | 0.041169 | 194.0832 | 0.041763 | 196.6348 | 0.011683 | 55.1992 | 0.012286 | 57.7887 | 0.041005 | 115.6007 | 0.040004 | 109.0522 | 0.069199 | 317.7624 | 0.073674 | 331.1021 | 0.02181 | 101.4539 | 0.023167 | 106.246 | 0.022898 | 104.6199 | 0.025049 | 111.4464 | -0.011495 | -140.4752 | -0.012496 | -152.5401 | 0.086216 | 0.020851 | 0.089211 | 0.022402 | 0.079923 | 0.020851 | 0.085196 | 0.022402 | 0.06202 | 0.020851 | 0.064166 | 0.022402 | 0.032534 | 0.020851 | 0.042196 | 0.020588 | 0.079923 | 0.010723 | 0.077666 | 0.013336 | 0.032534 | 0.010723 | 0.042196 | 0.011521
7 | San Diego - 83oF | /Fixture | 0.065273 | 307.3025 | 0.066671 | 312.9801 | 0.058833 | 273.3981 | 0.062438 | 285.9124 | 0.041131 | 194.1424 | 0.041707 | 196.7738 | 0.011644 | 55.2572 | 0.012229 | 57.9263 | 0.041027 | 115.9438 | 0.040036 | 109.5714 | 0.068912 | 317.5014 | 0.073248 | 330.8983 | 0.021723 | 101.3852 | 0.023038 | 106.2136 | 0.022852 | 104.8497 | 0.024981 | 111.8632 | -0.011473 | -140.0854 | -0.012464 | -151.9787 | 0.086024 | 0.020751 | 0.088926 | 0.022254 | 0.079584 | 0.020751 | 0.084693 | 0.022254 | 0.061882 | 0.020751 | 0.063961 | 0.022254 | 0.032395 | 0.020751 | 0.041693 | 0.020512 | 0.079584 | 0.010672 | 0.077461 | 0.013188 | 0.032395 | 0.010672 | 0.041693 | 0.011445
8 | Fullerton - 94⁰F | /Fixture | 0.06562 | 309.085 | 0.067219 | 315.6633 | 0.059728 | 277.231 | 0.063851 | 291.672 | 0.041274 | 195.0233 | 0.041932 | 198.1055 | 0.011789 | 56.1492 | 0.012458 | 59.2747 | 0.040894 | 115.2185 | 0.039835 | 108.5726 | 0.069988 | 321.5778 | 0.074946 | 337.0208 | 0.02205 | 102.8728 | 0.023553 | 108.4499 | 0.023136 | 106.0707 | 0.025413 | 113.6447 | -0.011606 | -141.6133 | -0.012665 | -154.1241 | 0.086744 | 0.021124 | 0.090062 | 0.022843 | 0.080852 | 0.021124 | 0.086694 | 0.022843 | 0.062399 | 0.021124 | 0.064775 | 0.022843 | 0.032914 | 0.021124 | 0.043694 | 0.020815 | 0.080852 | 0.010864 | 0.078275 | 0.013777 | 0.032914 | 0.010864 | 0.043694 | 0.011748
9 | Burbank-Glendale - 96⁰F | /Fixture | 0.065685 | 309.3668 | 0.067332 | 316.1256 | 0.059896 | 277.8123 | 0.064141 | 292.6268 | 0.041301 | 195.1766 | 0.041979 | 198.3564 | 0.011816 | 56.3041 | 0.012505 | 59.5281 | 0.040781 | 114.603 | 0.039648 | 107.6222 | 0.070191 | 322.1889 | 0.075295 | 338.0249 | 0.022111 | 103.1007 | 0.023659 | 108.8241 | 0.02338 | 106.9508 | 0.025815 | 115.0153 | -0.011719 | -142.8456 | -0.012852 | -156.0318 | 0.08688 | 0.021194 | 0.090296 | 0.022964 | 0.081091 | 0.021194 | 0.087106 | 0.022964 | 0.062495 | 0.021194 | 0.064943 | 0.022964 | 0.033011 | 0.021194 | 0.044106 | 0.020877 | 0.081091 | 0.0109 | 0.078443 | 0.013898 | 0.033011 | 0.0109 | 0.044106 | 0.01181
10 | Riverside - 100oF | /Fixture | 0.065818 | 309.876 | 0.06757 | 317.0003 | 0.060238 | 278.9238 | 0.064754 | 294.5367 | 0.041356 | 195.4188 | 0.042076 | 198.7721 | 0.011872 | 56.5495 | 0.012604 | 59.9495 | 0.040641 | 113.7571 | 0.0394 | 106.1927 | 0.070602 | 323.3758 | 0.076033 | 340.0644 | 0.022236 | 103.5305 | 0.023883 | 109.5627 | 0.023681 | 107.951 | 0.026348 | 116.7037 | -0.011859 | -144.453 | -0.0131 | -158.7472 | 0.087155 | 0.021337 | 0.09079 | 0.02322 | 0.081575 | 0.021337 | 0.087974 | 0.02322 | 0.062693 | 0.021337 | 0.065296 | 0.02322 | 0.033209 | 0.021337 | 0.044974 | 0.021008 | 0.081575 | 0.010973 | 0.078796 | 0.014153 | 0.033209 | 0.010973 | 0.044974 | 0.011942
11 | Red Bluff - 104oF | /Fixture | 0.065954 | 310.491 | 0.067824 | 318.0884 | 0.060589 | 280.0916 | 0.065409 | 296.6292 | 0.041412 | 195.8108 | 0.042181 | 199.4507 | 0.011929 | 56.9441 | 0.01271 | 60.6329 | 0.040544 | 113.9646 | 0.03922 | 106.4343 | 0.071024 | 324.5734 | 0.07682 | 342.219 | 0.022364 | 103.9981 | 0.024121 | 110.3978 | 0.023889 | 108.6111 | 0.026734 | 117.8856 | -0.011956 | -144.4321 | -0.01328 | -158.8936 | 0.087438 | 0.021483 | 0.091317 | 0.023493 | 0.082073 | 0.021483 | 0.088902 | 0.023493 | 0.062895 | 0.021483 | 0.065674 | 0.023493 | 0.033412 | 0.021483 | 0.045902 | 0.021149 | 0.082073 | 0.011049 | 0.079174 | 0.014426 | 0.033412 | 0.011049 | 0.045902 | 0.012082
12 | Sacramento - 100oF | /Fixture | 0.065818 | 309.235 | 0.06757 | 315.9647 | 0.060238 | 277.692 | 0.064754 | 292.5469 | 0.041356 | 195.0184 | 0.042076 | 198.1253 | 0.011872 | 56.1463 | 0.012604 | 59.2981 | 0.040641 | 113.6095 | 0.0394 | 105.9544 | 0.070602 | 322.1079 | 0.076033 | 338.0162 | 0.022236 | 103.0388 | 0.023883 | 108.7684 | 0.023681 | 107.2552 | 0.026348 | 115.5797 | -0.011859 | -144.3745 | -0.0131 | -158.6203 | 0.087155 | 0.021337 | 0.09079 | 0.02322 | 0.081575 | 0.021337 | 0.087974 | 0.02322 | 0.062693 | 0.021337 | 0.065296 | 0.02322 | 0.033209 | 0.021337 | 0.044974 | 0.021008 | 0.081575 | 0.010973 | 0.078796 | 0.014153 | 0.033209 | 0.010973 | 0.044974 | 0.011942
13 | Fresno - 101oF | /Fixture | 0.065851 | 309.527 | 0.067632 | 316.4558 | 0.051127 | 251.1417 | 0.064914 | 293.7112 | 0.041369 | 195.1249 | 0.042102 | 198.3062 | 0.011886 | 56.2551 | 0.01263 | 59.4829 | 0.040617 | 113.0395 | 0.039356 | 105.0112 | 0.070706 | 322.8654 | 0.076225 | 339.2857 | 0.022267 | 103.3021 | 0.023941 | 109.2102 | 0.023733 | 107.6428 | 0.026442 | 116.2298 | -0.011883 | -145.3395 | -0.013144 | -160.2207 | 0.087225 | 0.021373 | 0.090918 | 0.023287 | 0.0725 | 0.021373 | 0.088201 | 0.023287 | 0.062743 | 0.021373 | 0.065389 | 0.023287 | 0.033259 | 0.021373 | 0.045201 | 0.021043 | 0.081698 | 0.010992 | 0.078889 | 0.01422 | 0.033259 | 0.010992 | 0.045201 | 0.011976
14 | Palmdale - 103⁰F | /Fixture | 0.06592 | 310.2443 | 0.067759 | 317.6625 | 0.0605 | 279.7294 | 0.065241 | 295.9853 | 0.041397 | 195.593 | 0.042154 | 199.0853 | 0.011914 | 56.7262 | 0.012683 | 60.267 | 0.040444 | 112.5105 | 0.03903 | 103.9517 | 0.070917 | 324.2364 | 0.076618 | 341.6122 | 0.022331 | 103.8419 | 0.02406 | 110.1226 | 0.024104 | 109.4016 | 0.027144 | 119.3103 | -0.012056 | -146.812 | -0.01347 | -162.9876 | 0.087366 | 0.021446 | 0.091182 | 0.023423 | 0.081947 | 0.021446 | 0.088665 | 0.023423 | 0.062844 | 0.021446 | 0.065577 | 0.023423 | 0.033361 | 0.021446 | 0.045665 | 0.021113 | 0.081947 | 0.01103 | 0.079077 | 0.014356 | 0.033361 | 0.01103 | 0.045665 | 0.012046
15 | Palm Springs-Intl - 113⁰F | /Fixture | 0.066284 | 311.2139 | 0.068446 | 319.5016 | 0.061439 | 282.7686 | 0.067014 | 301.517 | 0.041547 | 195.5282 | 0.042437 | 199.0953 | 0.012067 | 56.6749 | 0.012971 | 60.3008 | 0.040365 | 108.442 | 0.038881 | 97.2008 | 0.072046 | 327.7425 | 0.07875 | 347.9475 | 0.022674 | 104.9327 | 0.024707 | 112.1228 | 0.024273 | 109.6516 | 0.027464 | 119.8179 | -0.012135 | -152.6617 | -0.013619 | -172.7322 | 0.088122 | 0.021838 | 0.092609 | 0.024162 | 0.083277 | 0.021838 | 0.091176 | 0.024162 | 0.063385 | 0.021838 | 0.066599 | 0.024162 | 0.033905 | 0.021838 | 0.048176 | 0.021493 | 0.083277 | 0.011231 | 0.080099 | 0.015096 | 0.033905 | 0.011231 | 0.048176 | 0.012426
16 | Blue Canyon - 85⁰F | /Fixture | 0.065334 | 308.9511 | 0.066762 | 315.5907 | 0.058992 | 275.9784 | 0.062672 | 289.9566 | 0.041157 | 195.5068 | 0.041744 | 198.9583 | 0.01167 | 56.6243 | 0.012267 | 60.1148 | 0.040894 | 118.6987 | 0.039835 | 114.1885 | 0.069103 | 319.969 | 0.073529 | 334.7492 | 0.021781 | 102.4763 | 0.023123 | 107.9291 | 0.023136 | 107.1172 | 0.025413 | 115.3334 | -0.011606 | -137.1294 | -0.012665 | -146.8886 | 0.086152 | 0.020817 | 0.089114 | 0.022352 | 0.079809 | 0.020817 | 0.085024 | 0.022352 | 0.061974 | 0.020817 | 0.064096 | 0.022352 | 0.032487 | 0.020817 | 0.042024 | 0.020562 | 0.079809 | 0.010706 | 0.077596 | 0.013285 | 0.032487 | 0.010706 | 0.042024 | 0.011495
[39 empty] | LT-89513 |  |  |  | LT-97154 |  |  |  | LT-17642 | [7 empty] | LT-20643 |  |  |  | LT-30954
|  |  | #REF! | #REF! | [22 empty] | #REF! | #REF! |  |  | #REF! | #REF! |  |  | #REF! | #REF! |  |  | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf
|  |  | #REF! | #REF! | [22 empty] | #REF! | #REF! |  |  | #REF! | #REF! |  |  | #REF! | #REF! |  |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT
|  | Single | [36 empty] | Base 4' (2)T12 | Measure 4' LED | Base 4' (2)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED
|  | 6 | [36 empty] | 0.089054 | 0.022321 | 0.09104 | 0.023349 | 0.084918 | 0.022321 | 0.088414 | 0.023349 | 0.064053 | 0.022321 | 0.065475 | 0.023349 | 0.034575 | 0.022321 | 0.045414 | 0.021075 | 0.084918 | 0.011479 | 0.078975 | 0.014283 | 0.034575 | 0.011479 |  |  | 0.041732
|  | 8 | [24 empty] | 16.6 | 26.56 | [10 empty] | 0.089959 | 0.022789 | 0.092287 | 0.023996 | 0.086511 | 0.022789 | 0.09061 | 0.023996 | 0.064701 | 0.022789 | 0.066369 | 0.023996 | 0.035226 | 0.022789 | 0.04761 | 0.021407 | 0.086511 | 0.01172 | 0.079869 | 0.014929 | 0.035226 | 0.01172
|  | 9 | [24 empty] | 6 | 9.6 | [10 empty] | 0.090211 | 0.02292 | 0.092625 | 0.024171 | 0.086955 | 0.02292 | 0.091205 | 0.024171 | 0.064882 | 0.02292 | 0.066611 | 0.024171 | 0.035408 | 0.02292 | 0.048205 | 0.021497 | 0.086955 | 0.011788 | 0.080111 | 0.015104 | 0.035408 | 0.011788 |  |  | RFF | Restaurant - Fast-Food
|  | 10 | [36 empty] | 0.090752 | 0.023201 | 0.093339 | 0.024541 | 0.087909 | 0.023201 | 0.092462 | 0.024541 | 0.06527 | 0.023201 | 0.067122 | 0.024541 | 0.035797 | 0.023201 | 0.049462 | 0.021687 | 0.087909 | 0.011932 | 0.080622 | 0.015474 | 0.035797 | 0.011932 |  |  | RtS | Retail - Small
|  | 13 | [36 empty] | 0.090896 | 0.023275 | 0.093526 | 0.024637 | 0.0725 | 0.023275 | 0.092791 | 0.024637 | 0.065373 | 0.023275 | 0.067256 | 0.024637 | 0.035901 | 0.023275 | 0.049791 | 0.021737 | 0.088161 | 0.01197 | 0.080756 | 0.015571 | 0.035901 | 0.01197 |  |  | Ofs | Office Small
|  | 14 | [36 empty] | 0.091194 | 0.023429 | 0.093911 | 0.024837 | 0.088686 | 0.023429 | 0.09347 | 0.024837 | 0.065586 | 0.023429 | 0.067533 | 0.024837 | 0.036115 | 0.023429 | 0.05047 | 0.02184 | 0.088686 | 0.012049 | 0.081033 | 0.01577 | 0.036115 | 0.012049
|  | 15 | [36 empty] | 0.092938 | 0.024333 | 0.096131 | 0.025987 | 0.091757 | 0.024333 | 0.097378 | 0.025987 | 0.066836 | 0.024333 | 0.069123 | 0.025987 | 0.03737 | 0.024333 | 0.054378 | 0.022431 | 0.091757 | 0.012514 | 0.082623 | 0.01692 | 0.03737 | 0.012514
|  | 16 | [36 empty] | 0.088951 | 0.022267 | 0.090894 | 0.023274 | 0.084737 | 0.022267 | 0.088158 | 0.023274 | 0.063979 | 0.022267 | 0.065371 | 0.023274 | 0.034501 | 0.022267 | 0.045158 | 0.021036 | 0.084737 | 0.011452 | 0.078871 | 0.014208 | 0.034501 | 0.011452
[39 empty] | LT-89513 |  |  |  | LT-97154 |  |  |  | LT-17642 | [7 empty] | LT-20643 |  |  |  | LT-30954
[39 empty] | 2T12 Canopy |  | 2T12 Canopy |  | 1T12 Canopy |  | 1T12 Canopy |  | 2T8 Canopy |  | 2T8 Canopy |  | 1T8 Canopy |  | 1T8 Canopy |  | 1T12 Shelf |  | 1T12 Shelf |  | 1T8 Shelf
[39 empty] | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT |  | LT |  | MT
|  | Multi | [36 empty] | Base 4' (2)T12 | Measure 4' LED | Base 4' (2)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (2)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T12 | Measure 4' LED | Base 4' (1)T8 | Measure 4' LED
|  | 6 | [36 empty] | 0.086216 | 0.020851 | 0.089211 | 0.022402 | 0.079923 | 0.020851 | 0.085196 | 0.022402 | 0.06202 | 0.020851 | 0.064166 | 0.022402 | 0.032534 | 0.020851 | 0.042196 | 0.020588 | 0.079923 | 0.010723 | 0.077666 | 0.013336 | 0.032534 | 0.010723 |  |  | 0.059072
|  | 8 | [36 empty] | 0.086744 | 0.021124 | 0.090062 | 0.022843 | 0.080852 | 0.021124 | 0.086694 | 0.022843 | 0.062399 | 0.021124 | 0.064775 | 0.022843 | 0.032914 | 0.021124 | 0.043694 | 0.020815 | 0.080852 | 0.010864 | 0.078275 | 0.013777 | 0.032914 | 0.010864 |  |  | Gro | Grocery
|  | 9 | [36 empty] | 0.08688 | 0.021194 | 0.090296 | 0.022964 | 0.081091 | 0.021194 | 0.087106 | 0.022964 | 0.062495 | 0.021194 | 0.064943 | 0.022964 | 0.033011 | 0.021194 | 0.044106 | 0.020877 | 0.081091 | 0.0109 | 0.078443 | 0.013898 | 0.033011 | 0.0109 |  |  | RSD | Restaurant - Sit-Down
|  | 10 | [36 empty] | 0.087155 | 0.021337 | 0.09079 | 0.02322 | 0.081575 | 0.021337 | 0.087974 | 0.02322 | 0.062693 | 0.021337 | 0.065296 | 0.02322 | 0.033209 | 0.021337 | 0.044974 | 0.021008 | 0.081575 | 0.010973 | 0.078796 | 0.014153 | 0.033209 | 0.010973 |  |  | Rt3 | Retail - Multistory Large
|  | 13 | [36 empty] | 0.087225 | 0.021373 | 0.090918 | 0.023287 | 0.0725 | 0.021373 | 0.088201 | 0.023287 | 0.062743 | 0.021373 | 0.065389 | 0.023287 | 0.033259 | 0.021373 | 0.045201 | 0.021043 | 0.081698 | 0.010992 | 0.078889 | 0.01422 | 0.033259 | 0.010992 |  |  | RtL | Retail - Single-Story Large
|  | 14 | [36 empty] | 0.087366 | 0.021446 | 0.091182 | 0.023423 | 0.081947 | 0.021446 | 0.088665 | 0.023423 | 0.062844 | 0.021446 | 0.065577 | 0.023423 | 0.033361 | 0.021446 | 0.045665 | 0.021113 | 0.081947 | 0.01103 | 0.079077 | 0.014356 | 0.033361 | 0.01103 |  |  | WRf | Warehouse - Refrigerated
|  | 15 | [36 empty] | 0.088122 | 0.021838 | 0.092609 | 0.024162 | 0.083277 | 0.021838 | 0.091176 | 0.024162 | 0.063385 | 0.021838 | 0.066599 | 0.024162 | 0.033905 | 0.021838 | 0.048176 | 0.021493 | 0.083277 | 0.011231 | 0.080099 | 0.015096 | 0.033905 | 0.011231
|  | 16 | [36 empty] | 0.086152 | 0.020817 | 0.089114 | 0.022352 | 0.079809 | 0.020817 | 0.085024 | 0.022352 | 0.061974 | 0.020817 | 0.064096 | 0.022352 | 0.032487 | 0.020817 | 0.042024 | 0.020562 | 0.079809 | 0.010706 | 0.077596 | 0.013285 | 0.032487 | 0.010706