## Sheet1
[7 empty] | HPS average lumens |  | 0.875 |  | Average maintained measure efficacy |  |  |  | 80
[7 empty] | PSMH average lumens |  | 0.85
|  |  |  | Base Case System (W) | [14 empty] | Source (HID base)
| Solution Codes | Measure Description | W Ranges |  | Base Case nominal (lamp)wattage | Base Case System Efficacy (lumens/W) | base case initial HID lamp lumens (Philips 2013 Lamp Spec Guide) | base case avg HID (HPS avg is 87.5% & PSMH avg is 85%) lamp lumens | est. base case fixture efficiency | est. base case fixture to target efficiency | est. net base lumens on target | Proposed Measure Case (W) | LED W is ? % of HID base system W | est. measure case mean light engine lumens based on an avg mntd efficacy of 80 lumens/W | est. measure case fixture efficiency | est. measure case fixture to target efficiency | est. net measure lumens on target | delta light check-want LED within zero to negative 15% of HID's light |  | Off-peak Demand saved (W)
1 | LT-45412 | LED IAMS Area Lighting | 50-90 | 188 | 150 | 85.1064 | 16000 | 14000 | 0.8 | 0.65 | 7280 | 90 | 0.47872 | 7200 | 0.95 | 0.92 | 6292.8 | 0.8644 | HPS | 98
2 | LT-33429 | LED IAMS Area Lighting | 91-120 | 250 | 200 | 85.6 | 21400 | 18725 | 0.8 | 0.65 | 9737 | 120 | 0.48 | 9600 | 0.95 | 0.92 | 8390.4 | 0.8617 | HPS | 130
3 | LT-89769 | LED IAMS Area Lighting | 121-150 | 295 | 250 | 91.5254 | 27000 | 23625 | 0.8 | 0.65 | 12285 | 150 | 0.50847 | 12000 | 0.95 | 0.92 | 10488 | 0.85372 | HPS | 145 | 104
4 | LT-62170 | LED IAMS Area Lighting | 151-203 | 365 | 310 | 100.4566 | 36666.6667 | 32083.3333 | 0.8 | 0.65 | 16683.3333 | 203 | 0.55616 | 16240 | 0.95 | 0.92 | 14193.76 | 0.85077 | HPS | 162
5 | LT-82363 | LED IAMS Area Lighting | 204-275 | 465 | 400 | 107.5269 | 50000 | 43750 | 0.8 | 0.65 | 22750 | 275 | 0.5914 | 22000 | 0.95 | 0.92 | 19228 | 0.84519 | HPS | 190
6 | LT-59558 | LED IAMS Area Lighting | 276-496 | 665 | 600 | 135.3383 | 90000 | 78750 | 0.8 | 0.65 | 40950 | 496 | 0.74586 | 39680 | 0.95 | 0.92 | 34680.32 | 0.84689 | HPS | 169
7 | LT-65209 | LED IAMS Area Lighting | 497-607 | 840 | 750 | 130.9524 | 110000 | 96250 | 0.8 | 0.65 | 50050 | 607 | 0.72262 | 48560 | 0.95 | 0.92 | 42441.44 | 0.84798 | HPS | 233
8 | LT-28370 | LED IAMS Area Lighting | 608-730 | 1100 | 1000 | 120.4545 | 132500 | 115937.5 | 0.8 | 0.65 | 60287.5 | 730 | 0.66364 | 58400 | 0.95 | 0.92 | 51041.6 | 0.84664 | HPS | 370
1 | LT-71476 | LED IAMS Area Lighting | 45-67 | 190 | 150 | 65.7895 | 12500 | 10625 | 0.8 | 0.65 | 5525 | 67 | 0.35263 | 5360 | 0.95 | 0.92 | 4684.64 | 0.8479 | PSMH | 123
2 | LT-27397 | LED IAMS Area Lighting | 68-90 | 208 | 175 | 80.5288 | 16750 | 14237.5 | 0.8 | 0.65 | 7403.5 | 90 | 0.43269 | 7200 | 0.95 | 0.92 | 6292.8 | 0.84998 | PSMH | 118
3 | LT-73969 | LED IAMS Area Lighting | 91-113 | 232 | 200 | 90.5172 | 21000 | 17850 | 0.8 | 0.65 | 9282 | 113 | 0.48707 | 9040 | 0.95 | 0.92 | 7900.96 | 0.85121 | PSMH | 119
4 | LT-25659 | LED IAMS Area Lighting | 114-123 | 288 | 250 | 79.4271 | 22875 | 19443.75 | 0.8 | 0.65 | 10110.75 | 123 | 0.42708 | 9840 | 0.95 | 0.92 | 8600.16 | 0.8506 | PSMH | 165
5 | LT-89014 | LED IAMS Area Lighting | 124-161 | 365 | 320 | 82.1918 | 30000 | 25500 | 0.8 | 0.65 | 13260 | 161 | 0.4411 | 12880 | 0.95 | 0.92 | 11257.12 | 0.84895 | PSMH | 204
6 | LT-62026 | LED IAMS Area Lighting | 162-194 | 400 | 350 | 90 | 36000 | 30600 | 0.8 | 0.65 | 15912 | 194 | 0.485 | 15520 | 0.95 | 0.92 | 13564.48 | 0.85247 | PSMH | 206
7 | LT-24181 | LED IAMS Area Lighting | 195-226 | 458 | 400 | 91.7031 | 42000 | 35700 | 0.8 | 0.65 | 18564 | 226 | 0.49345 | 18080 | 0.95 | 0.92 | 15801.92 | 0.85121 | PSMH | 232
8 | LT-55256 | LED IAMS Area Lighting | 227-254 | 506 | 450 | 93.3794 | 47250 | 40162.5 | 0.8 | 0.65 | 20884.5 | 254 | 0.50198 | 20320 | 0.95 | 0.92 | 17759.68 | 0.85038 | PSMH | 252
9 | LT-30938 | LED IAMS Area Lighting | 255-325 | 640 | 575 | 94.3359 | 60375 | 51318.75 | 0.8 | 0.65 | 26685.75 | 325 | 0.50781 | 26000 | 0.95 | 0.92 | 22724 | 0.85154 | PSMH | 315
10 | LT-56180 | LED IAMS Area Lighting | 326-440 | 818 | 750 | 100.2445 | 82000 | 69700 | 0.8 | 0.65 | 36244 | 440 | 0.5379 | 35200 | 0.95 | 0.92 | 30764.8 | 0.84882 | PSMH | 378
11 | LT-19782 | LED IAMS Area Lighting | 441-517 | 950 | 875 | 101.3158 | 96250 | 81812.5 | 0.8 | 0.65 | 42542.5 | 517 | 0.54421 | 41360 | 0.95 | 0.92 | 36148.64 | 0.84971 | PSMH | 433
12 | LT-19121 | LED IAMS Area Lighting | 518-643 | 1080 | 1000 | 111.1111 | 120000 | 102000 | 0.8 | 0.65 | 53040 | 643 | 0.59537 | 51440 | 0.95 | 0.92 | 44958.56 | 0.84763 | PSMH | 437