## 3Eplus Software Calcs
Section 2.2 Water Heating Piping Insulation Measure Calculation Method
The 3Eplus software program is available on the DOE Energy Efficiency and Renewable Energy website. The program performs the energy losses calculation for hot water pipes using the built-in thermal performance relationships of generic insulation materials or supply conductivity data for other materials.
The results of this program are used to estimate the energy savings per foot of pipe insulation for a typical residential situation with the following assumptions:
Single Family Home
BaseCase: Existing bare ¾” copper piping in unconditioned space. Measure: Gas water heater efficiency = 0.57 based on 2008 Residential ACM (Alternative Calculation Method) Approval Manual, Table R3-50. California Energy Commission. 5 feet of pipe are assumed to be insulated for each house.
According to Standard Table 150-B: Where insulation is required, one inch of R-4 insulation is typically required. This requirement applies to domestic hot water pipe (above 105° F) when the pipe diameter is 2 inches or smaller, the water temperature is between 105°F and 200°F, and the insulation conductivity between 0.24 and 0.28
Btu-in/hr-ft²-°F (typical of cellular foam pipe insulation material).The insulation specifications for the 3EPlus program are shown in table 10:
Table — Insulation Specifications
Temperature (degree F) | Thermal Conductivity ( Btu-in/ft2-h-°F)
39°F | 0.22
80°F | 0.23
112°F | 0.25
Average annual difference between water temperature and ambient air is 55 deg. F. (120-65)
The single family hot water draw profile is based on ASHRAE 90.2 Daily domestic hot water load profile generated an Equivalent Full Load Hours (EFLH) for water draw of approximately 1260 per year. Further investigation showed that piping will not store a significant amount of heat when water draws are not occurring.
The Energy Savings Rate is the difference between the heat loss for the bare pipe and the insulated pipe adjusted for the efficiency of the water heater (make-up energy).
Pipe Wrap measure using DOE software 3Eplus |  |  | Note
Bare pipe heat loss | 27.79 | Btu/hr/LF | per linear feet
Insulated pipe heat loss | 6.8 | Btu/hr/LF | using R-4.7 insulation
Heat loss reduction | 20.99 | Btu/hr/LF
Equivalent Full Load Hours | 1260 | hrs/yr | 6 draws/day/1 hr apart
Water Heater Energy Factor (EF) | 0.525
Gas savings | 0.5 | Therms/yr/LF
Savings for 5 feet pipe | 2.3 | Therms/yr

## Results
Pipe Wrap measure using DOE software 3Eplus
from 3Eplus page
|  | Bare pipe heat loss | 27.79 | Btu/hr/LF | per linear feet
|  | Insulated pipe heat loss | 6.8 | Btu/hr/LF | using R-4.7 insulation
|  | Heat loss reduction | 20.99 | Btu/hr/LF
|  | Equivalent Full Load Hours | 1260 | hrs/yr | 6 draws/day/1 hr apart
|  | Water Heater Energy Factor (EF) | 0.57
|  | Gas savings | 0.46399 | Therms/yr/LF
|  | Savings for 5 feet pipe | 2.3199 | Therms/yr

## CEC-500-2005-161.pdf
Hot Water Distribution System
Analysis of domestic hot water measures should consider including the findings and
the example calculation procedures included in the PIER Study, Hot Water
Distribution System, Research – Phase I, November 2005, CEC-500-2005-161
(addresses the intermittent nature of DHW draws and the cool down period between
draws).
ASHRAE 90.2 Daily Domestic Hot Water Load Profile is based on an average of 64.3 gallons/day/home
It assumes: 6 draws of 10.72 gallons of water, an hour apart.
Flow rate is equal to 3 gpm for 3.6 minutes per draw.
Note: data was established 25 years ago for a US family of four.
d
c
60 Minutes Draw Spacing for Bare 3/4" Rigged CU pipe
Calculations here are similar to example 3 Section-10, in the PIER report
Calculating the temperature to which a pipe has cooled as a function of time,
it is easiest to use the above-measured UAzero- flow values in an exponential
decay function of the form:
(Tpipe time 2 – Tair)/(Tpipe time 1 – Tair)= e-(UA/mCp)t.
Where:
mCp = total mass times specific heat of the pipe+water+insulation
t = time in proper units to make the expression (UA/mCp)(t) dimensionless
The temperature of water in the pipe, and the energy loss due to cool-down, can be calculated at
any time after flow has stopped by using the measured UAzero-flow value, the piping system mass
and specific heat per foot, and assuming an initial pipe temperature and surrounding air temperature.
Using the exponential temperature decay equation discussed in Appendix B, we see that:
The mCp for bare ¾ inch rigid copper pipe is approximately 0.2084 + 0.0417 = 0.2501 Btu/ft F. And from
figure 8-1 or table 8-1 we see that zero-flow UA for that pipe is 0.388 Btu/hr ft F. Thus:
(t)(UA)/(mCp) = (60 minutes)(0.388 Btu/hr ft F)/[(0.2501 Btu/ft F)(60 minutes/hr)]
(t)(UA)/(mCp) = 1.55
From table 8-2, we see the time for the pipe temperature to drop below 105 F is approximately
13 minutes. Using the steady-state temperature drop computation above, we can calculate the
average pipe water temperature at the beginning of cool-down as:
Thot water = 120 degF
Tcold water= 58 degF
Tair = 65 degF
Bare ¾ inch copper pipe in air
Tpipe avg.initial = (120 + 110.5)/2
Tpipe avg.initial = 115.25 F
And hence that:
Tpipe 60 minutes = 65 F + (115.25-65)e-1.55
Tpipe 60 minutes = 75.7F
We see that after the first draw the pipe cools down below 105 F before the second draw occurs.
This means that the water in the pipe is not at a usable temperature,