## VFD Costs 2018 RS Means REA
Cost Data from RS Means 2018 Electrical Cost Data
RS Means includes cost estimates from 3 HP to 200 HP.
Estimates for larger capacities are based on trendlines established from the available data
HP | enclosed $ | labor $ (enclosed) | enclosed $/HP | labor $/HP (enclosed) | trendline enclosed $/HP | trendline labor $/HP (enclosed)
3 | 1950 | 580 | 580 | 193.3333 | 475.6697 | 164.5389 |  | 5 HP to 10 HP |  |  | PR-50059
5 | 2225 | 580 | 445 | 116 | 407.3146 | 123.4717 |  | 5 | 407.3146 | 123.4717 | Material | 365.8109 | trendline average $/HP 5 HP to 10 HP enclosed VFD
7.5 | 2700 | 695 | 360 | 92.6667 | 360.1232 | 98.3075 |  | 7.5 | 360.1232 | 98.3075 | Labor | 101.8028 | trendline average labor $/HP (enclosed) 5 HP to 10 HP
10 | 2975 | 695 | 297.5 | 69.5 | 329.9949 | 83.6293 |  | 10 | 329.9949 | 83.6293 |  | 264.0081 | average non-labor $/HP 5 HP to 10 HP
15 | 3825 | 1050 | 255 | 70 | 291.7617 | 66.5852 |  |  |  |  | Total | 467.6137
20 | 4525 | 1050 | 226.25 | 52.5 | 267.3526 | 56.6434 |  | 15 to 20 HP |  |  | PR-34445
25 | 5550 | 1400 | 222 | 56 | 249.8347 | 49.9662 |  | 15 | 291.7617 | 66.5852 | Material | 279.5571 | trendline average $/HP 15 HP to 20 HP enclosed VFD
30 | 6950 | 1400 | 231.6667 | 46.6667 | 236.3771 | 45.0992 |  | 20 | 267.3526 | 56.6434 | Labor | 61.6143 | trendline average labor $/HP (enclosed) 15 HP to 20 HP
40 | 8025 | 1400 | 200.625 | 35 | 216.6016 | 38.3655 | [5 empty] | 217.9428 | average non-labor $/HP 15 HP to 20 HP
50 | 10300 | 1750 | 206 | 35 | 202.4091 | 33.8429 |  |  |  |  | Total | 341.1714
60 | 12400 | 2075 | 206.6667 | 34.5833 | 191.5061 | 30.5464
75 | 14400 | 2075 | 192 | 27.6667 | 178.958 | 26.9455 |  | 50 HP to 500 HP
100 | 18500 | 2325 | 185 | 23.25 | 163.9862 | 22.9223 |  | HP | trendline enclosed $/HP | trendline labor $/HP (enclosed)
125 | 20100 | 2325 | 160.8 | 18.6 | 153.2412 | 20.2202 |  | 50 | 202.4091 | 33.8429 |  | 142.6905 | trendline average $/HP 50 HP to 500 HP enclosed VFD
150 |  |  |  |  | 144.9867 | 18.2506 | t | 75 | 178.958 | 26.9455 |  | 18.7579 | trendline average labor $/HP (enclosed) 50 HP to 500 HP
200 |  |  |  |  | 132.857 | 15.5256 |  | 100 | 163.9862 | 22.9223 |  | 123.9326 | average non-labor $/HP 50 HP to 500 HP
250 |  |  |  |  | 124.1517 | 13.6955 |  | 125 | 153.2412 | 20.2202
300 |  |  |  |  | 117.4642 | 12.3614 |  | 150 | 144.9867 | 18.2506
350 |  |  |  |  | 112.0918 | 11.3354 |  | 175 | 138.3555 | 16.7358
400 |  |  |  |  | 107.637 | 10.5158 |  | 200 | 132.857 | 15.5256
450 |  |  |  |  | 103.8548 | 9.8421 |  | 225 | 128.1886 | 14.531
500 |  |  |  |  | 100.5843 | 9.2761 |  | 250 | 124.1517 | 13.6955
550 |  |  |  |  | 97.7145 | 8.7923 |  | 275 | 120.6096 | 12.981
600 |  |  |  |  | 95.1662 | 8.3726 |  | 300 | 117.4642 | 12.3614
650 |  |  |  |  | 92.8807 | 8.0042 |  | 325 | 114.6432 | 11.8176
700 |  |  |  |  | 90.8136 | 7.6777 |  | 350 | 112.0918 | 11.3354
750 |  |  |  |  | 88.9306 | 7.3856 |  | 375 | 109.7675 | 10.9042
800 |  |  |  |  | 87.2045 | 7.1225 |  | 400 | 107.637 | 10.5158
850 |  |  |  |  | 85.6136 | 6.8839 |  | 425 | 105.6733 | 10.1634
[8 empty] | 450 | 103.8548 | 9.8421
[8 empty] | 25 | 249.8347 | 49.9662
[8 empty] | 50 | 202.4091 | 33.8429
15 HP to 50 HP
[8 empty] | 15 | 291.7617 | 66.5852 |  | 237.3617 | trendline average $/HP 15 HP to 50 HP enclosed VFD
[8 empty] | 20 | 267.3526 | 56.6434 |  | 45.9707 | trendline average labor $/HP (enclosed) 15 HP to 50 HP
[8 empty] | 25 | 249.8347 | 49.9662 |  | 191.3909 | average non-labor $/HP 15 HP to 50 HP
[8 empty] | 30 | 236.3771 | 45.0992
[8 empty] | 35 | 225.566 | 41.3559
[8 empty] | 40 | 216.6016 | 38.3655
[8 empty] | 45 | 208.9905 | 35.9077
[8 empty] | 50 | 202.4091 | 33.8429

## Air Compressor Costs New-ROB
Rated Motor Power (HP) | Measure/unit ($) | Baseline/unit ($) | Incremental cost/unit ($) | Labor ($) | labor/Unit ($) | Base Case Total ($) | Measure Total ($) | Incremental Total ($)
5 | 1150.83 | 694.17 | 456.66 | 905 | 181
7.5 | 951.8567 | 605.5033 | 346.3533 | 1125 | 150
10 | 852.37 | 561.17 | 291.2 | 1300 | 130
15 | 752.8833 | 516.8367 | 236.0467 | 1775 | 118.3333
20 | 703.14 | 494.67 | 208.47 | 2025 | 101.25
PR-18655 | 985.02 | 620.28 | 364.74 |  | 153.67 | 773.95 | 1138.69 | 364.74
PR-18656 | 728.01 | 505.75 | 222.26 |  | 109.79 | 615.54 | 837.8 | 222.26
HP | Measure | Baseline
7.5 | 7863 | 5200
10 | 8600 | 5000
10 | 8241 | 6000
15 | 9154 | 6450
15 | 12035 | 7855
20 | 15000 | 11360 | [6 empty] | Regression Based Incremental Costs
20 | 14148 | 8747 |  | Installation Type | Incremental Measure Cost | Full Measure Cost |  |  | HP | Incremental Cost ($) | Labor ($) | Cost/Unit ($) | labor/Unit ($)
20 | 13920 | 10338 |  |  |  | 1st Baseline | 2nd Baseline |  | 5 | 2283.35 | 905 | 456.67 | 181
|  |  |  | ROB | (MEC + MLC) – (BEC + BLC) | (MEC + MLC) – (BEC + BLC) | N/A |  | 7.5 | 2597.675 | 1125 | 346.3567 | 150
|  |  |  | NEW/NC |  |  |  |  | 10 | 2912 | 1300 | 291.2 | 130
[9 empty] | 15 | 3540.65 | 1775 | 236.0433 | 118.3333
[9 empty] | 20 | 4169.3 | 2025 | 208.465 | 101.25 | Total
[10 empty] | PR-18655 | 5-10 HP | 364.7422 | 153.6667 | 518.4089
[10 empty] | PR-18656 | 15-20 HP | 222.2542 | 109.7917 | 332.0458
|  | Data | [8 empty] | 5-10 HP Costs
|  | http://oemaircompressor.com/ingersollrandnirvanavariablefrequencyrotarycompressors.aspx | [8 empty] | Measure | Baseline | Incremental
|  | IR | VFD | L/UL | [5 empty] | 7.5 | 7863 | 5200 | 2663
|  | 7.5 | 7863 | 5200 | 2663 |  |  |  |  | 10 | 8600 | 5000 | 3600
|  | 10 | 8241 | 6000 | 2241 |  |  |  |  | 10 | 8241 | 6000 | 2241
|  | 15 | 9154 | 6450 | 2704
|  | 20 | NA | NA | [5 empty] | 15 | 9154 | 6450 | 2704
[10 empty] | 15 | 12035 | 7855 | 4180
[10 empty] | 20 | 15000 | 11360 | 3640
|  | http://oemaircompressor.com/ga71115vsdoilinjectedscrewcompressors.aspx | [7 empty] | 20 | 14148 | 8747 | 5401
|  | Atlas Copco | VFD | L/UL | [5 empty] | 20 | 13920 | 10338 | 3582
|  | 7.5 | NA | 4950 |  | L/ul has 53 gallon tank |  |  |  |  | 713.2 | 495.1833 | 218.0167
|  | 10 | 8600 | 5000 | 3600 | L/ul has 53 gallon tank
|  | 15 | 9700 | 9000 | 700
|  | 20 | 15000 | 11360 | 3640
http://oemaircompressor.com/sullivanpalatekrotaryscrewvariablefrequencydrivevfd15-300hpaircompressors.aspx
|  | Sullivan | VFD | L/UL
|  | 7.5 | NA
|  | 10 | NA
|  | 15 | 12035 | 7855 | 4180
|  | 20 | 14148 | 8747 | 5401
http://oemaircompressor.com/bogecandcfvsdseriesrotaryscrewcompressors.aspx
|  | Boge | VFD CF | L/UL
|  | 7.5 | NA | 6367
|  | 10 | NA | 7841
|  | 15 | NA | 10117
|  | 20 | 13920 | 10338 | 3582
Note on F4: Standard Configuration: 2018 RS Means
Note on O21: Standard Configuration: 2018 RS Means

## Grainger 2018
Max. HP | Max. Output Amps | Output Voltage | Enclosure | With Bypass / No... | Item # | Price | $/HP | Distributor $
3 | 4.8 | 480VAC | NEMA 1 | No Bypass | 32WP74 | 1443 | 481 | Size | Avg Cost | Avg Cost/HP | Row Labels | Average of Price | Average of $/HP
3 | 5.6 | 480VAC | NEMA 1 | No Bypass | 32WP38 | 820 | 273.3333 | 5 HP to 10 HP | 1474.781 | 206.9486 | 3 | 1140.6 | 380.2
3 | 5.6 | 480VAC | NEMA 1 | No Bypass | 4LRP2 | 1381 | 460.3333 | 15 HP to 20 HP | 2099.3 | 161.1041 | 4 | 881 | 220.25
3 | 5.6 | 480VAC | NEMA 1 | No Bypass | 32WN88 | 1050 | 350 |  |  |  | 5 | 1300.4 | 260.08
3 | 5.6 | 480VAC | NEMA 1 | No Bypass | 40HZ18 | 1009 | 336.3333 |  |  |  | 7.5 | 1451.1429 | 193.4857
4 | 8 | 480VAC | NEMA 1 | No Bypass | 32WP39 | 881 | 220.25 |  |  |  | 10 | 1672.8 | 167.28
5 | 7.6 | 480VAC | NEMA 1 | No Bypass | 32WP75 | 1618 | 323.6 |  |  |  | 15 | 1838.2 | 122.5467
5 | 7.6 | 480VAC | NEMA 1 | No Bypass | 4LRP3 | 1473 | 294.6 |  |  |  | 20 | 2360.4 | 118.02
5 | 7.6 | 480VAC | NEMA 1 | No Bypass | 40HY75 | 1228 | 245.6 |  |  |  | 25 | 2814.4 | 112.576
5 | 7.6 | 480VAC | NEMA 1 | No Bypass | 32WN89 | 1279 | 255.8 |  |  |  | 30 | 3350.6 | 111.6867
5 | 9.6 | 480VAC | NEMA 1 | No Bypass | 32WP40 | 904 | 180.8 |  |  |  | 40 | 4274 | 106.85
7.5 | 12 | 480VAC | NEMA 1 | No Bypass | 4LRP4 | 1753 | 233.7333 |  |  |  | 50 | 5165 | 103.3
7.5 | 9 | 480VAC | NEMA 1 | No Bypass | 32WN90 | 1388 | 185.0667 |  |  |  | 60 | 6040.6 | 100.6767
7.5 | 11 | 480VAC | NEMA 1 | No Bypass | 32WP76 | 1799 | 239.8667 |  |  |  | 75 | 7445 | 99.2667
7.5 | 12 | 480VAC | NEMA 1 | No Bypass | 32WP41 | 1026 | 136.8
7.5 | 12 | 480VAC | NEMA 1 | No Bypass | 32WN91 | 1495 | 199.3333
7.5 | 12 | 480VAC | NEMA 1 | No Bypass | 40HZ22 | 1333 | 177.7333
7.5 | 12 | 480VAC | NEMA 1 | No Bypass | 40HY76 | 1364 | 181.8667
10 | 14 | 480VAC | NEMA 1 | No Bypass | 32WP77 | 1952 | 195.2
10 | 16 | 480VAC | NEMA 1 | No Bypass | 4LRP5 | 2086 | 208.6
10 | 16 | 480VAC | NEMA 1 | No Bypass | 32WN92 | 1601 | 160.1
10 | 16 | 480VAC | NEMA 1 | No Bypass | 40HZ21 | 1460 | 146
10 | 16 | 480VAC | NEMA 1 | No Bypass | 32WP42 | 1265 | 126.5
15 | 21 | 480VAC | NEMA 1 | No Bypass | 32WP78 | 2123 | 141.5333
15 | 23 | 480VAC | NEMA 1 | No Bypass | 4LRP6 | 1871 | 124.7333
15 | 23 | 480VAC | NEMA 1 | No Bypass | 40HY95 | 1697 | 113.1333
15 | 23 | 480VAC | NEMA 1 | No Bypass | 32WN93 | 1862 | 124.1333
15 | 23 | 480VAC | NEMA 1 | No Bypass | 32WP43 | 1638 | 109.2
20 | 27 | 480VAC | NEMA 1 | No Bypass | 32WP79 | 2565 | 128.25
20 | 31 | 480VAC | NEMA 1 | No Bypass | 40HZ33 | 2314 | 115.7
20 | 31 | 480VAC | NEMA 1 | No Bypass | 4LRP7 | 2304 | 115.2
20 | 31 | 480VAC | NEMA 1 | No Bypass | 32WP44 | 2083 | 104.15
20 | 31 | 480VAC | NEMA 1 | No Bypass | 32WN94 | 2536 | 126.8
25 | 34 | 480VAC | NEMA 1 | No Bypass | 32WP80 | 3299 | 131.96
25 | 38 | 480VAC | NEMA 1 | No Bypass | 40HZ02 | 2575 | 103
25 | 38 | 480VAC | NEMA 1 | No Bypass | 4LRP8 | 2706 | 108.24
25 | 38 | 480VAC | NEMA 1 | No Bypass | 32WP45 | 2669 | 106.76
25 | 38 | 480VAC | NEMA 1 | No Bypass | 32WN95 | 2823 | 112.92
30 | 40 | 480VAC | NEMA 1 | No Bypass | 32WP81 | 4028 | 134.2667
30 | 46 | 480VAC | NEMA 1 | No Bypass | 4LRP9 | 3015 | 100.5
30 | 46 | 480VAC | NEMA 1 | No Bypass | 32WP46 | 3109 | 103.6333
30 | 46 | 480VAC | NEMA 1 | No Bypass | 40HZ01 | 3149 | 104.9667
30 | 46 | 480VAC | NEMA 1 | No Bypass | 32WN96 | 3452 | 115.0667
40 | 52 | 480VAC | NEMA 1 | No Bypass | 32WP82 | 4916 | 122.9
40 | 61 | 480VAC | NEMA 1 | No Bypass | 4LRR1 | 3688 | 92.2
40 | 61 | 480VAC | NEMA 1 | No Bypass | 32WP47 | 3810 | 95.25
40 | 61 | 480VAC | NEMA 1 | No Bypass | 40HZ04 | 4089 | 102.225
40 | 61 | 480VAC | NEMA 1 | No Bypass | 32WN97 | 4867 | 121.675
50 | 65 | 480VAC | NEMA 1 | No Bypass | 32WP83 | 5979 | 119.58
50 | 72 | 480VAC | NEMA 1 | No Bypass | 4LRR2 | 5420 | 108.4
50 | 72 | 480VAC | NEMA 1 | No Bypass | 32WP48 | 4971 | 99.42
50 | 72 | 480VAC | NEMA 1 | No Bypass | 40HY92 | 4447 | 88.94
50 | 72 | 480VAC | NEMA 1 | No Bypass | 32WN98 | 5008 | 100.16
60 | 77 | 480VAC | NEMA 1 | No Bypass | 32WP84 | 7714 | 128.5667
60 | 87 | 480VAC | NEMA 1 | No Bypass | 4LRR3 | 5351 | 89.1833
60 | 87 | 480VAC | NEMA 1 | No Bypass | 32WP49 | 5603 | 93.3833
60 | 87 | 480VAC | NEMA 1 | No Bypass | 40HZ23 | 5347 | 89.1167
60 | 87 | 480VAC | NEMA 1 | No Bypass | 32WN99 | 6188 | 103.1333
75 | 96 | 480VAC | NEMA 1 | No Bypass | 32WP85 | 8281 | 110.4133
75 | 105 | 480VAC | 480VAC | 480VAC | 4LRR4 | 6609 | 88.12
75 | 105 | 480VAC | 480VAC | 480VAC | 40HZ09 | 6556 | 87.4133
75 | 105 | 480VAC | 480VAC | 480VAC | 32WP50 | 6417 | 85.56
75 | 105 | 480VAC | 480VAC | 480VAC | 32WP01 | 7588 | 101.1733
100 | 140 | 480VAC | 480VAC | 480VAC | 32WP51 | 7670 | 76.7
100 | 140 | 480VAC | 480VAC | 480VAC | 40HZ07 | 8207 | 82.07
100 | 140 | 480VAC | 480VAC | 480VAC | 4LRR5 | 8097 | 80.97
100 | 140 | 480VAC | 480VAC | 480VAC | 32WP02 | 9768 | 97.68
125 | 170 | 480VAC | 480VAC | 480VAC | 4LRR6 | 10463 | 83.704
125 | 170 | 480VAC | 480VAC | 480VAC | 40HY97 | 9082 | 72.656
150 | 205 | 480VAC | 480VAC | 480VAC | 4LRR7 | 11219 | 74.7933
200 | 261 | 480VAC | 480VAC | 480VAC | 4LRR8 | 12953 | 64.765
250 | 300 | 480VAC | 480VAC | 480VAC | 4LRR9 | 19468 | 77.872

## AM+ Results
AirMaster+ Results
5 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 13 | 4.3 | 35919
VFD | System Totals | 8400 | 13 | 3.4 | 28758 | Summary
Savings |  |  |  | 0.9 | 7161 | [17 empty] | Savings
[6 empty] | HP | 5 | 7.5 | 10 | 15 | 20 | 25 | 50 | 75 | 100 | 125 | 150 | 200 | 250 | 300 | 400 | 500 | Range | kW | kWh/yr
7.5 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh | Base kW | 4.3 | 6.3 | 8.2 | 12.1 | 15.7 | 19.6 | 38 | 56.8 | 75.8 | 94.5 | 112.5 | 148.2 | 185.1 | 221.2 | 294.1 | 367.6 | 5 HP - 10 HP | 0.1593 | 465.1606
load/unload | System Totals | 8400 | 19 | 6.3 | 52635 | Measure kW | 3.4 | 5.1 | 6.8 | 10.1 | 13.1 | 16.3 | 32 | 48 | 64.1 | 79.5 | 94.7 | 124.9 | 156.9 | 187.2 | 248.8 | 310.8 | 15 HP - 20 HP | 0.13185 | 384.991
VFD | System Totals | 8400 | 19 | 5.1 | 42630 | Base kWh (per 8400 op hours) | 35919 | 52635 | 69207 | 101787 | 132299 | 164238 | 319059 | 477222 | 637138 | 793744 | 944843 | 1244969 | 1555256 | 1858487 | 2470379 | 3087936
Savings |  |  |  | 1.2 | 10005 | Measure kWh (per 8400 op hours) | 28758 | 42630 | 56725 | 85076 | 110280 | 137117 | 269115 | 403619 | 538170 | 668121 | 795186 | 1048882 | 1317664 | 1572747 | 2089661 | 2610853
Baseline
10 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh | Base kWh (per DEER op hours) | 12486.1286 | 18296.9286 | 24057.6714 | 35383.1 | 45989.6524 | 57092.2571 | 110910.9857 | 165891.4571 | 221481.3048 | 275920.5333 | 328445.4238 | 432774.9381 | 540636.6095 | 646045.481 | 858750.7952 | 1073425.3714 | Range | kW | kWh/yr
load/unload | System Totals | 8400 | 27 | 8.2 | 69207 | Measure kWh (per DEER op hours) | 9996.8286 | 14819 | 19718.6905 | 29574.0381 | 38335.4286 | 47664.481 | 93549.5 | 140305.6524 | 187078.1429 | 232251.5857 | 276421.8 | 364611.3619 | 458045.1048 | 546716.8143 | 726405.9667 | 907582.2333 | 5 HP - 10 HP | 0.83819 | 2447.5278
VFD | System Totals | 8400 | 27 | 6.8 | 56725 | Saved kWh | 2489.3 | 3477.9286 | 4338.981 | 5809.0619 | 7654.2238 | 9427.7762 | 17361.4857 | 25585.8048 | 34403.1619 | 43668.9476 | 52023.6238 | 68163.5762 | 82591.5048 | 99328.6667 | 132344.8286 | 165843.1381 | 15 HP - 20 HP | 0.79766 | 2329.178
Savings |  |  |  | 1.4 | 12482
[6 empty] | Base kWh/HP | 2497.2257 | 2439.5905 | 2405.7671 | 2358.8733 | 2299.4826 | 2283.6903 | 2218.2197 | 2211.8861 | 2214.813 | 2207.3643 | 2189.6362 | 2163.8747 | 2162.5464 | 2153.4849 | 2146.877 | 2146.8507
15 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh | Measure kWh/HP | 1999.3657 | 1975.8667 | 1971.869 | 1971.6025 | 1916.7714 | 1906.5792 | 1870.99 | 1870.742 | 1870.7814 | 1858.0127 | 1842.812 | 1823.0568 | 1832.1804 | 1822.3894 | 1816.0149 | 1815.1645 | Measure
load/unload | System Totals | 8400 | 43 | 12.1 | 101787 | Saved kWh/HP | 497.86 | 463.7238 | 433.8981 | 387.2708 | 382.7112 | 377.111 | 347.2297 | 341.1441 | 344.0316 | 349.3516 | 346.8242 | 340.8179 | 330.366 | 331.0956 | 330.8621 | 331.6863 | Range | kW | kWh/yr
VFD | System Totals | 8400 | 43 | 10.1 | 85076 | [17 empty] | 5 HP - 10 HP | 0.67889 | 1982.3671
Savings |  |  |  | 2 | 16711 | Base kW/HP | 0.85521 | 0.83548 | 0.82389 | 0.80783 | 0.78749 | 0.78209 | 0.75966 | 0.7575 | 0.7585 | 0.75595 | 0.74988 | 0.74105 | 0.7406 | 0.73749 | 0.73523 | 0.73522 | 15 HP - 20 HP | 0.66582 | 1944.187
[6 empty] | Measure kW/HP | 0.68471 | 0.67667 | 0.6753 | 0.67521 | 0.65643 | 0.65294 | 0.64075 | 0.64067 | 0.64068 | 0.63631 | 0.6311 | 0.62433 | 0.62746 | 0.62411 | 0.62192 | 0.62163
20 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh | Saved kW/HP | 0.1705 | 0.15881 | 0.1486 | 0.13263 | 0.13107 | 0.12915 | 0.11891 | 0.11683 | 0.11782 | 0.11964 | 0.11878 | 0.11672 | 0.11314 | 0.11339 | 0.11331 | 0.11359
load/unload | System Totals | 8400 | 57 | 15.7 | 132299
VFD | System Totals | 8400 | 57 | 13.1 | 110280
Savings |  |  |  | 2.6 | 22019 | Modeled Operating Hours | 8400
[6 empty] | DEER Operating Hours | 2920
25 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 71 | 19.6 | 164238
VFD | System Totals | 8400 | 71 | 16.3 | 137117
Savings |  |  |  | 3.3 | 27121
50 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 158 | 38 | 319059
VFD | System Totals | 8400 | 158 | 32 | 269115
Savings |  |  |  | 6 | 49944
75 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 255 | 56.8 | 477222
VFD | System Totals | 8400 | 255 | 48 | 403619
Savings |  |  |  | 8.8 | 73603
100 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 331 | 75.8 | 637138
VFD | System Totals | 8400 | 331 | 64.1 | 538170
Savings |  |  |  | 11.7 | 98968
125 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 386 | 94.5 | 793744
VFD | System Totals | 8400 | 386 | 79.5 | 668121
Savings |  |  |  | 15 | 125623
150 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 510 | 112.5 | 944843
VFD | System Totals | 8400 | 510 | 94.7 | 795186
Savings |  |  |  | 17.8 | 149657
200 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 674 | 148.2 | 1244969
VFD | System Totals | 8400 | 674 | 124.9 | 1048882
Savings |  |  |  | 23.3 | 196087
250 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 843 | 185.1 | 1555256
VFD | System Totals | 8400 | 843 | 156.9 | 1317664
Savings |  |  |  | 28.2 | 237592
300 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 992 | 221.2 | 1858487
VFD | System Totals | 8400 | 992 | 187.2 | 1572747
Savings |  |  |  | 34 | 285740
400 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 1328 | 294.1 | 2470379
VFD | System Totals | 8400 | 1328 | 248.8 | 2089661
Savings |  |  |  | 45.3 | 380718
500 HP |  | Total OpHrs | Avg Airflow, acfm | Peak Demand, kW | Annual Energy, kWh
load/unload | System Totals | 8400 | 1724 | 367.6 | 3087936
VFD | System Totals | 8400 | 1724 | 310.8 | 2610853
Savings |  |  |  | 56.8 | 477083
58
0.12393

## compressor calculations
1 | gal/cfm |  |  | 8400 | hr/year |  | Note: results can be scaled to operating hours.
7.48 | gal/cf |  |  | 350 | days/year
0.13369 | cf/cfm
Assumptions:
| 0.7 | % full load
| 2 | gal/cfm storage
| 0.05 | % VFD overhead
| 0.4 | % at unload point
| AirMaster+ Load/Unload Compressor Description | [6 empty] | VFD Compressor inputs
| HP | full load ACFM | Part load ACFM | Storage gal | Storage CF | full load power kW | max full load power kW | full load power kW | no load power kW | unload point ACFM | unload kW | savings kWh | savings kW | savings kWh % | savings kWh/HP | savings kW/HP
| 5 | 18 | 12.6 | 25.2 | 3.369 | 4.7 | 4.9 | 4.935 | 0.235 | 7.2 | 2.115 | 7160 | 0.9 | 16.5 | 1432 | 0.18
| 7.5 | 27 | 18.9 | 37.8 | 5.0535 | 6.8 | 7.2 | 7.14 | 0.34 | 10.8 | 3.06 | 10005 | 1.2 | 16.5 | 1334 | 0.16
| 10 | 39 | 27.3 | 54.6 | 7.2995 | 9 | 9.4 | 9.45 | 0.45 | 15.6 | 4.05 | 12482 | 1.5 | 16.5 | 1248.2 | 0.15
| 15 | 62 | 43.4 | 86.8 | 11.6043 | 13.5 | 14.2 | 14.175 | 0.675 | 24.8 | 6.075 | 16711 | 2 | 16.5 | 1114.0667 | 0.13333
| 20 | 82 | 57.4 | 114.8 | 15.3476 | 17.5 | 18.5 | 18.375 | 0.875 | 32.8 | 7.875 | 22019 | 2.6 | 16.5 | 1100.95 | 0.13
| 25 | 102 | 71.4 | 142.8 | 19.0909 | 21.8 | 22.9 | 22.89 | 1.09 | 40.8 | 9.81 | 27121 | 3.2 | 16.5 | 1084.84 | 0.128
| 50 | 226 | 158.2 | 316.4 | 42.2995 | 42.7 | 45 | 44.835 | 2.135 | 90.4 | 19.215 | 49944 | 5.9 | 15.7 | 998.88 | 0.118
| 75 | 365 | 255.5 | 511 | 68.3155 | 64.1 | 67.6 | 67.305 | 3.205 | 146 | 28.845 | 73604 | 8.8 | 15.4 | 981.3867 | 0.11733
| 100 | 473 | 331.1 | 662.2 | 88.5294 | 85.4 | 90.1 | 89.67 | 4.27 | 189.2 | 38.43 | 98968 | 11.8 | 15.5 | 989.68 | 0.118
| 125 | 551 | 385.7 | 771.4 | 103.1283 | 106 | 111.8 | 111.3 | 5.3 | 220.4 | 47.7 | 125623 | 15 | 15.8 | 1004.984 | 0.12
| 150 | 729 | 510.3 | 1020.6 | 136.4439 | 126.3 | 133.2 | 132.615 | 6.315 | 291.6 | 56.835 | 149657 | 17.8 | 15.8 | 997.7133 | 0.11867
| 200 | 963 | 674.1 | 1348.2 | 180.2406 | 166.5 | 175.5 | 174.825 | 8.325 | 385.2 | 74.925 | 196087 | 23.3 | 15.8 | 980.435 | 0.1165
| 250 | 1204 | 842.8 | 1685.6 | 225.3476 | 209.2 | 220.6 | 219.66 | 10.46 | 481.6 | 94.14 | 237592 | 28.3 | 15.3 | 950.368 | 0.1132
| 300 | 1417 | 991.9 | 1983.8 | 265.2139 | 249.7 | 263.3 | 262.185 | 12.485 | 566.8 | 112.365 | 285740 | 34 | 15.4 | 952.4667 | 0.11333
| 400 | 1897 | 1327.9 | 2655.8 | 355.0535 | 331.6 | 349.6 | 348.18 | 16.58 | 758.8 | 149.22 | 380718 | 45.3 | 15.4 | 951.795 | 0.11325
| 500 | 2463 | 1724.1 | 3448.2 | 460.9893 | 414.4 | 437 | 435.12 | 20.72 | 985.2 | 186.48 | 477082 | 56.8 | 15.4 | 954.164 | 0.1136
[15 empty] | 986.0648 | 0.11726 | average
[15 empty] | 966.4993 | 0.11503 | weighted average

## Building types
References Mentioning Building Types as Compressor Markets
Compressor Building Types |  | Description | Reference
| Agriculture |  | http://www.quincycompressor.com/agriculture.html
Manufacturing - Bio/Tech
Manufacturing - Light Industrial
Industrial
| Retail - Single-Story Large | Tire Centers
| Health/Medical - Hospital | Hospitals | http://www.airbestpractices.com/system-assessments/compressor-controls/hospital-air-system-savings
| Health/Medical - Clinic | Medical Centers | http://www.quincycompressor.com/medical.html
| Transportation-Communication-Utilities | coal power plants | http://www.airbestpractices.com/industries/power/boiler-soot-blowing-power-plants
|  | nuclear power plants | http://www.airbestpractices.com/industries/power/instrument-air-nuclear-power-plants
|  | wastewater treatment | http://www.airbestpractices.com/industries/wastewater/compressed-air-wastewater-treatment
| Misc Commercial | "catch-all" for for customers not fitting other building types