## Savings Summary
eQuest Outputs and Savings Summary
Display Case Cooler Evaporator Fan ECM Motor replacing Shaded Pole Motor (DMT_SPM to ECM) | [7 empty] | RF-60192
Total Linear feet of Display Cases considered: | [6 empty] | 366 | ft
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/ft-yr) | Peak Demand Reduction (kW/ft) | Natural Gas Savings (therm/ft-yr)
1 | v14 | 1369231 | 3166751 | 31667.51 | 200.1876 | 1324276 | 3178189 | 31781.89 | 194.5124 | 122.8279 | 0.015506 | -0.31251
2 | v14 | 1466037 | 2254232 | 22542.32 | 285.2879 | 1420485 | 2263254 | 22632.54 | 278.892 | 124.459 | 0.017475 | -0.2465
3 | v14 | 1420757 | 2189161 | 21891.61 | 234.3414 | 1375348 | 2199163 | 21991.63 | 228.4933 | 124.0683 | 0.015978 | -0.27328
4 | v14 | 1474510 | 1894906 | 18949.06 | 270.2952 | 1428859 | 1903534 | 19035.34 | 264.5521 | 124.7295 | 0.015692 | -0.23574
5 | v14 | 1408519 | 2260581 | 22605.81 | 210.621 | 1363081 | 2270710 | 22707.1 | 204.7316 | 124.1475 | 0.016091 | -0.27675
6 | v14 | 1518117 | 1412941 | 14129.41 | 256.6767 | 1472321 | 1420090 | 14200.9 | 250.7653 | 125.1257 | 0.016151 | -0.19533
7 | v14 | 1499763 | 1300418 | 13004.18 | 244.3682 | 1453884 | 1308376 | 13083.76 | 238.505 | 125.3525 | 0.01602 | -0.21743
8 | v14 | 1528235 | 1310172 | 13101.72 | 261.6189 | 1482217 | 1316793 | 13167.93 | 256.0906 | 125.7322 | 0.015105 | -0.1809
9 | v14 | 1556535 | 1432363 | 14323.63 | 314.8137 | 1510344 | 1439401 | 14394.01 | 308.4672 | 126.2049 | 0.01734 | -0.1923
10 | v14 | 1559896 | 1471436 | 14714.36 | 313.2148 | 1513686 | 1478136 | 14781.36 | 306.6538 | 126.2568 | 0.017926 | -0.18306
11 | v14 | 1559335 | 1963597 | 19635.97 | 310.3721 | 1512978 | 1971181 | 19711.81 | 303.9798 | 126.6585 | 0.017465 | -0.20721
12 | v14 | 1526819 | 2005366 | 20053.66 | 303.3283 | 1480974 | 2013481 | 20134.81 | 296.9551 | 125.2596 | 0.017413 | -0.22172
13 | v14 | 1575153 | 1843275 | 18432.75 | 308.555 | 1528691 | 1850230 | 18502.3 | 302.1783 | 126.9454 | 0.017423 | -0.19003
14 | v14 | 1541740 | 1997988 | 19979.88 | 302.689 | 1495345 | 2005558 | 20055.58 | 296.3392 | 126.7623 | 0.017349 | -0.20683
15 | v14 | 1622756 | 900000 | 9000 | 297.2756 | 1577486 | 904573 | 9045.73 | 291.6743 | 123.6885 | 0.015304 | -0.12495
16 | v14 | 1362021 | 3335767 | 33357.67 | 235.3587 | 1316491 | 3345096 | 33450.96 | 229.535 | 124.3989 | 0.015912 | -0.25489
Display Case Freezer Evaporator Fan ECM Motor replacing Shaded Pole Motor (DLT_SPM to ECM) | [7 empty] | RF-89850
Total Linear feet of Display Cases considered: | [6 empty] | 443 | ft
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/ft-yr) | Peak Demand Reduction (kW/ft) | Natural Gas Savings (therm/ft-yr)
1 | v14 | 1384167 | 3168663 | 31686.63 | 201.779 | 1324276 | 3178189 | 31781.89 | 194.5124 | 135.1941 | 0.016403 | -0.21503
2 | v14 | 1481242 | 2255603 | 22556.03 | 287.3121 | 1420485 | 2263254 | 22632.54 | 278.892 | 137.149 | 0.019007 | -0.17271
3 | v14 | 1436607 | 2190676 | 21906.76 | 236.5578 | 1375348 | 2199163 | 21991.63 | 228.4933 | 138.2822 | 0.018204 | -0.19158
4 | v14 | 1490247 | 1896290 | 18962.9 | 272.4942 | 1428859 | 1903534 | 19035.34 | 264.5521 | 138.5734 | 0.017928 | -0.16352
5 | v14 | 1424239 | 2262289 | 22622.89 | 212.2422 | 1363081 | 2270710 | 22707.1 | 204.7316 | 138.0542 | 0.016954 | -0.19009
6 | v14 | 1534735 | 1413763 | 14137.63 | 258.6538 | 1472321 | 1420090 | 14200.9 | 250.7653 | 140.8894 | 0.017807 | -0.14282
7 | v14 | 1516112 | 1301508 | 13015.08 | 245.9936 | 1453884 | 1308376 | 13083.76 | 238.505 | 140.4695 | 0.016904 | -0.15503
8 | v14 | 1544441 | 1311041 | 13110.41 | 264.0377 | 1482217 | 1316793 | 13167.93 | 256.0906 | 140.4605 | 0.017939 | -0.12984
9 | v14 | 1572507 | 1433464 | 14334.64 | 316.5312 | 1510344 | 1439401 | 14394.01 | 308.4672 | 140.3228 | 0.018203 | -0.13402
10 | v14 | 1575788 | 1472507 | 14725.07 | 315.0092 | 1513686 | 1478136 | 14781.36 | 306.6538 | 140.1851 | 0.018861 | -0.12707
11 | v14 | 1574321 | 1965028 | 19650.28 | 312.7744 | 1512978 | 1971181 | 19711.81 | 303.9798 | 138.4718 | 0.019852 | -0.13889
12 | v14 | 1542316 | 2006646 | 20066.46 | 305.9196 | 1480974 | 2013481 | 20134.81 | 296.9551 | 138.4695 | 0.020236 | -0.15429
13 | v14 | 1589828 | 1844321 | 18443.21 | 310.5176 | 1528691 | 1850230 | 18502.3 | 302.1783 | 138.0068 | 0.018825 | -0.13339
14 | v14 | 1556813 | 1999253 | 19992.53 | 304.8323 | 1495345 | 2005558 | 20055.58 | 296.3392 | 138.754 | 0.019172 | -0.14233
15 | v14 | 1638835 | 900836 | 9008.36 | 299.5549 | 1577486 | 904573 | 9045.73 | 291.6743 | 138.4853 | 0.017789 | -0.084357
16 | v14 | 1376403 | 3337667 | 33376.67 | 237.1674 | 1316491 | 3345096 | 33450.96 | 229.535 | 135.2415 | 0.017229 | -0.1677
Walk-in Cooler Evaporator Fan ECM Motor replacing Shaded Pole Motor (WMT_SPM to ECM) | [7 empty] | RF-65986
Total Number of Motors considered: | [6 empty] | 14 | Motors
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/motor-yr) | Peak Demand Reduction (kW/motor) | Natural Gas Savings (therm/motor-yr)
1 | v14 | 1329999 | 3178160 | 31781.6 | 195.1507 | 1323584 | 3178191 | 31781.91 | 194.4369 | 458.2143 | 0.050986 | -0.022143
2 | v14 | 1426281 | 2263234 | 22632.34 | 279.7657 | 1419773 | 2263257 | 22632.57 | 278.77 | 464.8571 | 0.071121 | -0.016429
3 | v14 | 1381145 | 2199141 | 21991.41 | 229.2023 | 1374638 | 2199169 | 21991.69 | 228.416 | 464.7857 | 0.056164 | -0.02
4 | v14 | 1434684 | 1903519 | 19035.19 | 265.3637 | 1428148 | 1903539 | 19035.39 | 264.4683 | 466.8571 | 0.063957 | -0.014286
5 | v14 | 1368833 | 2270738 | 22707.38 | 205.4717 | 1362377 | 2270758 | 22707.58 | 204.6536 | 461.1429 | 0.058436 | -0.014286
6 | v14 | 1478143 | 1420096 | 14200.96 | 251.511 | 1471599 | 1420093 | 14200.93 | 250.6888 | 467.4286 | 0.058729 | 0.0021429
7 | v14 | 1459709 | 1308364 | 13083.64 | 239.249 | 1453165 | 1308373 | 13083.73 | 238.4259 | 467.4286 | 0.058793 | -0.0064286
8 | v14 | 1488053 | 1316824 | 13168.24 | 256.7563 | 1481505 | 1316793 | 13167.93 | 256.0092 | 467.7143 | 0.053364 | 0.022143
9 | v14 | 1516253 | 1439389 | 14393.89 | 309.3021 | 1509618 | 1439403 | 14394.03 | 308.2343 | 473.9286 | 0.076271 | -0.01
10 | v14 | 1519589 | 1478121 | 14781.21 | 307.3304 | 1512977 | 1478137 | 14781.37 | 306.5737 | 472.2857 | 0.05405 | -0.011429
11 | v14 | 1518895 | 1971169 | 19711.69 | 304.6589 | 1512259 | 1971186 | 19711.86 | 303.9101 | 474 | 0.053486 | -0.012143
12 | v14 | 1486833 | 2013463 | 20134.63 | 297.8251 | 1480264 | 2013482 | 20134.82 | 296.6391 | 469.2143 | 0.084714 | -0.013571
13 | v14 | 1534565 | 1850208 | 18502.08 | 302.8252 | 1527977 | 1850229 | 18502.29 | 302.0963 | 470.5714 | 0.052064 | -0.015
14 | v14 | 1501259 | 2005545 | 20055.45 | 297.0268 | 1494628 | 2005563 | 20055.63 | 296.1406 | 473.6429 | 0.0633 | -0.012857
15 | v14 | 1583243 | 904565 | 9045.65 | 292.3657 | 1576784 | 904573 | 9045.73 | 291.604 | 461.3571 | 0.054407 | -0.0057143
16 | v14 | 1322259 | 3345077 | 33450.77 | 230.3964 | 1315774 | 3345100 | 33451 | 229.4551 | 463.2143 | 0.067236 | -0.016429
Walk-in Cooler Evaporator Fan ECM Motor replacing Permanent Split Capacitor (PSC) Motor (WMT_PSC to ECM) | [8 empty] | RF-73198
Total Number of Motors considered: | [6 empty] | 14 | Motors
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/motor-yr) | Peak Demand Reduction (kW/motor) | Natural Gas Savings (therm/motor-yr)
1 | v14 | 1324276 | 3178189 | 31781.89 | 194.5124 | 1323290 | 3178190 | 31781.9 | 194.4043 | 70.4286 | 0.0077243 | -0.00071429
2 | v14 | 1420485 | 2263254 | 22632.54 | 278.892 | 1419475 | 2263258 | 22632.58 | 278.768 | 72.1429 | 0.0088571 | -0.0028571
3 | v14 | 1375348 | 2199163 | 21991.63 | 228.4933 | 1374342 | 2199146 | 21991.46 | 228.3927 | 71.8571 | 0.0071857 | 0.012143
4 | v14 | 1428859 | 1903534 | 19035.34 | 264.5521 | 1427845 | 1903539 | 19035.39 | 264.4323 | 72.4286 | 0.0085571 | -0.0035714
5 | v14 | 1363081 | 2270710 | 22707.1 | 204.7316 | 1362077 | 2270758 | 22707.58 | 204.632 | 71.7143 | 0.0071143 | -0.034286
6 | v14 | 1472321 | 1420090 | 14200.9 | 250.7653 | 1471300 | 1420094 | 14200.94 | 250.6563 | 72.9286 | 0.0077857 | -0.0028571
7 | v14 | 1453884 | 1308376 | 13083.76 | 238.505 | 1452859 | 1308381 | 13083.81 | 238.3218 | 73.2143 | 0.013086 | -0.0035714
8 | v14 | 1482217 | 1316793 | 13167.93 | 256.0906 | 1481203 | 1316796 | 13167.96 | 255.974 | 72.4286 | 0.0083286 | -0.0021429
9 | v14 | 1510344 | 1439401 | 14394.01 | 308.4672 | 1509305 | 1439404 | 14394.04 | 308.1971 | 74.2143 | 0.019293 | -0.0021429
10 | v14 | 1513686 | 1478136 | 14781.36 | 306.6538 | 1512666 | 1478137 | 14781.37 | 306.5389 | 72.8571 | 0.0082071 | -0.00071429
11 | v14 | 1512978 | 1971181 | 19711.81 | 303.9798 | 1511947 | 1971185 | 19711.85 | 303.8749 | 73.6429 | 0.0074929 | -0.0028571
12 | v14 | 1480974 | 2013481 | 20134.81 | 296.9551 | 1479961 | 2013484 | 20134.84 | 296.6 | 72.3571 | 0.025364 | -0.0021429
13 | v14 | 1528691 | 1850230 | 18502.3 | 302.1783 | 1527667 | 1850227 | 18502.27 | 302.0616 | 73.1429 | 0.0083357 | 0.0021429
14 | v14 | 1495345 | 2005558 | 20055.58 | 296.3392 | 1494324 | 2005566 | 20055.66 | 296.0898 | 72.9286 | 0.017814 | -0.0057143
15 | v14 | 1577486 | 904573 | 9045.73 | 291.6743 | 1576485 | 904573 | 9045.73 | 291.5706 | 71.5 | 0.0074071 | 0
16 | v14 | 1316491 | 3345096 | 33450.96 | 229.535 | 1315475 | 3345100 | 33451 | 229.4326 | 72.5714 | 0.0073143 | -0.0028571
Walk-in Freezer Evaporator Fan ECM Motor replacing Shaded Pole Motor (WLT_SPM to ECM) | [7 empty] | RF-89766
Total Number of Motors considered: | [6 empty] | 14 | Motors
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/motor-yr) | Peak Demand Reduction (kW/motor) | Natural Gas Savings (therm/motor-yr)
1 | v14 | 1332610 | 3178168 | 31781.68 | 195.297 | 1325442 | 3178186 | 31781.86 | 194.636 | 512 | 0.047214 | -0.012857
2 | v14 | 1428977 | 2263242 | 22632.42 | 279.9347 | 1421652 | 2263251 | 22632.51 | 278.9747 | 523.2143 | 0.068571 | -0.0064286
3 | v14 | 1383710 | 2199154 | 21991.54 | 229.4329 | 1376506 | 2199161 | 21991.61 | 228.6099 | 514.5714 | 0.058786 | -0.005
4 | v14 | 1437453 | 1903525 | 19035.25 | 265.6864 | 1430054 | 1903533 | 19035.33 | 264.8281 | 528.5 | 0.061307 | -0.0057143
5 | v14 | 1371434 | 2270695 | 22706.95 | 205.9579 | 1364244 | 2270708 | 22707.08 | 204.8551 | 513.5714 | 0.078771 | -0.0092857
6 | v14 | 1481380 | 1420078 | 14200.78 | 251.973 | 1473617 | 1420089 | 14200.89 | 250.8871 | 554.5 | 0.077564 | -0.0078571
7 | v14 | 1462807 | 1308367 | 13083.67 | 239.3419 | 1455122 | 1308372 | 13083.72 | 238.6243 | 548.9286 | 0.051257 | -0.0035714
8 | v14 | 1490867 | 1316782 | 13167.82 | 257.5777 | 1483445 | 1316790 | 13167.9 | 256.314 | 530.1429 | 0.090264 | -0.0057143
9 | v14 | 1519163 | 1439392 | 14393.92 | 309.4613 | 1511562 | 1439400 | 14394 | 308.5957 | 542.9286 | 0.061829 | -0.0057143
10 | v14 | 1522139 | 1478129 | 14781.29 | 307.6563 | 1514871 | 1478136 | 14781.36 | 306.8708 | 519.1429 | 0.056107 | -0.005
11 | v14 | 1521688 | 1971173 | 19711.73 | 305.0369 | 1514223 | 1971183 | 19711.83 | 304.0227 | 533.2143 | 0.072443 | -0.0071429
12 | v14 | 1489580 | 2013470 | 20134.7 | 298.4968 | 1482176 | 2013479 | 20134.79 | 297.2523 | 528.8571 | 0.088893 | -0.0064286
13 | v14 | 1537330 | 1850218 | 18502.18 | 303.7106 | 1529902 | 1850223 | 18502.23 | 302.3877 | 530.5714 | 0.094493 | -0.0035714
14 | v14 | 1504129 | 2005548 | 20055.48 | 297.6298 | 1496509 | 2005557 | 20055.57 | 296.5673 | 544.2857 | 0.075893 | -0.0064286
15 | v14 | 1586187 | 904566 | 9045.66 | 292.733 | 1578670 | 904571 | 9045.71 | 291.7956 | 536.9286 | 0.066957 | -0.0035714
16 | v14 | 1324425 | 3345080 | 33450.8 | 230.1496 | 1317602 | 3345095 | 33450.95 | 229.6606 | 487.3571 | 0.034929 | -0.010714
Walk-in Freezer Evaporator Fan ECM Motor replacing Permanent Split Capacitor (PSC) Motor (WLT_PSC to ECM) | [8 empty] | RF-78433
Total Number of Motors considered: | [6 empty] | 14 | Motors
|  | Base Case |  |  |  | Measure Case
CZ | Vintage | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Total Elec. Usage (kWh/yr) | Total Natural Gas Usage (kBtu/yr) | Total Natural Gas Usage (therms/yr) | Peak Demand (kW) | Elec. Savings (kWh/motor-yr) | Peak Demand Reduction (kW/motor) | Natural Gas Savings (therm/motor-yr)
1 | v14 | 1324276 | 3178189 | 31781.89 | 194.5124 | 1323505 | 3178190 | 31781.9 | 194.4168 | 55.0714 | 0.0068314 | -0.00071429
2 | v14 | 1420485 | 2263254 | 22632.54 | 278.892 | 1419721 | 2263255 | 22632.55 | 278.7191 | 54.5714 | 0.01235 | -0.00071429
3 | v14 | 1375348 | 2199163 | 21991.63 | 228.4933 | 1374571 | 2199169 | 21991.69 | 228.4146 | 55.5 | 0.0056214 | -0.0042857
4 | v14 | 1428859 | 1903534 | 19035.34 | 264.5521 | 1428071 | 1903538 | 19035.38 | 264.4648 | 56.2857 | 0.0062357 | -0.0028571
5 | v14 | 1363081 | 2270710 | 22707.1 | 204.7316 | 1362288 | 2270708 | 22707.08 | 204.6474 | 56.6429 | 0.0060143 | 0.0014286
6 | v14 | 1472321 | 1420090 | 14200.9 | 250.7653 | 1471482 | 1420091 | 14200.91 | 250.6816 | 59.9286 | 0.0059786 | -0.00071429
7 | v14 | 1453884 | 1308376 | 13083.76 | 238.505 | 1453000 | 1308379 | 13083.79 | 238.4159 | 63.1429 | 0.0063643 | -0.0021429
8 | v14 | 1482217 | 1316793 | 13167.93 | 256.0906 | 1481366 | 1316792 | 13167.92 | 255.9044 | 60.7857 | 0.0133 | 0.00071429
9 | v14 | 1510344 | 1439401 | 14394.01 | 308.4672 | 1509519 | 1439455 | 14394.55 | 308.323 | 58.9286 | 0.0103 | -0.038571
10 | v14 | 1513686 | 1478136 | 14781.36 | 306.6538 | 1512919 | 1478137 | 14781.37 | 306.4842 | 54.7857 | 0.012114 | -0.00071429
11 | v14 | 1512978 | 1971181 | 19711.81 | 303.9798 | 1512192 | 1971185 | 19711.85 | 303.8909 | 56.1429 | 0.00635 | -0.0028571
12 | v14 | 1480974 | 2013481 | 20134.81 | 296.9551 | 1480164 | 2013481 | 20134.81 | 296.7463 | 57.8571 | 0.014914 | 0
13 | v14 | 1528691 | 1850230 | 18502.3 | 302.1783 | 1527878 | 1850226 | 18502.26 | 302.0843 | 58.0714 | 0.0067143 | 0.0028571
14 | v14 | 1495345 | 2005558 | 20055.58 | 296.3392 | 1494552 | 2005558 | 20055.58 | 296.2427 | 56.6429 | 0.0068929 | 0
15 | v14 | 1577486 | 904573 | 9045.73 | 291.6743 | 1576680 | 904573 | 9045.73 | 291.6042 | 57.5714 | 0.0050071 | 0
16 | v14 | 1316491 | 3345096 | 33450.96 | 229.535 | 1315762 | 3345098 | 33450.98 | 229.4527 | 52.0714 | 0.0058786 | -0.0014286

## Reference
The Grocery prototype models were extracted from MASControl 3.00.20, Code 2013 Baseline models.
As an example, the MASControl Code 2013 Baseline models for climate zone 10 is: "Gro-w10-v14-cC13-mNE-HVAC-airAC-SpltPkg-65to109kBtuh".
eQuest modifications of a sample Display Case model is shown below: | eQuest modifications of a sample Walk-In model is shown below:
Baseline Model: | Baseline Model:
Measure Model: | Measure Model: