Workpaper SCGWP100315A

Revision 1

Southern California Gas Company

Customer Programs Department

Multifamily Domestic Hot Water Temperature Reset Controller

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| 0 | March 22, 2010 | Draft for review and comment | Eric Kirchhoff, PE |
| 1 | May 22, 2014 | Original release | Andrew Leishman (CTE) |

Measure Summary Table A

# Table of Contents

Revision History	i

Measure Summary Table A	ii

List of Tables	iv

List of Figures	iv

SECTION 1 - General Measure & Baseline Data	1

1.01	Measure & Delivery Description	1

1.02	DEER Differences Analysis	1

1.03	Code Analysis	1

1.04	Measure Effective Useful Life	2

1.05	Net-to-Gross Ratios for Different Program Strategies	2

1.06	Gross Realization Rate	2

1.07	Time-of-Use Adjustment Factor	2

SECTION 2 - Energy Savings & Demand Reduction Calculations	3

2.01	Load Shapes	3

2.02	Energy Savings	4

2.03	Methodology	4

2.04	Calibration	5

2.05	Measure	5

2.06	Results	7

SECTION 3 - Base Case & Measure Costs	8

3.01	Base Case Cost	8

3.02	Gross Measure Cost	8

3.03	Incremental Measure Cost	8

Attachments	9

List of Tables

Table 1 -	Table 1 - Comparison between the RASS Study and the Baseline of the eQuest Simulation	5

Table 2 - Logic of the Simulated Demand Based Control Strategy	6

Table 3 - Proposed Temperature Modulation and Continuous Monitoring Controller Schedule	7

Table 4 - Simulation Results	8

List of Figures

Figure 1 - DHW Demand for Weekdays, Saturdays and Sundays for Multifamily Buildings	3

Figure 2 - Operating Conditions of the Baseline Controls System	3

Figure 3 – Operating Conditions of the Domestic Hot Water Temperature Modulation and Monitoring Controller	4

General Measure & Baseline Data

Measure & Delivery Description

Measure Description

This measure involves installing additional controls on an existing Central Domestic Hot Water (CDHW) system that implements a temperature modulation protocol based off a real-time data stream or historical trending. Temperature modulation devices lower the temperature at times when hot water demand is expected to be low. A combined temperature modulation with monitoring control can automatically adjust control schedules based on measured hot water draw patterns.  This modulation of supply temperature will reduce the demand on the water heating equipment and result in natural gas savings by reducing the energy lost due to mass output and pipe losses.

Baseline Condition and Associated Inefficiencies

The Baseline CDHW system continuously maintains a supply temperature of 135F. This is sufficient to meet the demand requirements at design conditions, but this temperature is excessive for every other time.

With 135F water running through the recirculation loop, the heat loss through the piping is considered to be at a maximum.

Additionally, every water unit output from the system will result in the maximum amount of energy lost (through mass removal). Therefore any appliances that use hot water will consume the maximum amount of hot water heating energy with the Baseline CDHW system.

Market Applicability

These measures are applicable to multifamily properties only.  The CDHW system must utilize a recirculation loop to be eligible for incentives.

Application Type

The rebate applies to CDHW systems that use natural gas as the primary source of heat. This measure is a retrofit add-on (REA) therefore no existing demand based temperature controls are anticipated for the baseline.

Delivery Method

The preferred delivery method is a downstream rebate offered to the gas customer acquiring the controls system.

DEER Differences Analysis

    - There is no identical measure in the DEER database. However a similar measure exists for commercial and large institutional buildings. This workpaper adopts the useful life from the DEER database.

Code Analysis

- CA Title 24 Section 110.3 states the mandatory requirements as below.

  - Controls for hot water distribution systems - Service hot water systems with circulating pumps or with electrical heat trace systems shall be capable of automatically turning off the system.

Measure Effective Useful Life

DEER2014 includes equipment useful life (EUL) values for “Hot Water Loop Controllers” at 10 years for the non-residential sector, but nothing for the residential sector. However, since multifamily buildings have similar equipment to non-residential buildings, it was determined that 10 years is an appropriate EUL.

Net-to-Gross Ratios for Different Program Strategies

The DEER2014 documents recommend a net-to-gross ratio (NTGR) of 0.55 for “All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years”, which includes Domestic Hot Water Temperature Reset Controls.

Gross Realization Rate

Gross realization rate of 1.00 is applied to the measures in this document.

Time-of-Use Adjustment Factor

- N/A

Energy Savings & Demand Reduction Calculations

Load Shapes

To account for the unique Domestic Hot Water usage that can occur in multifamily units, the following default schedules were used in the eQuest simulation. These schedules were developed in two parts by the software developers of eQuest. The first portion is the design criteria where the maximum daily average consumption is calculated. The second portion is the fractional profile, which provides the variability throughout the day. The product of these two variables is the chart below.

DHW Demand for Weekdays, Saturdays and Sundays for Multifamily Buildings

In Figure 2 and 3 the daily operating conditions can be referenced for both control strategies.

Operating Conditions of the Baseline Controls System

Figure-2 above presents the hot water supply temperature (135°F), mixed water temperature -variable- (from the addition of makeup cold water to the return hot water in the recirculating loop), and including hot water draw schedule and hot water recirculation flow (both in gpm).

Operating Conditions of CDHW Temperature Modulation and Monitoring Controller

Temperature modulation control in (fig.-3) was assumed to reduce the supply temperature by 22°F (135-113°F) from 1 am to 5 am in the morning, and reaching maximum setpoint temperature of 135°F during peak hot water demand at 8am and 5pm before it drops again at the night hours.  A continuous monitoring system monitors different operation parameters of the DHW system and automatically provides system operation status and malfunction updates to system operators.

All other load shapes associated with this analysis are defaulted within the eQuest simulation software and can be referenced within the attached simulation files directly. Below is a brief list of load shapes that fit into this category:

Occupancy Fraction Profile

Lighting Fraction Profile

Task Lighting Fraction Profile

Miscellaneous Load Fraction Profile

…etc.

Energy Savings

Annual Electric Energy Savings

No electric energy savings will result from this measure.

Electric Demand Reduction

No electric demand reduction will result from this measure

Annual Gas Energy Savings

The goal of this analysis was to determine the annual Therm savings of installing temperature modulation control on a CDHW system serving a multifamily building.

Methodology

The initial step is to establish a simulation with as many similarities to the DEER database simulations as possible. This was done by referencing the prototypes published in 2005, and the initial eQuest default values. Below is a brief list of some of the key variables assumed in this manner:

eQuest Default Occupancy, Lighting, Ventilation, Miscellaneous Load Schedules

The most up-to-date eQuest schedules were chosen over the DEER 2005 schedules because the values found in 2005 analysis were relatively extreme and non-continuous compared to the newer schedules within the eQuest software.

Design Domestic Hot Water Flow (GPM) is approximately 1.90GPM.  This is a product from the eQuest and the relationship can be referenced in the equation below.

Design GPM= Daily Gal. /Person*Number of PeopleNumber of Active Hours/Day*60 Minutes/Hr

- Daily Gal. / Person / Day = 20

- Number of People = 36

- Number of Active Hours / Day = 6.329

To further the accuracy of the simulation a few details were added to ensure that the measure was being applied to realistic conditions:

The domestic hot water loop within the DEER Multi-Family model was altered to have 50% recirculation. This value was referenced within the DEER DHW Properties document under “Motels”.

A conservative estimated of the total heat loss through the piping (5F).

The measure variable that will be altered to quantify the energy savings is the Heating Schedule, which is a constant temperature of 135F for the baseline.

All other specific details can be referenced in the attached excel document.

Calibration

With these variables in place, the baseline simulation was compared with the Residential Appliance Saturation (RASS) study. The table below shows the comparison between the two sources:

Comparison between the RASS Study and the Baseline of the eQuest Simulation

Considering the statistical variance of the data collected by the RASS Study, the estimated error of 18% is deemed reasonable.

Measure

With a calibrated simulation, the demand based hot water temperature schedules were input into the simulation to emulate a demand based temperature controller.

The schedule was developed by referencing the eQuest default fractional load profiles on the domestic hot water circulation loops. It was assumed that a load factor of just above 0% would have a setpoint of 110F and a load factor of 67% would have a setpoint of 135F. Any load factor between the two reference points would simply be interpolated.

Table 2 - Logic of the Simulated Demand Based Control Strategy

| Load Factor | Set Point (F) |
| --- | --- |
| 0% | 110F |
| 0-67% | Interpolated |
| 67%+ | 135F |

- Below is a table detailing out the demand based curves for the simulation used in this analysis.

Proposed Temperature Modulation and Continuous Monitoring Controller Schedule

Results

With this control strategy implemented the recirculation loop will require less heating in low usage periods due to the lower setpoint. The results are tabulated in the table below:

Simulation Results

For further details it is recommended to reference the eQuest simulation and corresponding engineering spreadsheets.

Base Case & Measure Costs

Base Case Cost

This measure is a retrofit measure and as such, the base case condition is to do nothing.  Therefore the base case cost is $0.

Gross Measure Cost

The gross measure costs associated with this measure include the material and labor associated with the installation of the controller, sensors, utility hookup, equipment interfacing, adjustments needed to bring the system up to proper operating condition, and commissioning of the system upon completion of the installation.  Based on SCG’s historical records associated with the Reset Controller measure the material and labor costs amounted to $1,400 per controller unit (or $1,400 / 35 dwelling units = $40 per dwelling unit).  No cost information is available to account for additional cost to the customer associated with the RCx effort.  It is anticipated these costs will be minor and will be absorbed into the labor costs already allocated to the installation of the controller.

Incremental Measure Cost

The incremental measure costs associated with this measure are the same listed under Article 3.02 “Gross Measure Cost.”  For reference the IMC is $40 per dwelling unit.

Attachments

Attachment A – Simulation Results and Summary

Attachment B – eQuest Simulation

References

Technology and Measure Cost Data/Effective and Remaining Useful Life (EUL/RUL) Values, http://www.deeresources.com/index. “EUL_Summary_10-1-08.xls”

DEER2013 Net-To-Gross Ratios, http://www.deeresources.com, “READI v1.0.3”,

eQuest 3-64, http://www.doe2.com/

DEER 2005 Multifamily Prototype Model

DEER  2005 DHW Properties

Residential Appliance Saturation Study (RASS)