Workpaper SCGWP110812A

Revision 3

Southern California Gas Company

Customer Programs Department

Pipe Insulation

(Non-Space Conditioning)

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| --- | Jan. 31, 2006 | Original release | EEA (S. Knoke) |
| A | May 9, 2006 | - Added medium-pressure steam pipes - Other minor changes | EEA (S. Knoke) |
| B | July 6, 2006 | - Added Review and Acceptance page - Added Revision History page - Added Disclaimer page - Added discussion addressing reluctance to adopt technology in Executive Summary - Added line for steam pressure range to table in Executive Summary - Corrected minor error in the annual energy savings calculations - Added 3 and 4-inch pipe to Table 4 - Added annual energy savings chart (Figure 1) in Section 3 and attachment showing calculations - Added discussion addressing reluctance to adopt technology in Incentive and Payback chapter - Renumbered attachments | EEA (S. Knoke) |
| C | Jan. 26, 2007 | - Added smaller pipe sizes - Added second category for annual operating hours - Reduced incentives to two categories - Increased annual energy savings to 6 categories - Added cost to SCG | EEA (S. Knoke) |
| D | Mar. 23, 2007 | - Removed CPUC attachment | EEA (S. Knoke) |
| E | Sept 5, 2008 | - Added large pipes at small commercial - Added insulation on pipe fittings | EEA (S. Knoke) |
| 1 | Mar. 26,2009 | *Updated DEER values (NTG, EUL, Cost ) | Lucie Sidibe (SDGE) |
| 2 | Aug. 12, 2009 | Inclusion of CPUC’s comments | Stu Knoke Chan Paek |
| 3 | May 12, 2014 | 1. New WP template “SCG WP Template_Rev3” 2. Changed program type to REA 3. Include savings specific to each CA climate zone 3. Savings distinguished between indoor and outdoor pipes 5. Updated NTG 6. Updated CEC Boiler Data | Michael Crayne (PECI) |

Measure Summary Table A

| Measure ID | Measure Name | Program Type (ER, ROB, NC, RC,CE) | EUL / RUL (yr) | CZ | Building Type | Building Vintage | Unit Definition | NTGR IMC | NTGR Savings | Implementation/ Delivery Method | GRR | ISR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 307 | Large Commercial Pipe Insulation Hot Water <1" Pipe, Indoor | REA | 11 | Any | Com | Any | Linear Foot | 0.6 | 0.6 | PreReb | 1 | 1 |
| 308 | Large Commercial Pipe Insulation Hot Water <1" Pipe, Outdoor | REA | 11 | 1 | Com | Any | Linear Foot | 0.6 | 0.6 | PreReb | 1 | 1 |
| 324 | Large Commercial Pipe Insulation Hot Water >=1" Pipe, Indoor | REA | 11 | Any | Com | Any | Linear Foot | 0.6 | 0.6 | PreReb | 1 | 1 |
| 325 | Large Commercial Pipe Insulation Hot Water >=1" Pipe, Outdoor | REA | 11 | 1 | Com | Any | Linear Foot | 0.6 | 0.6 | PreReb | 1 | 1 |
| 205 | Large Commercial Fitting Insulation Hot Water <1" Pipe, Indoor | REA | 11 | Amy | Com | Any | Each Fitting | 0.6 | 0.6 | PreReb | 1 | 1 |
| 206 | Large Commercial Fitting Insulation Hot Water <1" Pipe, Outdoor | REA | 11 | 1 | Com | Any | Each Fitting | 0.6 | 0.6 | PreReb | 1 | 1 |
| 222 | Large Commercial Fitting Insulation Hot Water >=1" Pipe, Indoor | REA | 11 | Any | Com | Any | Each Fitting | 0.6 | 0.6 | PreReb | 1 | 1 |
| 223 | Large Commercial Fitting Insulation Hot Water >=1" Pipe, Outdoor | REA | 11 | 1 | Com | Any | Each Fitting | 0.6 | 0.6 | PreReb | 1 | 1 |

Note: For the complete list of Measures, refer to the accompanying calculation spreadsheets [A]

Measure Summary Table B

| Measure ID | 1st Baseline |  |  |  |  |  | 2nd Baseline |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Gas Savings (Therms) | User Entered kW Savings per unit (kW/unit) | Gross Unit Annual Electricity Savings (kWh/unit) | Base Case Cost ($/unit) | Measure Cost ($/unit) | Incremental Measure Cost ($/unit) | Gas Savings (Therms) | User Entered kW Savings per unit (kW/unit) | Gross Unit Annual Electricity Savings (kWh/unit) | Base Case Cost ($/unit) | Measure Cost ($/unit) | Incremental Measure Cost ($/unit) |
| 307 | 1.95 | 0 | 0 | $0.00 | $5.22 | $5.22 | N/A | N/A | N/A | N/A | N/A | N/A |
| 308 | 8.06 | 0 | 0 | $0.00 | $5.22 | $5.22 | N/A | N/A | N/A | N/A | N/A | N/A |
| 324 | 3.82 | 0 | 0 | $0.00 | $5.22 | $5.22 | N/A | N/A | N/A | N/A | N/A | N/A |
| 325 | 14.50 | 0 | 0 | $0.00 | $5.22 | $5.22 | N/A | N/A | N/A | N/A | N/A | N/A |
| 205 | 0.59 | 0 | 0 | $0.00 | $7.73 | $7.73 | N/A | N/A | N/A | N/A | N/A | N/A |
| 206 | 2.31 | 0 | 0 | $0.00 | $7.87 | $7.87 | N/A | N/A | N/A | N/A | N/A | N/A |
| 222 | 1.58 | 0 | 0 | $0.00 | $7.87 | $7.87 | N/A | N/A | N/A | N/A | N/A | N/A |
| 223 | 5.85 | 0 | 0 | $0.00 | $9.60 | $9.60 | N/A | N/A | N/A | N/A | N/A | N/A |

Note: For the complete list of Measures, refer to the accompanying calculation spreadsheets [A]

# Table of Contents

Revision History	i

Measure Summary Table A	ii

Measure Summary Table B	iii

List of Figures	v

List of Tables	v

SECTION 1 - General Measure & Baseline Data	1

1.01	Measure & Delivery Description	1

1.02	DEER Differences Analysis	2

1.03	Code Analysis	2

1.04	Measure Effective Useful Life	2

1.05	Net-to-Gross Ratios for Different Program Strategies	3

1.06	Gross Realization Rate	3

1.07	Time-of-Use Adjustment Factor	3

1.08	In-service rate/first year installation rate	3

1.09	EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	3

SECTION 2 - Energy Savings & Demand Reduction Calculations	3

2.01	Load Shapes	3

2.02	Energy Savings	4

SECTION 3 - Base Case & Measure Costs	11

3.01	Base Case Cost	11

3.02	Gross Measure Cost	11

3.03	Incremental Measure Cost	12

Attachments	15

References	16

List of Figures

Figure 1 -	CEC Efficiency Data (Hot Water Boilers ≤ 2 MMBtuh)	5

Figure 2 -	CEC Efficiency Data (Hot Water Boilers 2-10 MMBtuh)	5

Figure 3 -	CEC Efficiency Data (Steam Boilers ≤ 2 MMBtuh)	6

Figure 4 -	CEC Efficiency Data (Steam Boilers 2-10 MMBtuh)	6

List of Tables

Table 1 -	DEER Difference Summary	2

Table 2 -	Code Summary	2

Table 3 -	Average Steam Pressure Calculation	7

Table 4 -	Fluid Temperature Specification and Assumptions	8

Table 5 -	Average Ambient Temperatures	8

Table 6 -	Average Wind Speeds	9

Table 7 -	Key Parameters for Pipe and Fitting Insulation	10

Table 8 -	Pipe Insulation Cost in DEER 2014	11

Table 9 -	Pipe Insulation Costs (Material & Installation) Provided by Vendor	12

General Measure & Baseline Data

Measure & Delivery Description

Measure Description – Many commercial and industrial customers – particularly smaller, hard to reach businesses – configure piping systems with sub-optimal amounts of insulation. This measure addresses cost-effective energy efficiency opportunities in the pipe insulation area, and encompasses both fiberglass and heavier duty insulation systems such as Perlite and rigid phenolic insulation.  Pipe insulation applications in the industrial sector include brine, plating solutions, steam, condensate, hot water, chilled water, and refrigerant; in the commercial sector they include steam, hot water, chilled water, and refrigerant. See Appendix A for a more detailed description of this measure. Although the payback is short, experience shows that many customers are not installing pipe insulation, perhaps due to a general lack of awareness of the potential energy savings from pipe insulation.  The incentives described in this measure are expected to stimulate adoption primarily due to increased awareness, although the incentives also reduce economic barriers.

Base Case Description – The base case for this measure is existing, uninsulated commercial or industrial pipe systems used to transport hot fluids.

Delivery Mechanism – The delivery mechanism for this measure is Prescriptive Rebate.

Program Type/Install Type – The program type/install type for this measure is Retrofit Add-On (REA), which refers to measures that are added onto existing equipment to improve efficiency and performance.

Implementation Requirements – This measure is applicable to small commercial, large commercial and industrial buildings with existing uninsulated pipe systems. This measure is applicable in all CA climate zones.

Terms & Conditions

These measures are applicable to any small or medium commercial or industrial pipe insulation retrofit (i.e., non-new construction) application.  They cannot be used for residential purposes.

Insulation required by California Building Code (Title 24) or employee safety laws (Occupational Safety and Health Administration) is not eligible for a rebate.

The pipes must transfer hot water, low-pressure or high-pressure steam directly from gas-fired equipment. The fluid type must be indicated. If the fluid is steam, the pressure of the steam must also be indicated.

Maximum qualifying pipe diameter is 3”, and minimum qualifying pipe diameter is ½”.

The length of insulation to be installed at each pipe size must be indicated.

A minimum of 1” of pipe insulation must be added to existing bare commercial or industrial steel or copper pipe.

The hours of operation must be indicated on the top of the application.

Acceptable types of insulation for hot water pipes include elastomeric foam rubber, polyethylene foam, UV-resistant polyethylene foam and rigid polyurethane foam.

Acceptable types of insulation for steam pipes include silicone foam rubber, melamine foam, rigid urethane-based foam, cellular glass, rigid fiberglass and rigid mineral wool.

Replacement of damaged (existing) insulation is not eligible for a rebate.

The manufacturer’s specification sheet must be submitted with the application.

DEER Differences Analysis

These specific measure energy saving results and calculation method are not included in the DEER 2014. The liquid circulation measures included in DEER 2014 are:

- D03-044: Chilled Water Reset

- D03-045: Hot Water Reset

- D03-046: Variable Flow Chilled Water Loop

- D03-048: Variable Flow Hot Water Loop

- D03-070: Hydronic Heat Pump Var Flow Valve

- D03-089: Effic. Motors - Chilled Water Loop Pumps

- D03-090: Effic. Motors - Hot Water Loop Pumps

- D03-091: Effic. Motors - Cond. Water Loop Pumps

- D03-095: Circulation Pump Timeclock Retrofit

None of these measures has an energy impact similar to installing pipe insulation, as these measures address the energy used to circulate the fluid or heat/cool it at the plant, rather than addressing the heat losses that occur during circulation of the fluid.

The insulation measures contained in DEER 2014 pertain to building envelope insulation, which has a much different energy impact than the measure contained in this work paper.

However, the EUL, NTG, and other values used in this work paper are based on available information in DEER 2008.

- DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER does not contain this type of measure |
| DEER Version | N/A |
| DEER Run ID and Measure Name | N/A |

Code Analysis

Application of the pipe insulation to hot water piping covered by current CA Title 24 and OSHA Standard is not qualified. While Title 24 (2013) gives requirements for pipe insulation, this is a REA measure and so remains applicable for installations on existing, uninsulated pipe systems.

- Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2013) | Section 120.3, Pages 119-120 | July 1, 2014 |
| Title 20 (2012) | N/A | N/A |

Measure Effective Useful Life

Effective useful life (EUL) for these measures is listed in the CPUC DEER EUL tables. Pipe insulation is identified as having an 11-year life (WtrHt-Pipelns-Gas) for a gas water heater and a life of 13 years for an electric water heater.  A value of 11 years is used in this work paper as the recommended life of pipe insulation.

Net-to-Gross Ratios for Different Program Strategies

Net-To-Gross Ratio (NTGR) values were obtained from the “DEER2011_NTGR_2012-05-16.xls” spreadsheet.

For the Small Commercial and Large Commercial pipe/fitting insulation, the Com-Default>2yrs NTGR of 0.6 was used.

For the Industrial pipe/fitting insulation, the NonRes-sAll-mPipeIns NTGR of 0.71 was used.

Gross Realization Rate

A gross realization rate of 1.00 was applied to measures in this document.

Time-of-Use Adjustment Factor

The Time-of-Use (TOU) adjustment factor for this measure is 0, as this measure is not related to A/C equipment.

In-service rate/first year installation rate

An in-service rate (ISR) of 1.00 was applied to the measures in this document. This corresponds to the default GSIA value (Def-GSIA) from DEER 2011, which is used since a pipe insulation GSIA is not specified.

EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

The annual operating hours for Small Commercial hot water and steam systems were taken from a survey performed in Southern California by kW Engineering2 in November 2006. The intent of this survey was to determine potential savings from steam trap replacements in dry cleaner facilities, but the operating hours of the boiler systems that were surveyed are relevant to the measure in this work paper.

The average steam pressures input into the savings calculations were calculated using values from a survey of steam traps performed by Enbridge2. The sites in this survey represented a number of different building types, including pharmaceutical manufacturing, university, and paper mill. The sites were surveyed between 2002 and 2005. The steam pressures of the surveyed facilities were used to determine the average pressure for steam systems ≤ 15 psig and > 15 psig.

Energy Savings & Demand Reduction Calculations

Load Shapes

The load shape for this measure is the “Annual” gas load shape, as these pipe systems are expected to be operational throughout the year.

Energy Savings

Savings are based on installing insulation on bare pipes and fittings.  The energy savings that will be achieved depend upon pipe parameters, insulation parameters, boiler efficiency, annual operating hours, and other parameters such as fluid properties and ambient temperature.  The energy savings results are expressed per linear foot (LF) of straight pipe or per fitting.

Pipe Parameters – Steam and hot water pipe sizes ranging from ½ inch to 4 inches are commonly seen in commercial and industrial facilities.  Pipe sizes were divided into two ranges:  1-inch or less, and greater than 1-inch.  The physical dimensions of a Schedule-40 standard pipe size of ¾-inch were selected to represent ½-inch, ¾-inch, and 1-inch pipe sizes.  The 2006-2008 program evaluation effort found that the average pipe diameter for pipes whose diameter was greater than 1 inch was 1.7 inches.  Therefore, the physical dimensions of 1.5-inch and 2-inch Schedule-40 standard pipe sizes were interpolated to represent pipe sizes larger than 1-inch.  The thermal conductivity and surface emittance of black steel pipe were applied in all cases.  The thermal conductivity of steel (314.4 Btu-in/hr-ft2-F or 26.2 Btu/hr-ft/F) is required to calculate the outside wall temperature of the steel pipe.  In addition, the radiation from the bare pipe surface is characterized by an emittance of 0.94.

Insulation Parameters – Acceptable types of pipe insulation for hot water pipes include polyethylene foam (up to 180 °F), UV-resistant polyethylene foam, and elastomer foam rubber.  Acceptable types of insulation for steam pipes include silicone foam rubber (to 425 °F), melamine foam (to 400 °F), rigid urethane-based foam (to 300 °F), cellular glass (to 400 °F), fiberglass, and mineral wool.  The protection offered by jacketing is also recommended, especially outdoors.  Only some jacket materials are suitable for outdoor use, such aluminum, UV-resistant PVC, and paints.  The parameters used to describe the insulation (thermal conductivity, surface emittance) are generally based on prefabricated 1-inch thick fiberglass pipe insulation with paper or aluminum wrap (paper for indoor locations and aluminum for outdoor locations).  The energy savings analysis is based on adding 1-inch thick insulation around bare Schedule 40 black steel pipe.  In addition to insulation thickness, it is necessary to know the thermal conductivity of the insulation and the thermal radiation emittance of the insulation wrap.  The thermal conductivity of pipe insulation varies somewhat by material and temperature rating.  Based on two sources (ASHRAE Handbook and McMaster-Carr catalog, a thermal conductivity value of 0.29 Btu-in / hr-ft2-°F (0.024 Btu/hr-ft-°F) was chosen for both hot water and steam pipe.  In addition, the insulation surface participates in radiative heat transfer.  Pipe insulation used indoors typically has a paper wrap (with an emittance of about 0.9) and pipe insulation used outdoors typically has an aluminum wrap (with an emittance of about 0.1).  These emittances are not critical parameters, since the heat loss is not very sensitive to radiative heat loss from the rather cool surface of the insulation, an average value of 0.5 was applied.

Boiler Efficiency – To calculate the natural gas energy savings from insulating bare hot water and steam pipes, it is necessary to have an estimate of the thermal efficiency of the hot water or steam generation boiler.  To determine representative boiler efficiencies, data from the California Energy Commission (CEC) was examined.  CEC lists several hundred natural gas boilers, and these boilers were divided into four groups:

≤ 2 MMBtuh (hot water only)

2-10 MMBtuh (hot water only)

≤ 2 MMBtuh (steam only)

2-10 MMBtuh (steam only)

The CEC results for hot water boilers are plotted in Figure 1 and Figure 2.  As shown in both figures, a relatively large number of boilers are rated at 80% thermal efficiency.  The combustion efficiency is assumed to be 2% higher than the overall thermal efficiency.  Based on these data, a combustion efficiency value of 82% was used to compute the cost of hot water generation.

The CEC results for steam boilers are plotted in Figure 3 and Figure 4.  As shown in both figures, most boilers are rated to be in the range of 80% to 82% efficiency.  Based on these data, a combustion efficiency value of 83% was used to compute the cost of steam generation.

CEC Efficiency Data (Hot Water Boilers ≤ 2 MMBtuh)

CEC Efficiency Data (Hot Water Boilers 2-10 MMBtuh)

CEC Efficiency Data (Steam Boilers ≤ 2 MMBtuh)

CEC Efficiency Data (Steam Boilers 2-10 MMBtuh)

Annual Operating Hours and Other Assumptions – Commercial establishments might operate their steam system anywhere from about 2,000 hours per year (8 hours/day, 5 days/week) to about 6,000 hours per year (16 hours/day, 7 days/week).

The annual operating time for small commercial steam and hot water systems is based on the average operating time of small commercial dry cleaners establishments.  Based on a survey performed in Southern California by kW Engineering2, the average annual operating time for the small commercial category is 2,425 hours per year.

Operating hours also vary for large commercial applications such as lodging facilities, schools, prisons, office buildings, and dry cleaners serving industrial customers.  Based on an operating schedule of 12 hours per day for 365 days per year, an annual operating time of 4,380 hours was adopted.

Actual operating hours of industrial steam and hot water system vary depending on end-use applications, boiler size, and seasonal variations.  Also, not every pipe in the system operates for the same number of hours in a year, but most large plants keep the system operating essentially all the time.  In this work paper, the basis used for annual operating hours is large plants that nominally operate 24 hour per day, 7 days per week, except that the majority of the hot water or steam system is assumed to be unheated for a total of six weeks per year to allow for scheduled and unscheduled maintenance activities, implying a total of 7,752 hours per year at normal operating temperature.

To determine the energy savings, additional assumptions were made concerning the pressure, temperature, and average velocity of the hot water and steam inside the pipe; the average ambient temperature; and the average speed of the air moving past the pipe.

The average steam pressure was calculated using an Enbridge survey2 of steam traps.  For this workpaper, the Enbridge data was divided into two pressure groups:  ≤ 15 psig and > 15 psig.  As shown in Table 3 -, the average steam pressure for the two groups was calculated by weighting each pressure by the number of leaking traps.  For each pressure category, the weighted average is the sum of the average pressure in the range times the number of traps in the range, divided by the sum of the number of traps in the range.  The resulting values for the low-and medium-pressure categories are 10.9 and 85.9 psig, respectively.

The temperature ranges of the hot water and low-pressure steam are specified in the 2006 Express Efficiency Rebate Program brochure and are listed in Table 4 -.  Based on Energy Division recommendations, the temperature of the hot water was assumed to be 150 °F.  The temperatures of the low-pressure and medium-pressure steam correspond to the saturated temperatures of water at the average steam pressures obtained above, which are 241 °F and 328 °F.

The flow velocity is needed to calculate the pipe inside wall temperature; it is usually based on considerations of pressure drop due to pipe friction.  A typical water flow speed of 10 ft/s and a typical steam flow speed of 100 ft/s are assumed.  These are not critical parameters, since the heat loss is not very sensitive to fluid velocity inside the pipe.

Savings were determined for pipes in both indoor and outdoor settings. For indoor pipes, an ambient temperature of 75 °F was used, as recommended by The Energy Division. Air speed for the indoor pipes was assumed to be 0 mph.

For outdoor pipes, the ambient temperature and wind speed were calculated using the Title 24 (2013) weather data. The average annual temperature and wind speed in each climate zone was determined by averaging the ambient temperatures and wind speeds (converted from knots to miles per hour) in the weather files over the estimated operating hours for each building type. See Table 5 - for the average ambient temperatures for each climate zone and building type and Table 6 - for the average wind speeds for each climate zone and building type.

- Average Steam Pressure Calculation

| Pressure range (psig) | Number of Steam Traps | Average Pressure in Range (psig) | (Average Pressure) X (Number in Range) | Average Pressure in Category (psig) |
| --- | --- | --- | --- | --- |
| Low Pressure (≤ 15 psig) |  |  |  |  |
| <5 | 234 | 2.5 | 585 | 10.9 |
| 5 | 0 | 5 | 0 |  |
| 6 to 9 | 24 | 7.5 | 180 |  |
| 10 | 515 | 10 | 5150 |  |
| 11 to 14 | 249 | 12.5 | 3112.5 |  |
| 15 | 517 | 15 | 7755 |  |
| Medium Pressure (> 15 psig) |  |  |  |  |
| 16 to 19 | 37 | 17.5 | 647.5 | 85.9 |
| 20 | 28 | 20 | 560 |  |
| 25 | 33 | 25 | 825 |  |
| 30 | 73 | 30 | 2190 |  |
| 40 | 61 | 40 | 2440 |  |
| 50 | 26 | 50 | 1300 |  |
| 60 | 60 | 60 | 3600 |  |
| 61 to 99 | 175 | 80 | 14000 |  |
| 100 | 45 | 100 | 4500 |  |
| 101 to 124 | 117 | 112.5 | 13162.5 |  |
| 125 | 14 | 125 | 1750 |  |
| 150 | 54 | 150 | 8100 |  |
| 200 | 2 | 200 | 400 |  |
| 250+ | 26 | 425 | 11050 |  |

- Fluid Temperature Specification and Assumptions

| Working Fluid | Fluid Temperature (F) |  |
| --- | --- | --- |
|  | Specification | Used in Analysis |
| Hot Water | 120-200 | 150 |
| Low-Pressure Steam | 200-250 | 241 |
| Medium-Pressure Steam | 250-500 | 328 |

- Average Ambient Temperatures

| Climate Zone | Average Ambient Temperature (F) |  |  |
| --- | --- | --- | --- |
|  | Small Commercial | Large Commercial | Industrial |
| 1 | 53.09 | 53.14 | 51.08 |
| 2 | 60.46 | 61.18 | 57.01 |
| 3 | 59.18 | 59.19 | 56.76 |
| 4 | 62.94 | 63.38 | 59.24 |
| 5 | 60.31 | 59.64 | 55.54 |
| 6 | 65.67 | 65.03 | 61.47 |
| 7 | 63.92 | 63.75 | 62.24 |
| 8 | 67.02 | 66.86 | 63.44 |
| 9 | 66.94 | 66.94 | 63.53 |
| 10 | 68.57 | 68.55 | 63.87 |
| 11 | 65.37 | 66.26 | 62.97 |
| 12 | 63.21 | 64.17 | 60.63 |
| 13 | 65.86 | 66.90 | 63.85 |
| 14 | 67.34 | 67.32 | 62.43 |
| 15 | 78.54 | 78.83 | 75.21 |
| 16 | 53.70 | 53.54 | 51.50 |

- Average Wind Speeds

| Climate Zone | Average Wind Speed (mph) |  |  |
| --- | --- | --- | --- |
|  | Small Commercial | Large Commercial | Industrial |
| 1 | 7.13 | 7.52 | 6.18 |
| 2 | 4.98 | 5.71 | 5.08 |
| 3 | 8.78 | 9.51 | 8.76 |
| 4 | 6.86 | 7.87 | 7.08 |
| 5 | 8.23 | 8.89 | 6.95 |
| 6 | 6.48 | 7.05 | 6.34 |
| 7 | 7.57 | 7.78 | 6.26 |
| 8 | 5.10 | 5.53 | 4.52 |
| 9 | 5.95 | 6.51 | 5.73 |
| 10 | 6.16 | 6.85 | 5.50 |
| 11 | 8.45 | 8.57 | 7.82 |
| 12 | 6.66 | 6.98 | 6.44 |
| 13 | 5.39 | 5.79 | 5.96 |
| 14 | 8.74 | 9.92 | 9.60 |
| 15 | 6.10 | 6.85 | 6.92 |
| 16 | 6.70 | 6.58 | 5.64 |

Annual Energy Savings – The annual energy savings attributed to the installation of pipe insulation was calculated based on the operating time, steam boiler efficiency, and reduction in heat loss.  The complete heat loss calculations for straight pipe are included in Attachments [C] and [D] and for pipe fittings are included in Attachments [E] and [F].  The calculations included the following heat transfer mechanisms:

Turbulent forced convection heat transfer inside the pipe or fitting

Steady conduction through the pipe or fitting wall and through the insulation

Forced convection around a horizontal cylindrical pipe or fitting if the pipe or fitting is bare and around the insulation if the pipe or fitting is insulated

Radiation from the pipe or fitting surface if the pipe or fitting is bare and from the insulation surface if the pipe or fitting is insulated

Due to the radiation, the heat transfer from the bare pipe, fitting, or insulation is a non-linear function of temperature.  In the heat transfer calculations in Attachments [C]-[F], an iterative scheme was used to converge on the temperature of the outer surface of the bare pipe or insulation.  With careful choice of initial conditions, satisfactory convergence was achieved in ten iterations for each.

Pipe fittings include elbows, tees, valves, unions, flanges, reducers, bushings, couplings, and more.  The pipe fittings were modeled as a piece of straight pipe with the length of a tee and with the outer dimensions of the elbow and tee.

The annual energy saved by pipe insulation can be calculated as follows:

∆Q = 0.00001 x T x (Qp - Qi) / Eb					Eqn-1

∆Q – Energy Saved (therms/yr/LF), as a result of installing the pipe insulation.

T – Scheduled Operating Time (hrs/yr).  The scheduled operating time represents the time that gas boiler is expected to be in operation.  Hours when the equipment is shut down are not included.

Qp – Heat Loss from Bare Pipe (Btu/hr/LF)

Qi – Heat Loss from Insulated Pipe (Btu/hr/LF)

Eb – Efficiency (%) of the boiler being used to generate the hot water or steam in the pipe.

The key parameters for the different fluid types and pipe sizes are shown below. These parameters were entered into the savings calculations, and the ambient temperature and air speed were varied to produce savings for each climate zone and indoor and outdoor pipe locations. This resulted in 612 different savings values. Savings for each measure can be found in the attached savings spreadsheets [A].

- Key Parameters for Pipe and Fitting Insulation

| Parameter | Hot Water |  | Low-pressure Steam (0-15 psig) |  | Medium-pressure Steam (>15 psig) |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pipe Size (inch) | ≤1" | >1" | ≤1" | >1" | ≤1" | >1" |
| Insulation Thickness (inch) | 1 | 1 | 1 | 1 | 1 | 1 |
| Average Steam Pressure (psig) | --- | --- | 10.9 | 10.9 | 85.9 | 85.9 |
| Temperature, Fluid in Pipe (F) | 150 | 150 | 241 | 241 | 328 | 328 |
| Pipe Parameters |  |  |  |  |  |  |
| Pipe Size for Heat Loss Calculations (inch) | 0.75 | 1.7 | 0.75 | 1.7 | 0.75 | 1.7 |
| Outer Diameter, Pipe, Actual (in.) | 1.05 | 2.09 | 1.05 | 2.09 | 1.05 | 2.09 |
| Outer Diameter, Fitting, Actual (in.) | 1.46 | 2.6 | 1.46 | 2.6 | 1.46 | 2.6 |
| Insulation Parameters |  |  |  |  |  |  |
| Outer Diameter, Pipe Insulation (in.) | 3.05 | 4.09 | 3.05 | 4.09 | 3.05 | 4.09 |
| Outer Diameter, Fitting Insulation (in.) | 3.46 | 4.60 | 3.46 | 4.60 | 3.46 | 4.60 |
| Plant Parameters |  |  |  |  |  |  |
| Boiler Efficiency (%) | 82% | 82% | 83% | 83% | 83% | 83% |

Base Case & Measure Costs

Base Case Cost

The base case cost is $0.00 as a “do-nothing” case.

Gross Measure Cost

Pipe Insulation

Measure costs for pipe insulation adopts the information provided in 2008 DEER measure cost summary as shown in Table 8 -below. DEER 2014 does not include updates to measure costs.

DEER 2008 cost data is available on pipe insulation for space heating and cooling.  It does not provide the costs for high pressure steam (greater than 15 psig).  The costs of pipe insulation for non-space heating application and of high pressure steam, as covered in this document, are assumed to be the same as shown in Table 8 -below.

- Pipe Insulation Cost in DEER 2014

| Cost Case Description | Cost Case ID | Program Delivery Strategies | Material Cost | Installation Man Hours - Retrofit | Installation Labor Cost - Retrofit | Normalizing Unit | IMC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pipe Insulation - 1" Hot Water 120-200F, over 2" pipe | PipeIns-1inch-120to200F-hth2o | Downstream Prescriptive Rebates/Incentives | $1.59 | $0.07 | $3.63 | Ln. Ft. | $5.22 |
| Pipe Insulation - 1" Low Pressure (<15psig) steam 200 -250F, over 2" pipe | PipeIns-1inch-200to250F-lt15psigsteam | Downstream Prescriptive Rebates/Incentives | $1.59 | $0.07 | $3.63 | Ln. Ft. | $5.22 |

Fitting Insulation

- Fitting insulation costs (cost of insulation materials plus cost of installation) were determined based on telephone conversations with and written quotes provided by pipe insulation vendors.  They provided installed cost for a selection of typical insulation jobs for steam and hot water piping systems.  The data was processed to get a breakout of the cost to insulate straight pipe and the pipe fittings, as listed in Table 9 -.  Indoor installations specified an all-service jacket (ASJ), while outdoor installations specified a more durable aluminum wrap.  The vendor quoted 1 inch of insulation on hot water pipe and 1.5 inches on steam pipe.  The average costs represent an average of typical indoor and outdoor costs.

- Pipe Insulation Costs (Material & Installation) Provided by Vendor

| Parameter | Hot Water |  | Low-pressure Steam (0-15 psig) |  | High-pressure Steam (>15 psig) |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pipe Size (inch) | 0.75 | 2 | 0.75 | 2 | 0.75 | 2 |
| Insulation Thickness (inch) | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 |
| Pipe Fittings |  |  |  |  |  |  |
| Indoors ($/fitting) | $7.73 | $7.87 | $7.60 | $9.47 | $7.60 | $9.47 |
| Outdoors ($/fitting) | $7.87 | $9.60 | $8.67 | $7.33 | $8.67 | $7.33 |

Incremental Measure Cost

The incremental measure costs are the same as the measure case costs since the base case cost is $0.

# Appendix A.	Measure Description

Adapted from “Temperature’s Rising, an analysis of insulation options for hot applications,” by Robin DeGraff and Mike Irlbacher.

- A variety of pipe insulation products are commercially available, to provide energy savings and to protect personnel from burns.  In addition to hot water and steam, pipe insulation is applied to process fluid piping, HVAC piping, and cryogenic piping.  The difficult task is determining not what type of insulation could be used, but what type of insulation should be used in a specific application.  The answer depends on why the insulation is needed, its required lifetime, the pipe temperature, and its environment (indoors, outdoors, near food products, near corrosive chemicals, underfoot, overhead, etc.).  Equally important to the proper selection of the insulation material is the quality of workmanship involved in the installation, e.g., properly sealing the jacket to keep the insulation dry.

Insulation Materials

- Pipe insulation typically consists of the insulation material and a protective jacket (see Figure 1).  Both are available in a wide variety of materials.  Before an insulation material and jacketing system can be chosen, many parameters must be considered.  Fiberglass, mineral wool, calcium silicate, ceramic fiber, perlite, cellular glass, removable covers and more recently, high temperature polyisocyanurate, all have maximum operating temperatures good to 450 F or above.  Preformed or fabricated, these insulation materials are readily available.

- Courtesy of Accessible Products Company

Figure 1.	Pipe Insulation with Flexible Jacket

- Material Selection

- Criteria for selecting insulation material should include the reason for insulating.  Most piping is insulated to protect personnel or to provide an acceptable heat loss.  In the high temperature market, the primary reason for insulating a process line is process control.  Insulation may be extremely critical to the process.

- Each manufacturer publishes test data for the product it makes.  They typically list physical properties such as thermal conductivity, compressive strength, density, temperature range and flame and smoke development.  Each characteristic has a direct bearing on the insulation product’s ability to perform properly during operation of a given process or application at its service temperature.

- Installation

- Common problems associated with failed insulation could be avoided if the substrate could be designed to allow for the proper insulation application.  Design features that interfere with the insulator’s ability to properly insulate the system include the following:

- Pipes that are not spaced far enough apart and do not allow for the correct insulation thickness to be installed, nor enough room to work and provide a good installation of the insulation.

- Flanges, valves, elbows and other items installed too close together, making it impossible to properly insulate.

- The use of valves that do not have extended bonnets on them to allow for the correct insulation thickness under the valve handle or allow for maintenance of the valve.

- I-beams, braces, brackets and other items coming in contact with the pipe, causing a thermal short.

- Gauges, pipes, and man-way doors installed too close to the vessel or equipment, making it impossible to insulate around or above.

- Improper type of pipe support used.

- Pipes not primed before insulation is installed because it was never specified.

- Final Design Considerations

- The biggest reason for insulation failure is water; all choices for the system must be reviewed to make sure that the system is breathable, yet water-tight.  Additional lines of defense against water should be incorporated into the total design.

- Water ingress can be noted under improperly installed or maintained jacket laps, improper spacing of jacket ends, at fittings, flanges, valves and other areas.  The minimum insulation surface temperature for personnel protection is approximately 110 F.  Even when considering high-temperature lines of pipe to 450 F, the thickness of insulation will experience a temperature gradient from 450 ºF to 212 ºF, which is below the temperature of steam, to 110 F at the surface.  The thickness of insulation that lies between 212 F and 110 F is where water can be retained in the insulation.  If left in operation, this portion can be dried, but the resulting expense is not only an increase in energy required to dry the system, but the added danger of a raised surface temperature.  Since water is a conductor, not an insulator, the surface temperature will rise and may exceed that which is safe for personnel.  The presence of water also increases in the risk of corrosive under the insulation, which will eventually destroy the piping, at huge expense to the owner.

Attachments

[A]

[B]

[C]

[D]

[E]

[F]

References

Previous Revision, Pipe Insulation Workpaper

Attachment Files, Zipped, Previous Revision, Pipe Insulation Workpaper

CPUC Decision-138907(ALJ/DMG), July 14, 2011, Attachments A – B, Page A6.

EUL Summary Table, DEER, 2014

Net-to-Gross Support Table, DEER, 2014

CEC Database – Boilers Large Non-Electric, http://www.energy.ca.gov/appliances/database/historical_excel_files/Boilers/, Accessed April 29, 2014

DEER2011 and DEER2014 Weather Data Comparison, Basis for Attachment [B]

http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2013-Weather-Data-Comparison.zip

Pipe Insulation Calculations - Attachments [C] and [D]

Pipe Fitting Calculations - Attachments [E] and [F]

Revised DEER Measure Cost Summary (05_30_2008) Revised (06_02_2008).xls