## Refrigeration Data
| Compressor Type |  | Compressor HP | Condensing Temp |  | Suction Temp |  |  | Condenser Type |  | Condenser Motor HP |  | Existing VFD Control |  | Display Case Type | [8 empty] | Open multi deck | [14 empty] | Reach in multi deck | [13 empty] | Walk Ins
n=1,802 Unique Store Audits Average LT Suction Group/Store = 1.9 Average MT Suction Group/Store = 2.4 | Recip | Other | Average Compressor HP/Compressor | Average SCT Setpoint/Suction Group | FHP Present | Average SST Setpoint/ Med Temp Suction Group | Average SST Setpoint/ Low Temp Suction Group | FSP Present | Air Cooled | Evap Cooled | Avg. HP/Air Cooled Condenser | Avg. HP/Evap Cooled Condenser | Air Cooled | Evap Cooled | Glass Front Beverage Merchandiser | Island/coffin closed | Island/coffin open | Large Lighted Refrigerated Vending Machine | Open multi deck | Reach in multi deck | Service Case | Single-deck | Single-deck Doors | Avg. Mfg. Date | Avg. Med Temp. Setpoint | Avg. Low Temp Setpoint | Avg. Length Ft./Case | % Motors Shaded Pole | Avg. Qty. Motors/Case | % LED | Avg Qty of Lights in Canopy | Avg Qty of Lights in Rail | Avg Qty of Lights RI End | Avg Qty of Lights RI Mullion | Avg Qty of Lights Shelf | Avg. Qty of Lights Vert. RI Door | ASH Control Present? | % Night Covers Present | Avg. Mfg. Date | Avg. Med Temp. Setpoint | Avg. Low Temp Setpoint | Avg. Length Ft./Case | % Shaded Pole | Qty. Motors/Case | % LED | Avg Qty of Lights in Canopy | Avg Qty of Lights in Rail | Avg Qty of Lights RI End | Avg Qty of Lights RI Mullion | Avg Qty of Lights Shelf | Avg. Qty of Lights Vert. RI Door | ASH Control Present? | Avg. Area/Walk In | Avg. Med. Temp Setpoint | Avg. Low Temp Setpoint | Avg. Evap. Fan Qty./Walk In | Avg. Evaporator Qty./Walk In | % ECM | % Overhead Lighting LED | % Overhead Lighting CFL | % Overhead Lighting LFL | Avg. Overhead Lamp Count/Walk In | % Gasket Condition: Good | % Strip Curtains: Present | Main Door Size (Sq. Ft.) | WI-RI Door % Double Glazed | WI-RI Door % Triple Glazed | WI-RI Avg. Door Qty/Walk-In | WI-RI Avg. Door Length/Walk-In | ASH Control Present?
CZ01 | [8 empty] | 86.11% | 13.89% | 2.5 | 1
Built before 1978 | 87.5% | 12.5% | 10 | 90 | 23.25% | 16 | -21 | 16.59% |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 53.66% | 29.27% | 9.756% | 7.317% | 0% | 2005 | 34 | 0 | 21 | 100% | 5 | 0% | 4 | 0 | 0 | 0 | 1 | 0 | n/a | 36.36% | 2007 | 31 | -17 | 18 | 50% | 7 | 47.06% | 2 | 6 | 1 | 1 | 0 | 0 | 0% | 586 | 35 | -8 | 4.3 | 1.88 | 0% | 0% | 66.67% | 22.22% | 3.6 | 83.33% | 50% | 28 | 66.67% | 33.33% | 28.5 | 85 | 16.67%
Built between 1978 and 1992 | 100% | 0% | 14 | 68 | 0% | 19 | -19 | 9.434% |  |  |  |  | 0% | 0% | 5.825% | 0% | 3.883% | 0% | 55.34% | 25.24% | 9.709% | 0% | 0% | 2007 | 32 | -5 | 23 | 59.65% | 7 | 0% | 6 | 8 | 0 | 0 | 15 | 0 | 0% | 7.018% | 2007 | 21 | -12 | 35 | 42.31% | 18 | 61.9% | 0 | 0 | 2 | 1 | 0 | 27 | 23.08% | 413 | 34 | -8 | 7.4 | 1.91 | 34.15% | 0% | 42.86% | 57.14% | 6.7 | 81.25% | 78.57% | 35 | 50% | 50% | 18.8 | 47 | 50%
Built between 1993 and 2001 | 58.04% | 41.96% | 10 | 75 | 58.62% | 16 | -23 | 58.62% |  |  |  |  | 0% |  | 13.68% | 0.5263% | 2.632% | 0.5263% | 43.68% | 20% | 11.05% | 7.895% | 0% | 2012 | 33 | -2 | 27 | 81.93% | 9 | 24.35% | 5 | 6 | 0 | 0 | 7 | 0 | 21.43% | 22.89% | 2015 | 24 | -12 | 34 | 86.84% | 13 | 59.65% | 10 | 0 | 1 | 1 | 0 | 13 | 18.42% | 374 | 35 | -8 | 5.7 | 1.81 | 13.04% | 25.58% | 34.88% | 30.23% | 3.5 | 94.68% | 56.6% | 28 | 100% | 0% | 13.4 | 40 | 28.57%
Built between 2002 and 2005 | 54.17% | 45.83% | 8 | n/a | 24.79% | 20 | -25 | 0% | [6 empty] | 0% | 0% | 5.882% | 0% | 70.59% | 17.65% | 5.882% | 0% | 0% | 0 | n/a | -5 | 18 | 70.83% | n/a | 0% | 4 | 6 | 0 | 0 | 6 | 0 | 0% | 66.67% | 0 | n/a | -6 | 24 | 66.67% | n/a | 0% | 20 | 0 | 0 | 0 | 0 | 3 | 0% | 183 | n/a | n/a | 3.7 | 1.22 | 29.63% | 0% | 0% | 100% | 10.5 | 96.77% | 46.15% | 28 | 50% | 50% | 7.5 | 16 | 0%
CZ02 | [8 empty] | 67.47% | 32.53% | 5 | 1.9
Built 2006 and later | 100% | 0% | 14 | 72 | 27.74% | 20 | -23 | 40.38% |  |  |  |  | 50% | 0% | 0% | 0% | 0% | 0% | 55.56% | 5.556% | 11.11% | 27.78% | 0% | 2010 | 32 | -14 | 35 | 10% | 10 | 0% | 9 | 0 | 0 | 0 | 6 | 0 | 0% | 65% | 2009 | n/a | -7 | 28 | 50% | 20 | 50% | 0 | 0 | 0 | 0 | 0 | 14 | 50% | 499 | 29 | -8 | 6.2 | 1.88 | 84.38% | 0% | 0% | 80% | 7.8 | 97.22% | 52% | 35 | 0% | 100% | 53.7 | 134 | 100%
Built before 1978 | 87.19% | 12.81% | 11 | 89 | 58.54% | 16 | -20 | 58.54% |  |  |  |  | 0% | 0% | 0.8547% | 0% | 3.134% | 0% | 62.11% | 20.8% | 9.402% | 3.704% | 0% | 2014 | 34 | -1 | 23 | 61.47% | 6 | 8.333% | 5 | 5 | 0 | 0 | 5 | 0 | 25% | 42.2% | 2012 | 17 | -7 | 43 | 50.68% | 17 | 59.21% | 6 | 10 | 10 | 10 | 0 | 16 | 45.83% | 309 | 34 | -9 | 4.7 | 1.53 | 38.24% | 17.44% | 36.05% | 34.88% | 4.7 | 92.95% | 54.39% | 28 | 72.73% | 18.18% | 8.3 | 18 | 18.18%
Built between 1978 and 1992 | 86.55% | 13.45% | 12 | 76 | 15.48% | 19 | -21 | 34.2% |  |  |  |  | 0% | 40% | 0% | 0% | 9.893% | 0% | 61.76% | 20.05% | 7.487% | 0.8021% | 0% | 2014 | 34 | -3 | 31 | 68.4% | 8 | 8.178% | 9 | 6 | 0 | 6 | 5 | 0 | 0% | 24.24% | 2011 | 20 | -7 | 59 | 58.67% | 31 | 13.04% | 2 | 1 | 28 | 19 | 4 | 14 | 45.95% | 358 | 33 | -6 | 6.2 | 1.67 | 16.48% | 0% | 24.24% | 53.03% | 5.9 | 87.67% | 50% | 28 | 58.82% | 29.41% | 9.2 | 19 | 5.882%
Built between 1993 and 2001 | 90.27% | 9.728% | 13 | 84 | 44.85% | 17 | -21 | 56.44% |  |  |  |  | 5.882% | 55.56% | 0.2198% | 0% | 8.791% | 0% | 57.58% | 20.88% | 8.791% | 3.736% | 0% | 2013 | 35 | -4 | 31 | 71.37% | 11 | 10.38% | 9 | 9 | 4 | 7 | 7 | 4 | 0% | 32.44% | 2014 | 32 | -5 | 49 | 61.05% | 23 | 19.8% | 10 | 9 | 10 | 22 | 2 | 15 | 26.88% | 427 | 33 | -7 | 6.2 | 1.8 | 19.14% | 1.835% | 10.09% | 72.48% | 7.8 | 83.01% | 50.57% | 28 | 43.75% | 50% | 16.9 | 42 | 12.5%
Built between 2002 and 2005 | 48.67% | 51.33% | 9 | 89 | 21.11% | 19 | -18 | 35.2% |  |  |  |  | 0% | 33.33% | 0% | 1.587% | 11.9% | 0% | 57.14% | 19.05% | 4.762% | 5.556% | 0% | 2010 | 35 | -6 | 27 | 43.06% | 7 | 1.724% | 6 | 9 | 0 | 0 | 12 | 0 | 0% | 37.5% | 2010 | 20 | -7 | 69 | 41.67% | 27 | 57.14% | 1 | 1 | 19 | 31 | 0 | 28 | 4.167% | 479 | 35 | -7 | 7.2 | 2.09 | 21.82% | 0% | 4.255% | 93.62% | 7.4 | 100% | 45% | 28 | 33.33% | 66.67% | 29 | 73 | 0%
CZ03 | [8 empty] | 79.62% | 20.38% | 4.7 | 2.1
Built 2006 and later | 59.27% | 40.73% | 11 | 78 | 30.09% | 20 | -20 | 33.65% |  | 100% |  |  | 23.53% | 50% | 0% | 0% | 7.42% | 0% | 65.37% | 12.37% | 9.187% | 5.654% | 0% | 2014 | 32 | -6 | 28 | 14.05% | 8 | 29.44% | 7 | 6 | 0 | 0 | 11 | 0 | 0% | 45.95% | 2014 | 30 | -6 | 44 | 14.29% | 18 | 73.68% | 9 | 3 | 13 | 24 | 0 | 16 | 34.29% | 459 | 32 | -6 | 6 | 2.48 | 46.77% | 17.02% | 1.064% | 74.47% | 8.6 | 98.39% | 52.9% | 28 | 23.53% | 70.59% | 34.7 | 91 | 17.65%
Built before 1978 | 71.49% | 28.51% | 9 | 82 | 60.65% | 19 | -17 | 57.98% |  | 100% |  |  | 12.33% | 20% | 0.2933% | 0% | 4.985% | 0% | 60.22% | 20.43% | 10.36% | 3.715% | 0% | 2017 | 34 | -5 | 27 | 60.55% | 7 | 12.23% | 7 | 6 | 16 | 26 | 9 | 8 | 3.846% | 24.35% | 2016 | 23 | -7 | 47 | 63.64% | 20 | 39.53% | 10 | 9 | 8 | 13 | 9 | 18 | 26.34% | 266 | 32 | -7 | 4.9 | 1.47 | 23.67% | 2.713% | 23.64% | 48.45% | 5 | 82.66% | 48.69% | 28 | 69.09% | 29.09% | 11.9 | 30 | 5.455%
Built between 1978 and 1992 | 86.95% | 13.05% | 11 | 84 | 20.26% | 19 | -19 | 21.98% |  | 100% |  |  | 2.273% | 44% | 0.8568% | 0.306% | 9.18% | 0.4284% | 56.24% | 20.93% | 9.18% | 2.876% | 0% | 2017 | 34 | -6 | 30 | 53.21% | 8 | 6.203% | 7 | 6 | 4 | 2 | 8 | 19 | 10.89% | 31.01% | 2014 | 21 | -7 | 38 | 50.88% | 15 | 41.11% | 6 | 5 | 7 | 9 | 22 | 22 | 19.82% | 350 | 33 | -6 | 5.6 | 1.65 | 21.85% | 3.989% | 17.09% | 55.56% | 5.6 | 83.6% | 58.18% | 28 | 57.97% | 36.23% | 17.2 | 42 | 17.39%
Built between 1993 and 2001 | 80.65% | 19.35% | 11 | 82 | 23.76% | 19 | -21 | 33.72% |  | 100% |  |  | 22.45% | 34.78% | 0% | 0.5499% | 10.76% | 0% | 58.84% | 19.17% | 7.148% | 3.535% | 0% | 2015 | 32 | -8 | 28 | 56.34% | 7 | 11.06% | 8 | 7 | 7 | 33 | 8 | 2 | 0% | 26.97% | 2014 | 25 | -7 | 50 | 50.41% | 16 | 50% | 5 | 5 | 12 | 18 | 7 | 24 | 24.79% | 361 | 34 | -7 | 5.8 | 1.75 | 18.41% | 14.34% | 9.836% | 60.66% | 7.7 | 90.27% | 57% | 28 | 26.76% | 70.42% | 20.2 | 55 | 5.634%
Built between 2002 and 2005 | 57.95% | 42.05% | 12 | 85 | 35.57% | 20 | -21 | 39.24% |  | 100% |  |  | 18.75% | 27.27% | 0% | 0.4219% | 9.916% | 0% | 58.23% | 21.1% | 6.751% | 3.586% | 0% | 2010 | 32 | -5 | 28 | 41.67% | 8 | 7.311% | 8 | 6 | 7 | 11 | 12 | 0 | 75% | 35.51% | 2010 | 18 | -6 | 47 | 27% | 22 | 20.69% | 3 | 4 | 9 | 11 | 0 | 19 | 18.37% | 336 | 33 | -8 | 5.5 | 1.55 | 28.95% | 0% | 15.71% | 62.86% | 5.6 | 92.11% | 66.15% | 35 | 70% | 30% | 11.8 | 22 | 30%
CZ04 | [8 empty] | 84.09% | 15.91% | 5 | 2.9
Built 2006 and later | 39.44% | 60.56% | 8 | 89 | 24.27% | 16 | -21 | 29.51% |  | 100% |  |  | 0% | 0% | 0% | 0% | 12.37% | 0% | 52.58% | 18.56% | 11.34% | 5.155% | 0% | 2010 | 31 | -5 | 30 | 13.73% | 7 | 8.696% | 11 | 7 | 4 | 9 | 12 | 0 | 100% | 52.94% | 2013 | 35 | -4 | 64 | 5.556% | 27 | 60% | 6 | 1 | 7 | 10 | 48 | 25 | 33.33% | 801 | 33 | -8 | 6.3 | 1.55 | 59.52% | 4% | 20% | 44% | 5 | 94.34% | 97.5% | 35 | 100% | 0% | 14 | 35 | 0%
Built before 1978 | 91.84% | 8.163% | 15 | 84 | 36.99% | 18 | -20 | 5.479% |  | 100% |  |  | 0% | 0% | 0% | 0% | 8.584% | 0% | 57.08% | 24.03% | 9.013% | 1.288% | 0% | 2011 | 34 | -5 | 32 | 87.97% | 8 | 6.154% | 8 | 6 | 0 | 0 | 13 | 0 | 0% | 9.774% | 2011 | 16 | -7 | 39 | 83.93% | 19 | 11.11% | 8 | 9 | 0 | 4 | 0 | 21 | 19.64% | 408 | 32 | -6 | 5.5 | 1.63 | 8.065% | 0% | 11.76% | 44.12% | 3.9 | 85.33% | 56.52% | 28 | 46.15% | 53.85% | 12.1 | 37 | 30.77%
Built between 1978 and 1992 | 88.3% | 11.7% | 9 | 88 | 26.67% | 19 | -18 | 30% |  | 100% |  |  | 37.93% | 16.67% | 0.2532% | 0% | 10.63% | 0% | 57.72% | 18.48% | 9.62% | 3.291% | 0% | 2014 | 34 | -5 | 32 | 73.68% | 8 | 1.271% | 7 | 5 | 0 | 0 | 9 | 0 | 22.22% | 12.72% | 2015 | 11 | -6 | 59 | 83.56% | 22 | 18.82% | 5 | 5 | 6 | 11 | 4 | 32 | 25% | 330 | 33 | -7 | 4.9 | 1.48 | 18.35% | 7.965% | 21.24% | 61.95% | 5 | 83.06% | 45.16% | 28 | 75% | 15.62% | 10.1 | 30 | 0%
Built between 1993 and 2001 | 80.29% | 19.71% | 11 | 85 | 15% | 20 | -21 | 20.51% |  | 100% |  |  | 22.22% | 42.86% | 0% | 0.8493% | 13.16% | 0% | 58.81% | 17.62% | 7.643% | 1.911% | 0% | 2016 | 33 | -5 | 32 | 60.29% | 9 | 13.29% | 10 | 9 | 0 | 0 | 6 | 0 | 13.33% | 11.55% | 2010 | 27 | -6 | 73 | 62.65% | 45 | 45.59% | 25 | 4 | 29 | 53 | 0 | 38 | 42.17% | 327 | 33 | -6 | 4.9 | 1.58 | 21.25% | 18.92% | 1.802% | 70.27% | 8.8 | 87.21% | 49.64% | 28 | 50% | 36.84% | 11.2 | 35 | 18.42%
Built between 2002 and 2005 | 46.02% | 53.98% | 9 | 89 | 32.79% | 18 | -20 | 45.98% |  | 100% |  |  | 0% | 0% | 0% | 0.9434% | 8.491% | 0% | 49.06% | 33.02% | 4.717% | 3.774% | 0% | 2012 | 33 | -5 | 35 | 0% | 8 | 48.98% | 11 | 8 | 0 | 0 | 17 | 0 | 0% | 25% | 2010 | 27 | -5 | 60 | 2.857% | 25 | 84.62% | 0 | 0 | 16 | 22 | 0 | 58 | 20% | 377 | 36 | -8 | 5 | 1.71 | 61.54% | 0% | 0% | 93.18% | 5.9 | 93.75% | 88.46% | 35 | 20% | 70% | 30.8 | 82 | 20%
CZ05 | [8 empty] | 79.55% | 20.45% | 4 | 5
Built before 1978 | 81.97% | 18.03% | 7 | 90 | 43.78% | 17 | -13 | 45.81% |  | 100% |  |  | 0% | 0% | 0% | 0% | 1.587% | 0% | 66.67% | 22.22% | 7.937% | 1.587% | 0% | 2001 | 34 | 0 | 27 | 73.81% | 8 | 5% | 7 | 7 | 0 | 0 | 7 | 0 | n/a | 2.381% | 2001 | 38 | -7 | 46 | 85.71% | 13 | 55.56% | 1 | 33 | 0 | 0 | 0 | 27 | 7.143% | 297 | 33 | -3 | 3.7 | 1.45 | 2.5% | 13.33% | 33.33% | 53.33% | 3.9 | 84.78% | 46.51% | 24 | 80% | 0% | 6.4 | 28 | 0%
Built between 1978 and 1992 | 98.57% | 1.429% | 9 | 83 | 0% | 16 | -23 | 28.21% |  | 100% |  |  | 0% | 33.33% | 4.211% | 0% | 7.368% | 0% | 51.58% | 26.32% | 7.368% | 3.158% | 0% | 2014 | 31 | 0 | 31 | 75.51% | 7 | 54.05% | 9 | 9 | 0 | 0 | 4 | 0 | 0% | 4.082% | 2012 | 30 | -3 | 45 | 20% | 16 | 88.57% | 0 | 0 | 4 | 6 | 0 | 37 | 48% | 518 | 35 | -5 | 6.3 | 1.64 | 30% | 20% | 24% | 48% | 9.3 | 70.69% | 64.15% | 28 | 66.67% | 33.33% | 29.8 | 80 | 16.67%
Built between 1993 and 2001 | 95% | 5% | 9 | n/a | 22.73% | 19 | -16 | 9.091% |  | 100% |  |  | 0% | 0% | 0% | 0% | 4.348% | 0% | 67.39% | 19.57% | 7.609% | 1.087% | 0% | 1999 | 32 | 0 | 39 | 56.45% | 17 | 3.279% | 16 | 11 | 0 | 0 | 18 | 2 | 0% | 12.9% | 1999 | 13 | -3 | 96 | 66.67% | 62 | 8% | 13 | 0 | 0 | 0 | 3 | 30 | 50% | 344 | n/a | n/a | 5.2 | 1.58 | 0% | 52.94% | 0% | 47.06% | 11 | 80% | 56.06% | 28 | 100% | 0% | 11.3 | 27 | 15.38%
CZ11 | [8 empty] | 50% | 50% | 2.5 | 1.5
Built 2006 and later | 69.77% | 30.23% | 12 | 87 | 29.04% | 19 | -21 | 29.96% |  | 100% |  |  | 50% | 100% | 0% | 0% | 12.9% | 0% | 58.06% | 25.81% | 3.226% | 0% | 0% | 2010 | 33 | 0 | 33 | 24.07% | 13 | 9.195% | 7 | 6 | 0 | 0 | 5 | 0 | 0% | 9.259% | 2010 | 32 | 0 | 54 | 25% | 23 | 8.13% | 6 | 6 | 9 | 14 | 6 | 22 | 33.33% | 535 | 33 | -8 | 6.9 | 1.87 | 40% | 0% | 0% | 100% | 22 | 97.1% | 61.11% | 35 | 66.67% | 33.33% | 7 | n/a | 0%
Built before 1978 | 100% | 0% | 15 | 85 | 20.24% | 17 | -20 | 33.33% |  | 100% |  |  | 0% | 0% | 0% | 2.381% | 2.381% | 0% | 69.05% | 25% | 1.19% | 0% | 0% | 2003 | 37 | 0 | 23 | 86.21% | 6 | 28.12% | 7 | 8 | 0 | 0 | 5 | 0 | 0% | 24.14% | 2002 | 16 | 0 | 41 | 90.48% | 24 | 38.89% | 20 | 4 | 12 | 20 | 0 | 35 | 5% | 418 | 35 | -4 | 4.5 | 1.35 | 5.769% | 6.497% | 11.37% | 66.36% | 6.8 | 62.71% | 27.27% | 28 | 58.12% | 35.9% | 14.1 | 40 | 6.838%
Built between 1978 and 1992 | 100% | 0% | 13 | 80 | 25% | 21 | -21 | 31.03% |  | 100% |  |  | 9.091% | 43.75% | 0.9843% | 0.3937% | 8.661% | 0% | 56.1% | 26.18% | 5.512% | 2.165% | 0% | 2010 | 34 | 0 | 32 | 67.02% | 8 | 0% | 7 | 8 | 0 | 0 | 8 | 0 | 7.143% | 27.72% | 2014 | 18 | 0 | 42 | 69.17% | 17 | 6.25% | 3 | 3 | 11 | 18 | 0 | 8 | 14.17% | 416 | 33 | -8 | 5.3 | 1.5 | 6.224% | 0% | 0% | 48% | 7.5 | 75.25% | 62.07% | 28 | 25% | 75% | 28.4 | 76 | 0%
Built between 1993 and 2001 | 94.44% | 5.556% | 17 | 87 | 23.68% | 19 | -22 | 23.77% |  | 100% |  |  | 0% | 50% | 0% | 0% | 3.974% | 0% | 68.87% | 15.89% | 8.609% | 2.649% | 0% | 2015 | 33 | 0 | 30 | 53.85% | 8 | 6.068% | 7 | 8 | 3 | 3 | 7 | 0 | 16.67% | 32.69% | 2014 | 7 | 0 | 60 | 29.17% | 24 | 36.65% | 9 | 12 | 10 | 15 | 3 | 28 | 37.5% | 395 | 34 | -8 | 6.5 | 1.61 | 46.15% | 1.333% | 14.67% | 64% | 5.7 | 87.1% | 47.83% | 35 | 62.5% | 29.17% | 12.8 | 32 | 12.5%
Built between 2002 and 2005 | 97.83% | 2.174% | 16 | 70 | 28.05% | 16 | -21 | 32.93% |  | 100% |  |  |  | 0% | 0% | 0% | 5.97% | 0% | 47.76% | 26.87% | 8.955% | 10.45% | 0% | 2004 | 36 | 0 | 31 | 15.62% | 7 | 38.46% | 15 | 17 | 0 | 0 | 47 | 0 | n/a | 34.38% | 2004 | 18 | 0 | 37 | 38.89% | 18 | 100% | 0 | 0 | 0 | 0 | 0 | 54 | 27.78% | 384 | 32 | -8 | 6.3 | 1.73 | 0% | 4.545% | 18.83% | 60.39% | 6 | 100% | 59.26% | 28 | 66.67% | 31.25% | 12.6 | 33 | 8.333%
CZ12 | [8 empty] | 68.08% | 31.92% | 4 | 1.7
Built 2006 and later | 72.94% | 27.06% | 11 | 80 | 25.53% | 21 | -21 | 27.02% |  | 100% |  |  | 0% | 100% | 0% | 0% | 15.52% | 0% | 58.62% | 20.69% | 5.172% | 0% | 0% | 2010 | 30 | 0 | 46 | 50% | 13 | 3.067% | 7 | 8 | 1 | 1 | 6 | 0 | n/a | 23.53% | 2010 | 32 | 0 | 76 | 41.67% | 42 | 25% | 11 | 9 | 8 | 15 | 0 | 22 | 33.33% | 549 | 34 | -10 | 7.1 | 2.06 | 61.7% | 0% | 0% | 83.67% | 6.5 | 96.72% | 60% | 40 | 30% | 60% | 12.2 | 32 | 0%
Built before 1978 | 95.78% | 4.219% | 11 | 84 | 24.71% | 21 | -18 | 18.82% |  | 100% |  |  | 0% | 54.55% | 0% | 0.9259% | 4.63% | 0% | 51.54% | 27.78% | 8.642% | 6.481% | 0% | 2014 | 33 | 0 | 28 | 60.48% | 7 | 7.735% | 7 | 5 | 2 | 4 | 8 | 0 | 12.5% | 28.14% | 2014 | 27 | 0 | 53 | 44.44% | 17 | 39.86% | 4 | 20 | 9 | 14 | 3 | 29 | 11.24% | 1002 | 31 | -8 | 4.9 | 1.42 | 25.68% | 4.668% | 5.651% | 77.4% | 6.8 | 73.96% | 56.64% | 24 | 73.43% | 23.78% | 16.7 | 49 | 5.594%
Built between 1978 and 1992 | 93.67% | 6.332% | 13 | 84 | 16.19% | 20 | -20 | 14.17% |  | 100% |  |  | 12.9% | 76.92% | 0% | 1.048% | 6.985% | 0% | 58.21% | 23.4% | 8.498% | 1.863% | 0% | 2015 | 33 | 0 | 28 | 68.6% | 8 | 11.92% | 10 | 11 | 6 | 0 | 12 | 0 | 12.75% | 22% | 2012 | 27 | 0 | 49 | 62.19% | 21 | 45.83% | 30 | 0 | 16 | 22 | 0 | 37 | 15% | 386 | 34 | -6 | 6 | 1.75 | 8.73% | 0% | 0% | 76.92% | 6.5 | 78.63% | 49.59% | 28 | 28.57% | 71.43% | 34.3 | 105 | 28.57%
Built between 1993 and 2001 | 79.47% | 20.53% | 13 | 84 | 21.73% | 19 | -22 | 26.39% |  | 100% |  |  | 14.29% | 50% | 0% | 0.1592% | 9.554% | 0% | 55.25% | 23.09% | 7.006% | 4.936% | 0% | 2016 | 32 | 0 | 32 | 47.55% | 9 | 6.159% | 8 | 7 | 4 | 8 | 9 | 20 | 48.57% | 30.84% | 2016 | 20 | 0 | 56 | 35.17% | 21 | 29.19% | 10 | 5 | 9 | 16 | 3 | 33 | 33.1% | 448 | 31 | -7 | 6.4 | 1.85 | 27.04% | 1.818% | 29.09% | 56.36% | 7.7 | 85.25% | 50.76% | 28 | 87.1% | 9.677% | 12.8 | 29 | 3.226%
Built between 2002 and 2005 | 51.91% | 48.09% | 9 | 83 | 29.28% | 18 | -19 | 32.61% |  | 100% |  |  | 0% | 33.33% | 0% | 0% | 14.16% | 0% | 55.71% | 21.46% | 4.11% | 4.566% | 0% | 2011 | 31 | 0 | 34 | 45.9% | 12 | 0% | 6 | 7 | 0 | 0 | 4 | 0 | 0% | 31.15% | 2013 | 22 | 0 | 68 | 51.06% | 35 | 12.5% | 0 | 6 | 8 | 1 | 0 | 63 | 44.68% | 516 | 36 | -8 | 6.9 | 1.94 | 15.53% | 0% | 1.942% | 93.2% | 6.3 | 97.35% | 62.32% | 35 | 82% | 14% | 14.7 | 41 | 8%
CZ13 | [8 empty] | 51.56% | 48.44% | 1.7 | 1.2
Built 2006 and later | 78.46% | 21.54% | 18 | 83 | 23.9% | 18 | -23 | 31.98% |  | 100% |  |  | 0% | 33.33% | 0% | 0% | 8.824% | 0% | 57.84% | 18.63% | 2.941% | 11.76% | 0% | 2014 | 33 | 0 | 29 | 44.07% | 7 | 5.652% | 8 | 5 | 0 | 0 | 9 | 42 | 0% | 11.86% | 2007 | n/a | 0 | 50 | 26.32% | 22 | 13.92% | 8 | 2 | 12 | 24 | 0 | 29 | 10.53% | 600 | 32 | -8 | 7.5 | 2.25 | 11.63% | 4.587% | 0% | 88.07% | 6.7 | 98.25% | 88.24% | 32 | 57.14% | 42.86% | 21 | 53 | 0%
Built before 1978 | 88.95% | 11.05% | 10 | 80 | 0% | 20 | -18 | 60% |  | 100% |  |  | 12.5% | 33.33% | 1.111% | 0% | 9.259% | 0% | 51.11% | 24.81% | 11.11% | 2.593% | 0% | 2015 | 34 | 0 | 29 | 75.36% | 6 | 10.94% | 10 | 9 | 4 | 8 | 8 | 0 | 0% | 13.04% | 2015 | 24 | 0 | 37 | 83.58% | 12 | 41.89% | 6 | 6 | 7 | 12 | 0 | 33 | 4.478% | 476 | 31 | -7 | 5.9 | 1.88 | 15.48% | 0% | 0% | 100% | 20.3 | 85.37% | 68.39% | 28 | 37.5% | 62.5% | 18.6 | 64 | 12.5%
Built between 1978 and 1992 | 96.54% | 3.463% | 10 | 80 | 17.06% | 18 | -20 | 11.89% |  | 100% |  |  | 0% | 66.67% | 1.484% | 0% | 8.72% | 0% | 52.88% | 25.05% | 8.163% | 3.711% | 0% | 2017 | 34 | 0 | 30 | 69.47% | 8 | 2.509% | 8 | 7 | 0 | 0 | 11 | 0 | 4.762% | 4.211% | 2017 | 27 | 0 | 48 | 71.85% | 31 | 50% | 41 | 0 | 9 | 17 | 3 | 49 | 15.91% | 441 | 32 | -6 | 5.8 | 1.59 | 12.18% | 0% | 0% | 100% | 16 | 86.59% | 67.02% | 28 | 50% | 50% | 19 | n/a | 0%
Built between 1993 and 2001 | 88.22% | 11.78% | 11 | 84 | 21.45% | 20 | -20 | 36.92% |  | 100% |  |  | 9.091% | 60% | 0.4717% | 0.2358% | 12.74% | 0% | 56.37% | 20.52% | 6.132% | 3.538% | 0% | 2009 | 31 | 0 | 36 | 52.3% | 11 | 0% | 5 | 4 | 0 | 0 | 10 | 0 | 40% | 10.88% | 2009 | 15 | 0 | 47 | 66.67% | 17 | 0% | 0 | 0 | 0 | 0 | 1 | 16 | 19.54% | 477 | 35 | -8 | 6.2 | 1.83 | 18.37% | 0% | 0% | 100% | 21.7 | 88.71% | 62.37% | 28 | 100% | 0% | 14 | 35 | 0%
Built between 2002 and 2005 | 65.76% | 34.24% | 10 | 89 | 19.2% | 18 | -19 | 27.73% |  | 100% |  |  | 38.89% | 44.44% | 0% | 0.8772% | 13.16% | 0% | 55.85% | 19.3% | 6.433% | 3.509% | 0.8772% | 2013 | 33 | 0 | 30 | 45.55% | 9 | 0% | 5 | 4 | 0 | 0 | 10 | 0 | 0% | 3.141% | 2013 | 13 | 0 | 74 | 50% | 21 | 0% | 0 | 0 | 0 | 0 | 1 | 16 | 24.62% | 548 | 34 | -8 | 7.5 | 2.04 | 0.6944% | 0% | 0% | 100% | 17 | 82.18% | 66.67% | 35 | 0% | 100% | 19.7 | 73 | 33.33%
CZ16 | [8 empty] | 72.73% | 27.27% | 2.9 | 1.7
Built before 1978 | 100% | 0% | 9 | 44 | 11.11% | 22 | -23 | 29.37% |  | 100% |  |  | 5.882% | 55.56% | 0% | 0% | 8.197% | 0% | 49.18% | 31.15% | 11.48% | 0% | 0% | 2012 | 32 | 0 | 23 | 96.67% | 3 | n/a | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 0% | 2011 | 32 | 0 | 32 | 89.47% | 2 | n/a | 3 | 16 | 0 | 4 | 0 | 0 | 0% | 327 | 39 | -5 | 4.7 | 1.41 | 0% | 0% | 0% | 0% | 2 | 76.47% | 51.61% | 28 | 57.14% | 42.86% | 5.5 | 14 | 0%
Built between 1978 and 1992 | 94.2% | 5.797% | 12 | 86 | 0% | 17 | -21 | 29.09% |  | 100% |  |  | 0% | 33.33% | 0% | 0% | 6.25% | 0% | 59.03% | 24.31% | 8.333% | 2.083% | 0% | 2008 | 34 | 0 | 26 | 76.47% | 6 | n/a | 0 | 0 | 0 | 0 | 0 | 0 | n/a | 25.88% | 2007 | 35 | 0 | 36 | 62.86% | 15 | n/a | 8 | 9 | 2 | 3 | 0 | 22 | 20% | 371 | 34 | -7 | 5.9 | 1.58 | 19.35% | 0% | 14.81% | 85.19% | 7.3 | 90% | 60.42% | 28 | 75% | 25% | 13.6 | 29 | 0%
Average | 80.98% | 19.02% | 11.3333 | 81.9459 | 25.21% | 18.6154 | -20.2564 | 30.96% | 71.02% | 28.98% |  |  | 9.406% | 33.32%
ISP Determination | Recriprocation; non-centrifugal |  |  | 80 | None | None | None | [5 empty] | None | VFD for 2006 or after
ISP Notes |  |  |  | DEER2005 prototypes have SCT setpoint at 80 oF which is stringent than the ISP. Hence, no revisions required. | Only Few Instances with FHP w/o noticable trend | No a parameters in eQuest prototypes |  | Only Few Instances with FHP w/o noticable trend | Separate prototypes will be created for Air-cooled and evap-cooled |  |  |  |  | Certain climate zones have 100% VFDs Built after 2006
Note on AA1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Due to time contraints, individual case attribute data was only analyzed for Open Multi-Deck and Reach In Multideck. These two case types represent the majority of cases found in typical grocery applications.
Note on AP1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Due to time contraints, individual case attribute data was only analyzed for Open Multi-Deck and Reach In Multideck. These two case types represent the majority of cases found in typical grocery applications.

## Building Data
n=1,071 Unique Store Audits | Avg. Sq. Ft. Floor Area/Building | Avg. Year Store Built | Avg. No. of Unoccupied Hours/Building | % Has Meat Prep | % Has Bakery | % Has Deli
CZ01 | 28850 | 1994 | 7 | 25% | 8.333% | 16.67%
Built between 1978 and 1992 | 23333 |  | 8 | 0% | 0% | 0%
Built between 1993 and 2001 | 32954 |  | 6 | 37.5% | 12.5% | 25%
Built between 2002 and 2005 | 12568 |  | 11 | 0% | 0% | 0%
CZ02 | 23793 | 1992 | 6 | 16% | 12% | 32%
Built before 1978 | 12300 |  | 7 | 25% | 25% | 25%
Built between 1978 and 1992 | 22389 |  | 5 | 11.11% | 11.11% | 33.33%
Built between 1993 and 2001 | 28556 |  | 7 | 18.18% | 9.091% | 36.36%
Built between 2002 and 2005 | 30000 |  | 0 | 0% | 0% | 0%
CZ03 | 22389 | 1977 | 6 | 17.5% | 13.75% | 25%
Built before 1978 | 20645 |  | 6 | 22.22% | 22.22% | 16.67%
Built between 1978 and 1992 | 20634 |  | 6 | 16.28% | 11.63% | 23.26%
Built between 1993 and 2001 | 28215 |  | 6 | 20% | 13.33% | 33.33%
Built between 2002 and 2005 | 27250 |  | 2 | 0% | 0% | 50%
CZ04 | 33448 | 1988 | 6 | 9.091% | 9.091% | 18.18%
Built before 1978 | 30187 |  | 7 | 0% | 0% | 0%
Built between 1978 and 1992 | 33766 |  | 6 | 14.29% | 14.29% | 28.57%
Built between 1993 and 2001 | 41000 |  | 6 | 0% | 0% | 0%
CZ05 | 22013 | 1991 | 7 | 100% | 100% | 100%
Built between 1978 and 1992 | 22013 |  | 7 | 100% | 100% | 100%
CZ11 | 25182 | 1993 | 4 | 17.24% | 6.897% | 62.07%
Built before 1978 | 17332 |  | 10 | 16.67% | 0% | 66.67%
Built between 1978 and 1992 | 24476 |  | 3 | 0% | 0% | 61.11%
Built between 1993 and 2001 | 37144 |  | 5 | 80% | 40% | 60%
CZ12 | 23336 | 1989 | 3 | 15.91% | 6.818% | 29.55%
Built before 1978 | 17333 |  | 3 | 0% | 0% | 0%
Built between 1978 and 1992 | 21440 |  | 3 | 16.13% | 6.452% | 29.03%
Built between 1993 and 2001 | 30311 |  | 3 | 0% | 0% | 28.57%
Built between 2002 and 2005 | 32667 |  | 3 | 66.67% | 33.33% | 66.67%
CZ13 | 27582 | 1987 | 6 | 14.29% | 7.143% | 28.57%
Built before 1978 | 17250 |  | 8 | 0% | 0% | 25%
Built between 1978 and 1992 | 29936 |  | 6 | 14.29% | 0% | 28.57%
Built between 1993 and 2001 | 35867 |  | 4 | 33.33% | 33.33% | 33.33%
CZ16 | 10000 | 1960 | 10 | 0% | 0% | 100%
Built before 1978 | 10000 |  | 10 | 0% | 0% | 100%

## Summary-Ref Data
Refrigeration Parameter | Results based on n=1802 store audits | ISP determination
Compressor Type | Average 81% stores have reciprocating compressors | The existing prototypes already uses non-centrifugal compressor.
Average Saturating Condensing Temperature (SCT) Setpoint | 82 degree F | The existing prototypes use 80 degree F which is more stringent. Hence no updates.
Floating Head Pressure (FHP) controls | Average 25% stores have FHP. Very few CZs have >50% FHP for certain vintages | Not an ISP
Floating Suction Pressure (FSP) controls | Average 31% stores have FHP. Very few CZs have >50% FHP for certain vintages | Not an ISP
Air Cooled | Average 71% | Protypes for both air cooled and evap cooled are generated
Evap Cooled | Average 29%
Existing VFD Control-Air Cooled Condenser | Average 9% have VFDs with no instances of >50% | Not an ISP
Existing VFD Control-Evaporative Cooled Condenser | Average 33% have VFDs with a few instances of >50% | No pattern to determine this as an ISP for the population