## New Calcs
Equation 1 - Base Refrigeration Energy Use
|  |  |  | Wide Code equivilant base (5-12') | Narrow Code equivilant base (6-12' and 1- 8')
Hours / year | 8760 |  |  | 43438.992 | 58467.648 | EB,REFRIGERAT is refrigeration energy use for the base case, coffin case scenario (kWh/lf-year)
No. defrost cycles/day | 2 |  |  | 422 | 426 | QB is the base case cooling coil capacity, (426 Btu/Hr-LF) from Hill Phoenix OIZ 12’ Island Frozen Food Merchandiser. See Figure 1 - Base Case- Code Coffin, Hill Phoenix ONZ.
Defrot cyle duration | 0.25 |  |  | 8578 | 8578 | HB,REFRIG is the number of hours of refrigeration operation (The Average EER value should be used with a refrigeration system duty load of 100%. However, the refrigeration system will not run during defrost hours (153 hrs/year, see footnote 10), so this value is reduced to 8,578 hrs/year..
Defrost operating hours | 182.5 |  |  | 60 | 80 | LB is the base case length in linear feet (60 LF) for wide base and 80 LF for narrow case
Hb,fan | 8577.5 |  |  | 5 | 5 | EERB is compressor refrigeration system energy efficiency (5 Btu/Hr-W) | added justification-> | 2006 ASHRAE Handbook, Refrigeration: Page 46.14 – “EERs range from 4 to 5 Btu/h per watt for frozen food units to as low as 3.5 to 4.0 Btu/h per watt for ice cream units.”
Equation 2 - Base Case Auxiliary Equipment Annual Energy Consumption
|  | Wide Code equivilant base (5-12') | Narrow Code equivilant base (6-12' and 1- 8')
|  |  | Total code case power (80 ') | 8' | 12'
|  | 14692.77 | 21909.426 | 2292.834 | 19616.592 | EB,AUX is the base case scenario annual energy consumption of the auxiliary equipment, (fans, anti-sweat-heaters, defrost heaters, and drain heaters.) Lighting is not included because this case does not contain display case lighting. Units are kWh / year.
|  | 33 | N/A | 33 | 44 | PB,FAN is the base case fan direct power consumption per case. This value is 68 Watts / Case, and is taken directly from the manufacturers data. See Figure 1 - Base Case- Code Coffin, Hill Phoenix ONZ.
|  | 8578 | N/A | 8578 | 8578 | HB,FAN is the annual base case fan operating hours. This value is 8669[1] hrs / year. [1] Base case fan annual operating hours are the number of hours in a year, minus the time they are off during the defrost cycle, which occurs for 15 minutes a day. 8760 hrs / year - .25 hrs / cycle * 1 cycle / day * 365 days / year = 8669 hrs / year.
|  | 253 | N/A | 181 | 265 | PB,ASH is the base case anti-sweat-heater direct power consumption per case. This value is 265 Watts / Case, and is taken directly from the manufacturers data. See Figure 1 - Base Case- Code Coffin, Hill Phoenix ONZ.
|  | 8760 | N/A | 8760 | 8760 | HB,ASH is the annual base case anti-sweat-heater operating hours. This value is 8760 hrs / year, as the duty cycle is assumed to be 100%, where no controllers are present.
|  | 2400 | N/A | 1600 | 2400 | PB,DEF is the base case defrost-heater direct power consumption per case. This value is 2400 Watts / Case, and is taken directly from the manufacturers data. See Figure 1 - Base Case- Code Coffin, Hill Phoenix ONZ.
|  | 183 | N/A | 183 | 183 | HB,DEF is the annual base case defrost-heater operating hours. This value is 91[2] hrs / year.[2] Base case defrost-heater operating hours are the number of hours on per cycle times the cycles per day times the day per year. .25 hrs / cycle * 1 cycle / day * 365 days / year = 91 hrs / year
|  | 0 | N/A | 15 | 15 | PB,DRAIN is the base case drain-heater direct power consumption per case. This value is 15 Watts / Case, and is taken directly from the manufacturers data. See Figure 1 - Base Case- Code Coffin, Hill Phoenix ONZ.
|  | 8760 | N/A | 8760 | 8760 | HB,DRAIN is the annual base case anti-sweat-heater operating hours. This value is 8760 hrs / year, as the duty cycle is assumed to be 100%.
|  | 5 | N/A | 1 | 6 | CASESB is the number of 12’ cases in the 60’ case lineup (wide case). This value is 5 cases.
Equation 3 - Base Case Annual Energy Consumption
|  |  |  | Wide Code equivilant base (5-12') | Narrow Code equivilant base (6-12' and 1- 8')
|  |  |  | 58131.762 | 80377.074 | EB, is the annual energy used by the base case lineup.
|  |  |  | 43438.992 | 58467.648 | EB,REFRIG is refrigeration energy use for the base case coffin lineup. See Equation 1 - Base Refrigeration Energy Use.
|  |  |  | 14692.77 | 21909.426 | EB,AUX is the base case scenario annual energy consumption of the auxiliary equipment, (fans, anti-sweat-heaters, defrost heaters, and drain heaters.) Lighting is not included because this case does not contain display case lighting. See Equation 2 - Base Case Auxiliary Equipment Annual Energy Consumption.
Equation 4 - Proposed Case Refrigeration System EER
[5 empty] | 5.1 | EERP is the proposed case energy efficiency ratio of the refrigeration system. this value was calculated to be 6.2 Btu/hr/Watt
| Frozen Food | Ice Cream | FF Delta T | Ice Cream Delta T | 1.02 | 1.02 is a coefficient to create the 2% increase[1] in efficiency for every single degree Fahrenheit increase in evaporator suction temperature. This coefficient is unit less. [1] The efficiency of a compressor in a refrigeration system increases by about 2% per degree Fahrenheit increase in suction temperature. “Industrial Refrigeration Best Practices Guide” December 2004, prepared by Cascade Energy Engineering with support from Northwest Energy Efficiency Alliance. Page 46, Effect of increasing Suction Pressure.
ONZ Evap Temp | -12 | -22 |  |  | 1 | DEGREE INCREASED is the number of degrees Fahrenheit that the energy efficient evaporator suction temperature is increased. This value is 11[2]. [2] DEGREE INCREASED = 11, this is the difference between the Base Case (ONZ Coffin) evaporator suction temperature of -22°F, (See Figure 1 - Base Case Coffin, Hill Phoenix OIZ) and the proposed case (ORZ Reach-in) evaporator suction temperature of -11°F (see Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in.)
ORZ Evap Temp | -11 | -17 | 1 | 5 | 5 | EERB is the base case compressor refrigeration system energy efficiency. This value is 5.0[3] Btu/Hr-W. [3] 2006 ASHRAE Handbook, Refrigeration: Page 46.14 – “EERs range from 4 to 5 Btu/h per watt for frozen food units to as low as 3.5 to 4.0 Btu/h per watt for ice cream units.”
ONRIZ Evap Temp | -11 | -17 | 1 | 5
Equation 5 - Proposed Case Reach-in Refrigeration Annual Energy Consumption
|  |  |  | High Eff RI | Code RI
|  |  |  | 11504.6118 | 13294.218 | EP,REFRIG is refrigeration energy use for the base case coffin lineup.
|  |  |  | 855 | 988 | QP is the base case cooling coil capacity. This value accounts for the reduced load due to high efficiency fans, a reduction of 96 Btu/ hr / door. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in.
|  |  |  | 8578 | 8578 | HB,REFRIG is the number of hours of refrigeration operation (The Average EER value should be used with a refrigeration system duty load of 100%. However, the refrigeration system will not run during defrost hours (153 hrs/year, see footnote 10), so this value is reduced to 8,578 hrs/year..
|  |  |  | 8 | 8 | DP is the base case number of doors. This value is 8 doors. See Table 2 - Base and Proposed Volume, Length, and Door Relationships.
|  |  |  | 5.1 | 5.1 | EERP is compressor refrigeration system energy efficiency. This value is 6.2 Btu/Hr-W (it should be 5.1). See Equation 4 - Proposed Case Refrigeration System EER.
Equation 6 - Proposed Case Annual Auxiliary Equipment Energy Consumption
|  |  |  | High Eff RI | Code RI
|  |  |  | 6874.292 | 6297.952 | EP,AUX is the proposed case scenario annual energy consumption of the auxiliary equipment, (fans, anti-sweat-heaters, defrost heaters, and lighting.)
|  |  |  | 37 | 37 | PP,FAN is the proposed case fan direct power consumption per case. This value is taken directly from the manufacturers data. Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in.
|  |  |  | 8578 | 8578 | HP,FAN is the annual proposed case fan operating hours. This value is 8578[1] hrs / year. [1] Proposed case fan annual operating hours are the number of hours in a year, minus the time they are off during the defrost cycle, which occurs once a day for 30 minutes a day. 8760 hrs / year - 0.5 hrs / cycle * 1 cycle / day * 365 days / year = 8669 hrs / year. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in
|  |  |  | 418 | 403 | PP,ASH is the proposed case anti-sweat-heater direct power consumption per case. This value is taken directly from the manufacturers data. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in.
|  |  | Should we use the PECI recommended value of 50%? | 4380 | 4380 | HP,ASH is the annual proposed case anti-sweat-heater operating hours. This value is 2278 hrs / year. This is based on a 26% run time[2]. [2] ASHC runtime: Three Studies and one assumption to find an average value of 26%: Final Evaluation, Monitoring, and Verification (EM&V) Report for 2004-2005 EnergySmart Grocer Program. 2006. PWP, Inc. Page 28-29. Value was 8%. Retrocommissiong for ASHC – PECI. Value was 27%. Technical Study Report: Product Tsting Anit Sweat Heater Control – kW Engineering to Utah power. Value is 17%. A fourth value, 50%, is the most convervative estimate, which was made by a PECI Sr Enginer.
|  |  |  | 4572 | 3388 | PP,DEF is the proposed case defrost-heater direct power consumption per case. This value is taken directly from the manufacturers data. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in.
|  |  |  | 183 | 183 | HP,DEF is the annual base case defrost-heater operating hours. This value is 183[3] hrs / year. [3] Base case defrost-heater operating hours are the number of hours on per cycle times the cycles per day times the day per year. 0.5 hrs / cycle * 1 cycle / day * 365 days / year = 183 hrs / year. Min Defrost is 15 min, cut off is 46 minutes. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in
|  |  |  | 78 | 77 | PP,LIGHT is the proposed case fluorescent display case lighting direct power consumption per case. This value is 288 Watts / Case, and is taken directly from the manufacturers data. See Figure 2 - Proposed Case Hill Phoenix ORZ Reach-in
|  |  |  | 5798 | 5798 | HP,LIGHT is the annual proposed case lighting operating hours. This value is 5798[1] hrs / year. [1] GrocerSmart Survey of Main Lighting Schedule of Large Grocery Stores in PG&E Service Territory: Out to 422 stores meeting criteria, average hours/year is 5,798.
|  |  |  | 2 | 2 | CASESP is the number of 4 door reach-in cases in the proposed case scenario. This value is 2 cases. See Table 2 - Base and Proposed Volume, Length, and Door Relationships.
Equation 7 - Proposed Case Annual Energy Consumption
|  |  |  | High Eff RI | Code RI
|  |  |  | 18378.9038 | 19592.17 | EP is the annual energy consumed by the proposed case scenario.
|  |  |  | 11504.6118 | 13294.218 | EP,REFRIG is refrigeration energy use for the proposed case reach-in lineup. See Equation 5 - Proposed Case Reach-in Refrigeration Annual Energy Consumption
|  |  |  | 6874.292 | 6297.952 | EP,AUX is the proposed case scenario annual energy consumption of the auxiliary equipment, (fans, anti-sweat-heaters, defrost heaters, and lighting. See Equation 7 - Proposed Case Annual Energy Consumption)
Equation 8 - Annual Energy Savings
narrow to code
Above code Narrow | Above code Wide | Wide Code RI to High Eff RI | Narrow Code to High Eff RI | Wide to Code Equivalent Base (5-12') | Narrow to Code Equivalent Base (6-12' and 1- 8')
60.6633 | 60.6633 | 1987.6429 | 3099.9085 | 1926.9796 | 3039.2452 | ESAVE is the annual energy savings per linear foot of installed reach-in display case.
|  | 58131.762 | 80377.074 | 58131.762 | 80377.074 | EB is the annual energy used by the base case lineup. See Equation 3 - Base Case Annual Energy Consumption
|  | 18378.9038 | 18378.9038 | 19592.17 | 19592.17 | EP is the annual energy consumed by the proposed case scenario. See Equation 7 - Proposed Case Annual Energy Consumption
|  | 20 | 20 | 20 | 20 | LP is the length of the proposed case scenario, the reach-in display cases. This value is 20 linear feet. This value ensures that the energy savings report the amount of energy saved for replacing the entire existing coffin case lineup with about 1/4 the length of a proposed case lineup. See Table 2 - Base and Proposed Volume, Length, and Door Relationships
Equation 9 - Demand Reduction
|  | SWCR019A | SWCR019B
Above code Narrow | Above code Wide | Wide Code RI to High Eff RI | Narrow Code to High Eff RI | Wide to Code Equivalent Base (5-12') | Narrow to Code Equivalent Base (6-12' and 1- 8')
0.0056093 | 0.0056093 | 0.18379 | 0.28664 | 0.17818 | 0.28103 | DREDUCTION is the demand reduction per linear foot of reach-in display case installed. The rebate should be limited to 1/3rd of the length of the original base case, coffin case lineup.
60.6633 | 60.6633 | 1987.6429 | 3099.9085 | 1926.9796 | 3039.2452 | ESAVE is the annual energy savings per linear foot of installed reach-in display case.
8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 is the number of hours in a year.
0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | FP-C-D is the peak coincident demand factor. This value is 0.81.
Note on F21: Rosillo, Adan: These hours is for two defrost cycles/day not one as indicated
Note on E22: Rosillo, Adan: ASH value for a F-8' Glass Front
Note on F22: Rosillo, Adan: ASH value for a F-12' Glass Front
Note on E24: Rosillo, Adan: Defrost power should be for a F-8' or 1,600 W
Note on F24: Rosillo, Adan: Defrost power should be 2400 watts
Note on F25: Rosillo, Adan: This value is for 2 defrost cycles/day
Note on F46: Rosillo, Adan: This number compares Frozen Food and Ice Cream, which creates a larger DeltaT. It should compare FF to FF and/or IceC to ICeC.
Note on F57: Rosillo, Adan: This number should be for a ORZ Frozen Food w/Eliminator = 988
Note on E72: Rosillo, Adan: ASH Eliminator = 418
Note on F72: Rosillo, Adan: Should be ORZ 4-D/Eliminator = 403

## Base and Proposed Vol & Length
Scenario | Code equivilant Wide Base Case | Code equivilant Narrow Base Case | Proposed Code Case | Proposed HE Code Case
Description | 60 linear feet of Wide Coffin Case | 80 linear feet of Narrow Coffin Case | 20 linear feet (8 doors) of Reach-in Case | 20 linear feet (8 doors) of Reach-in Case
Manufactuer / Model | Hill Phoenix OWZGG | Hill Phoenix ONZ | Hill Phoenix ORZ | Hill Phoenix ONRIZ
Line up length (inches) | 720 | 960 | 240 | 240
Display Width (inches) | 43.25 | 34.6875 | 30.875 | 29.75
Display Height (inches) | 16.125 | 13.375 | 59 | 62.375
Dislpay Volume (cubic feet) | 290.5859 | 257.7474 | 253.0035 | 257.73
TDA, SQ.FT. | 216.25 | 231.25 | 98.3333 | 103.9583
Max Energy Daily Usage, kWh/day | 130.1425 | 138.6925 | 57.6767 | 60.8267
Max Energy Daily Usage, btu/day | 444064.6382 | 473238.4489 | 196800.9537 | 207549.1997
for and 18 hrs cycle, btu/hr | 24670.2577 | 26291.0249 | 10933.3863 | 11530.5111
Max Energy Usage, Btu/hr-lf & Btu/hr-door | 308.3782 | 328.6378 | 1366.6733 | 1441.3139

## COSTS
Quote from case Manf June 7, 2012
2.5 ft/door
WI RI | 2000 | /door | Equip | 800 | ft
| 300 | /door | Labor | 120 | ft
High eff doors | 90 | /door | Upgraded door | 36 | ft